## Slide 1: Opacity
Sources other than wood-fired boilers
Source | Location | Limit | Compliance Date
Pre 1970 | Outside special control area | 40% | Through 12/31/19
 |  | 20% | After 01/01/20
Pre 1970 | Inside special control area | 20% | 04/16/15
Post 1970 | Statewide | 20% | 04/16/15

## Slide 2: Opacity
Wood-fired boilers
*as long as grate cleaning is performed in accordance with DEQ approved grate cleaning plan **Source can request boiler specific opacity between 20-40% measured during boiler specific grain loading source test
Source | Limit | Exception | Compliance Date
Pre 1970 | 40% | 55% for 2 6-minute blocks | Through 12/31/19
Pre 1970 | 20% | 40% for 2 6-minute blocks | After 01/01/20
 |  | 40% during grate cleaning* | 
 |  | Boiler specific up to 40%** | 
Post 1970 <04/16/15 | 20% | 40% for 2 6-minute blocks | 04/16/15
Post- 04/16/15 | 20% | None | 04/16/15

## Slide 3: Grain loading ALL Equipment
Source | Limit (gr/dscf) | Compliance Date
ALL sources < 0.080 gr/dscf | 0.10 | 04/16/15
Pre 1970 | 0.24 | Until 12/31/19
 | 0.15 | On 01/01/20
Used < 876 hours/year | 0.24 | Until 12/31/19
 | 0.20 | On 01/01/20
Post 1970 | 0.14 | 04/16/15
After 04/16/15 | 0.10 | 04/16/15
Pre 1970 WOOD-FIRED BOILER >0.15 gr/dscf | 0.17 | 10/01/19
Notes: This is an overview of the proposed changes to the grain loading standards.
“Sensitive areas” are designated because of air quality problems