Sources Potentially Exceeding 0.1 gr/dscf

| Source | Permit No. | Emissions Unit | Source Test Results | Comment |
| --- | --- | --- | --- | --- |
| Boise Cascade (Pilot Rock) | 30-0016 | 3 wood-fired boilers | Backup to natural gas fired boiler. Previous test results: Boiler 1: 0.08-0.17 and 0.4% (6 tests); Boiler 3: 0.08-0.19 and 0-1% (8 tests); Boiler 4: 0.06-0.10 (4 tests) | 3 hogged fuel boilers cannot meet standard, would shut down permanently. Cannot add control device which requires an air flow system that is incompatible with stacks. Need great fuel (size & moisture), steady load. And luck |
| Collins (Fremont Sawmill) | 19-0002 | Two wood-fired boilers | Most recent test results are 0.13 for boiler 1 and 0.09 for boiler 2. | Already does a lot of maintenance, cannot meet 0.10 consistently, needs controls. Thinking of package NG boiler |
| Columbia Forest Products | 18-0014 | 2 wood-fired boilers (BLR-S and BLR-N) | Previous test results: BLR-S: 0.08 – 0.19 (11 tests); 5 – 17% (10 tests); BLR-N: 0.09 – 0.14 (3 tests); 1 – 5% (3 tests) |  |
| Interfor Pacific | 18-0005 | 2 wood fired boilers | Common stack – can comply with 0.1 during normal operations. Last results: Boiler 1 – 6% and 0.11; Boiler 2 – 2% and 0.15 | Already does a lot of maintenance and tuning, needs controls |
| Frank Lumber | 22-2525 | HFB w/multiclones | 0.137 source test | Need natural gas or ESP, cannot be tuned any better, talked about adding small supplemental NG boiler 10/10/89 0.19 gr/dscf 8/5/97 0.178 gr/dscf 8/17/04 0.137 gr/dscf 8/25/09 0.137 gr/dscf In 1999, changed fuel auger from a hydraulic drive to variable speed drive and reconnected overfire air system. In 2000, changed fuel screen size to 3 inches to keep large hunks from getting in boiler. Seems to have helped PM emissions but didn’t reduce the CO emissions. |
| Swanson Group Roseburg | 10-0030 | Wood fired boiler | 0.17 at 26,800 #/hr steam | > 26,800 then NG boiler starts up |
| Harney Rock and Paving | 13-0010 | Asphalt plant | 19% and 0.22 (1999 source test) | Old asphalt plant with scrubber, would probably scrap because hardly ever runs and has other asphalt plants |
| Rogers Asphalt Paving | 31-0001 | Asphalt plant | 0.11 source test |  |