## Boiler MACT summary
Emission Limits for Existing Boilers (Units with heat input capacity of 10 million Btu per hour or greater)
|  | PM |  |  |  | HCl |  |  |  | Hg |  |  |  | CO |  |  |  | D/F
Fuel | Boiler | NACAA | Original | Major | Area | NACAA | Original | Major | Area | NACAA | Original | Major | Area | NACAA | Original | Major | Area | NACAA | Original | Major | Area
Type | Type | lbs/MMBtu | lbs/MMBtu | lbs/MMBtu | lbs/MMBtu | lbs/MMBtu | lbs/MMBtu | lbs/MMBtu | lbs/MMBtu | lbs/MMBtu | lbs/MMBtu | lbs/MMBtu | lbs/MMBtu | ppm | ppm | ppm | ppm | ng/dscm | ng/dscm | ng/dscm | ng/dscm
Coal |  | 0.008-0.012 | 0.07 | 0.02 | None | 0.015-0.030 | 0.09 | 0.02 |  | 4.5E-06-7.5E-06 | 9e-07 | 3e-06 | 3e-06 | 35-60 | None |  | 310
Coal | Pulverized | [14 empty] | 90 |  | None | None | 0.004
Coal | Stoker | [14 empty] | 50 |  | None | None | 0.003
Coal | Fluidized Bed | [14 empty] | 30 |  | None | None | 0.002
Biomass |  | 0.01-0.02 | 0.07 | 0.02 | None | 0.006-0.012 | 0.09 | 0.006 |  | 2.5E-06-4.5E-06 | None | 9e-07 |  | 100-150 | None |  | 160
Biomass | Stoker | [14 empty] | 560 |  | None | None | 0.004
Biomass | Fluidized Bed | [14 empty] | 250 |  | None | None | 0.02
Biomass | Suspension/Dutch Oven | [14 empty] | 1010 |  | None | None | 0.03
Biomass | Fuel Cells | [14 empty] | 270 |  | None | None | 0.02
Liquid |  | 0.015-0.025 | None | 0.004 | None | 0.006 | 0.09 | 0.0009 |  | None | None | 4e-06 |  | 3-10 | None | 1 | 2 | None | None | 0.002
Other Gases* |  | None | None | 0.05 | None | None | None | 3e-06 |  | None | None | 2e-07 |  | 3-10 | None | 1 |  | None | None | 0.009
*Does not include natural gas or refinery gas

## Convert to Grain Loading
| PM |  |  | PM
Fuel Type | NACAA | Original | Major | Major
| lbs/MMBtu | lbs/MMBtu | lbs/MMBtu | gr/dscf
Coal | 0.008-0.012 | 0.07 | 0.02 | 0.011542
Biomass | 0.01-0.02 | 0.07 | 0.02 | 0.01085
Liquid | 0.015-0.025 | None | 0.004 | 0.0026415
Other Gases* | None | None | 0.05
*Does not include natural gas or refinery gas
Combustion Data: | Fuel Gas | Fuel Oil | Coal
Higher heating value, Btu / scf | 1093
Higher heating value, Btu / gallon |  | 150000
Higher heating value, Btu / pound |  |  | 8020
Amount of dry exhaust gas, scf / MMBtu of fuel | 9510 | 10600 | 12130
CO2 in dry exhaust gas, volume % | 10.8 | 14.0 | 15.5
O2 in dry exhaust gas, volume % | 2.5 | 2.9 | 3.8
Molecular weight of dry exhaust gas | 29.9 | 30.4 | 30.8
http://www.air-dispersion.com/formulas.html#flow
Combustion air and flue gas for some common fuel gases, solids and fluids are indicated in the table below:
Fuel | Theoretical air for combustion |  | Theoretical flue gas
| Volume at standard pressure |  | Volume at standard pressure
Solids | (m3/kg) | (ft3/lb) | (m3/kg) | (ft3/lb)
Anthracite | 9.4 | 150 | 9.5 | 152
Bituminous coal | 6.9 | 110 | 7 | 112
Lignite | 5.7 | 92 | 8.4 | 93
Wood (dry) | 4.4 | 70 | 5 | 80
Gas | (m3air/m3fuel) | (ft3air/ft3fuel) | (m3air/m3fuel) | (ft3air/ft3fuel)
Butane C4H10 | 31 | 31 | 27 | 27
Natural gas | 9.5 | 9.5 | 8.5 | 8.5
Propane C3H8 | 24 | 24 | 22 | 22
Fluids | (m3air/literfuel) | (ft3air/galfuel) | (m3air/literfuel) | (ft3air/galfuel)
Gas oil | 9.8 | 1570 | 10.4 | 1670
Heavy fuel oil | 10.8 | 1730 | 11.6 | 1860
http://www.engineeringtoolbox.com/fuels-air-flue-gas-d_170.html
Fuel | Higher Calorific Value
(Gross Calorific Value - GCV)
| kJ/kg | Btu/lb
Anthracite | 32,500 - 34,000 | 14,000 - 14,500
Bituminous coal | 17,000 - 23,250 | 7,300 - 10,000
Coal | 15,000 - 27,000 | 8,000 - 14,000
Diesel | 44800 | 19300
Gasoline | 47300 | 20400
Methane | 55530
Petroleum | 43000
Propane | 50350
Wood (dry) | 14,400 - 17,400 | 6,200 - 7,500 | Use 6,200 Btu/lb wood
| kJ/l | Btu/gal
Gas oil | 38000 | 164000
Heavy fuel oil | 41200 | 177000
Kerosene | 35000 | 154000
1 kJ/kg = 0.4299 Btu/ lbm = 0.23884 kcal/kg
1 Btu/lbm = 2.326 kJ/kg = 1.8 kcal/kg
http://www.engineeringtoolbox.com/fuels-higher-calorific-values-d_169.html