## Grain Loading
GRAIN LOADING TEST RESULTS
Rosboro Springfield | Opacity (%) | Grain Loading (gr/dscf, if boiler then @ 12% C02)
2006-07-31 | 0% |  | wood boilers
2003-02-04 | 2% | 0.061 | wood boilers
2002-07-18 | 0% |  | wood boilers
1993-08-06 | None recorded | 0.07 | wood boilers
Rosboro Vaughn
2007-10-23 | 8% |  | wood boiler
2001-09-06 | 10% |  | wood boiler
2002-08-28 | 20% | 0.0575 | wood boiler
2000-02-23 | 17% |  | wood boiler
1998-02-13 |  | 0.099 | wood boiler
Swanson Group
2004-02-19 | 0% | 0.073 | wood boiler w/ multiclone
2003-03-04 | 5% | 0.115 | wood boiler w/ multiclone
2002-08-28 | 3% | 0.0081 | Dryers 3&4 w/ scrubber
2002-08-28 | 4% | 0.013 | Dryers 1&2 w/scrubber
2000-09-21 | 0% | 0.021 | Veneer dryer w/scrubber
Emerald Plant 1
2000-10-03 | 5% | 0.032 | Veneer Dryer w/burley scrubber
Emerald Plant 3
2003-11-18 | 0% | NA
Egge Asphalt
2007-10-11 | 0% | 0.029 | No RAP
EWEB
2008-02-11 |  | 0.0003 | 120 MMBtu/hr boiler on No.2 oil
Flakeboard
2003-06-26 | 0% | 0.0116 | Dryer 1, Stack 1 on sanderdust w/WESP
2003-06-26 | 0% | 0.0097 | Dryer 1, Stack 2 on sanderdust
2003-06-24 | 0% | 0.0072 | Dryer 1 on natural gas w/WESP
2003-06-27 | 0% | 0.0004 | Dryer 2 on sanderdust w/baghouse
2007-08-02 | 0% | 0.0146 | Boiler 2, baghouse on sanderdust and natural gas
Jasper Wood Products
2005-02-28
Murphy Panelboard (GP)
2001-12-18 |  | 0.026 | Veneer Dryer w/burley scrubber
2001-12-18 |  | 0.4449 | West Heat Cell at 12% CO2 (0.1 gr/dscf limit)
2002-04-24 | 4% | 0.2405 | West Heat Cell at 12% CO2
2003-08-26 | NA | 0.0063 | West Heat Cell at 12% CO2 (installed WESP under compliance order)
Natron (Timber)
2000-02-15 | 5% | 0.034 | Veneer Dryer w/burley scrubber
Sierra Pine
2000-07-18 |  | 0.006 | Press 44.2
2000-07-19 |  | 0.008 | Press 45.2
2000-07-19 |  | 0.008 | Press 45.4
2000-07-21 |  | 0.008 | Mec 3 Dryer, 0.2 gr permit limit
2001-10-30 |  | 0.004 | Mec 1 Dryer, 0.2 gr permit limit
2001-10-31 |  | 0.018 | Mec 2 Dryer, 0.2 gr permit limit
2001-10-31 |  | 0.009 | Mec 3 Dryer, 0.2 gr permit limit
2001-11-01 |  | 0.008 | Mec 4 Dryer, 0.2 gr permit limit
2001-10-31 |  | 0.004 | Press 45.1, 0.2 gr permit limit
2001-10-31 |  | 0.0087 | Press 45.2, 0.2 gr permit limit
2001-11-01 |  | 0.0061 | Press 45.3, 0.2 gr permit limit
2001-11-01 |  | 0.0039 | Press 45.4, 0.2 gr permit limit
2001-11-02 |  | 0.0123 | Press 45.6, 0.2 gr permit limit
2006-12-14 | 0% | 0.008 | Mec 1 WESP
2006-12-13 |  | 0.0112 | Mec 3 WESP
2006-12-12 | 1.04% | 0.0139 | Mec 4 WESP
2006-12-05 |  | 0.0094 | Press 2 (45.5)
2006-12-05 |  | 0.0074 | Press 2 (45.6)
2002-07-09 | 0% | 0.009 | Press 2 (44.2)
2002-07-09 | 0% | 0.008 | Press 2 (44.3)
2002-07-09 | 0% | 0.004 | Press 2 (44.4)
2006-06-06 | 0.49% | 0.0015 | Press-2 baghouse 45.2
2006-06-06 | 1% | 0.0009 | Press-2 baghouse 45.3
States Industries
2006-01-17 |  | 0.021 | Veneer Dryer, Enid Rd
2006-01-17 |  | 0.014 | Veneer Dryer, Foch St.
2002-04-15 |  | 0.021 | Cyclone No. 1
Trus Joist Eugene and Junction City
2004-02-18 | 0% | 0.0019 | Veneer Dryer w/RTO
1999-07-29 | 0% | 0.068 | Veneer Dryer w/RTO
1999-12-02 | 0% | 0.0007 | Baghouse no.1
1999-12-02 | 0% | 3.5e-05 | Clark Baghouse no. 3
1998-05-05 | 0% | 0.00041 | Baghouse no.1
2003-04-30 | 0% | 0.0037 | Junction City RTO on veneer dryer
2007-09-12 | 0% | 0.0054 | Junction City RTO on veneer dryer
Pacific States (Willamette, Weyco)
1998-06-02 |  | 0.053 | Veneer Dryer 1, heart
1998-06-02 |  | 0.035 | Veneer Dryer 1, Sap
1998-06-01 |  | 0.02 | Veneer Dryer 2, Heart
1998-06-01 |  | 0.015 | Veneer Dryer 2, Sap
1997-08-14 |  | 0.008 | Veneer Dryer RTO
2001-06-14 | 0% | 0.0029 | Veneer Dryer RTO
2001-06-14 |  | 0.0985 | Veneer Dryer 1
2001-06-14 |  | 0.045 | Veneer Dryer 2
Oregon Industrial Lumber
1978-12-07 | 5% | 0.05 | Wood-fired boiler, natural draft, no controls
Westwood Lumber Saginaw
2007-03-13 |  | 0.017 | wood-fired boiler w/ multi clone and baghouse
Widish Asphalt
1998-06-11 |  | 0.088 | hot mix asphalt plant w/wet scrubber

## Hog Fuel Boilers
Wood-fired Boilers
Facility | Control Device | EU Descr. | Test Result
Rosboro Sprngfld | Integral Multiclones | Three Hog-fueld Boilers | < 10% based on several tests
Rosboro Vaughn | Multiclone | Hog-fueled Boiler | < 20% based on several tests
Swanson Group | Multiclone | Hog-fueled Boiler | <10% based on several tests
Oregon Industrial Lumber | None | Hog-fueled Boiler | <10% 8/17/00, 5/4/04 and 7/27/05 JM inspections
Weyco Coburg | WESP | Hog-fueled Boiler | 20% limit | Note: 0.05 gr/dscf BACT limit
American Laminators | Multiclone and Wet Scrubber | Hog-fueled Boiler | 20% limit | <5% several JM inspections
Jasper Wood Products | Baghouse | Hog-fueled Boiler | 20% limit | 15% May 2008 JM inspection
Seneca Sustainable E | WESP, SNCR | Hog-fueled Boiler | 20% limit | not yet in operation
Westwood Lumber Saginaw | Multiclone and baghouse | Hog-fueled Boiler | 20% limit
Weyco Hardwoods Prarie Rd | Baghouse | Hog-fueled Boiler | 20% limit
BOILERS
Rosboro Springfield | Opacity (%) | Grain Loading (gr/dscf@ 12% C02)
July 31, August 1, 2006 | 0%
2003-02-04 | 2% | 0.061
2002-07-18 | 0%
1993-08-06 | None recorded | 0.07
Rosboro Vaughn
2007-10-23 | 8%
2001-09-06 | 10%
2002-08-28 | 20% | 0.0575
2000-02-23 | 17%
1998-02-13 |  | 0.099
Swanson Group
2004-02-19 | 0% | 0.073
2003-03-04 | 5% | 0.115
2002-02-28 | 3% | 0.1
2000-09-21 | 0% | 0.021
Oregon Industrial Lumber
1978-12-07 | 5% | 0.05
Westwood Lumber Saginaw
2007-03-13 |  | 0.017 | wood-fired boiler w/ multi clone and baghouse