## NOTES
Notes
Cells are password protected so that the formulas are not accidentialy changed. PASSWORD= qwer1234

## Jan, 2021
January, 2021
Filters | [15 empty] | Rain | Cl2 | Pump Hours | [8 empty] | Chemicals | [5 empty] | Misc. |  |  | Turbidity
Day |  | CW.Tot.1 | Cla.Wst.1 | BW.Wst.1 | FTWst.1 | CW.Tot.2 | Cla.Wst.2 | BW.Wst.2 | FTWst.2 | Treated Total | Wastewater | Total Influent | Totalizer |  |  | Inches | Resid | Pump | Ef.Pmp.1 | Ef.Pmp.2 | Blo.1 | Blo.2 | URT.1 | URT.2 | BWP | SWP | Chem | ACH | SA | Poly | Cl2.1 | Cl2.2 | water | Temp | pH | F1 |  | F2
1 | Pres. | 82533900 | 741666 | 1593980 | 2895670 | 94605300 | 865284 | 2892860 | 4744520 | 924800 | 80644 | 1005444 | now | 940847500 |  | 0.45 | 1.02 | now | 1110 | 1274.5 | 12.7 | 23.1 | 1163.6 | 1360.3 | 28.1 | 3.9 | "/lb | 2 | 8.75 | 1.75 | 9 | 0 | Raw | 11.2 | 7.58 | ef.turb.1 | 0 | ef.turb.2 | 0.042
| Prev | 82533900 | 741666 | 1593980 | 2895670 | 93680500 | 857640 | 2860630 | 4703750 |  |  |  | prev | 939973300 |  |  |  | prev | 1110 | 1263.1 | 12.5 | 23 | 1163.6 | 1348.4 | 27.9 | 3.9 | Lbs. | 21.48 | 19.25 | 0.4375 | 9 |  | Trtd | 8.7 | 7.8 | AC.1 | 0 | AC.2 | 0.658
| Total | 0 | 0 | 0 | 0 | 924800 | 7644 | 32230 | 40770 |  |  |  | Total | 874200 |  |  |  | Total | 0 | 11.4 | 0.2 | 0.1 | 0 | 11.9 | 0.2 | 0 | mg/L | 2.785 | 2.4958 | 0.056724 | 1.1669 |  |  |  |  | Raw.Trb. | 2.28 | Cmb.Trb. | 0.034
2 | Pres. | 82533900 | 741666 | 1593980 | 2895670 | 95331200 | 872827 | 2892860 | 4752620 | 725900 | 15643 | 741543 | now | 941643500 |  | 0.57 | 1.01 | now | 1110 | 1283.3 | 12.8 | 23.1 | 1163.6 | 1369.3 | 28.1 | 3.9 | "/lb | 2 | 7.25 | 1.25 | 7 | 0 | Raw | 11.6 | 7.57 | ef.turb.1 | 0 | ef.turb.2 | 0.043
| Prev | 82533900 | 741666 | 1593980 | 2895670 | 94605300 | 865284 | 2892860 | 4744520 |  |  |  | prev | 940847500 |  |  |  | prev | 1110 | 1274.5 | 12.7 | 23.1 | 1163.6 | 1360.3 | 28.1 | 3.9 | Lbs. | 21.48 | 15.95 | 0.3125 | 7 |  | Trtd | 9.1 | 7.79 | AC.1 | 0 | AC.2 | 0.78
| Total | 0 | 0 | 0 | 0 | 725900 | 7543 | 0 | 8100 |  |  |  | Total | 796000 |  |  |  | Total | 0 | 8.8 | 0.1 | 0 | 0 | 9 | 0 | 0 | mg/L | 3.5481 | 2.6346 | 0.051619 | 1.1563 |  |  |  |  | Raw.Trb. | 3.34 | Cmb.Trb. | 0.038
10.6
3 | Pres. | 82533900 | 741666 | 1593980 | 2895670 | 96157900 | 887879 | 2925280 | 4815060 | 826700 | 109912 | 936612 | now | 942594300 |  | 0.77 | 1.01 | now | 1110 | 1297.6 | 13 | 23.3 | 1163.6 | 1384.7 | 28.1 | 3.9 | "/lb | 1.25 | 7.25 | 2.125 | 12 | 0 | Raw | 10.6 | 7.48 | ef.turb.1 | 0 | ef.turb.2 | 0.05
| Prev | 82533900 | 741666 | 1593980 | 2895670 | 95331200 | 872827 | 2892860 | 4752620 |  |  |  | prev | 941643500 |  |  |  | prev | 1110 | 1283.3 | 12.8 | 23.1 | 1163.6 | 1369.3 | 28.1 | 3.9 | Lbs. | 13.425 | 15.95 | 0.53125 | 12 |  | Trtd | 9.5 | 7.76 | AC.1 | 0 | AC.2 | 3.59
| Total | 0 | 0 | 0 | 0 | 826700 | 15052 | 32420 | 62440 |  |  |  | Total | 950800 |  |  |  | Total | 0 | 14.3 | 0.2 | 0.2 | 0 | 15.4 | 0 | 0 | mg/L | 1.9472 | 2.3134 | 0.077052 | 1.7405 |  |  |  |  | Raw.Trb. | 52.87 | Cmb.Trb. | 0.04
4 | Pres. | 82533900 | 741666 | 1593980 | 2895670 | 96935900 | 903021 | 2982810 | 4871390 | 778000 | 129002 | 907002 | now | 943474200 |  | 0.63 | 1.05 | now | 1110 | 1307.2 | 13.2 | 23.4 | 1163.6 | 1395.1 | 28.6 | 3.9 | "/lb | 1.625 | 7.5 | 1.625 | 8 | 0 | Raw | 11.5 | 7.46 | ef.turb.1 | 0 | ef.turb.2 | 0.045
| Prev | 82533900 | 741666 | 1593980 | 2895670 | 96157900 | 887879 | 2925280 | 4815060 |  |  |  | prev | 942594300 |  |  |  | prev | 1110 | 1297.6 | 13 | 23.3 | 1163.6 | 1384.7 | 28.1 | 3.9 | Lbs. | 17.4525 | 16.5 | 0.40625 | 8 |  | Trtd | 9.7 | 7.09 | AC.1 | 0 | AC.2 | 1.555
| Total | 0 | 0 | 0 | 0 | 778000 | 15142 | 57530 | 56330 |  |  |  | Total | 879900 |  |  |  | Total | 0 | 9.6 | 0.2 | 0.1 | 0 | 10.4 | 0.5 | 0 | mg/L | 2.6898 | 2.543 | 0.062611 | 1.2329 |  |  |  |  | Raw.Trb. | 7.12 | Cmb.Trb. | 0.038
5 | Pres. | 82533900 | 741666 | 1593980 | 2895670 | 97862400 | 918717 | 3015360 | 4975670 | 926500 | 152526 | 1079026 | now | 944388800 | 0 | 0.14 | 1.06 | now | 1110 | 1318.6 | 13.4 | 23.6 | 1163.6 | 1407.9 | 28.8 | 3.9 | "/lb | 2.5 | 9 | 1.875 | 10 | 0 | Raw | 10.2 | 7.56 | ef.turb.1 | 0 | ef.turb.2 | 0.043
| Prev | 82533900 | 741666 | 1593980 | 2895670 | 96935900 | 903021 | 2982810 | 4871390 |  |  |  | prev | 943474200 |  |  |  | prev | 1110 | 1307.2 | 13.2 | 23.4 | 1163.6 | 1395.1 | 28.6 | 3.9 | Lbs. | 26.85 | 19.8 | 0.46875 | 10 |  | Trtd | 10.8 | 7.17 | AC.1 | 0 | AC.2 | 1.365
| Total | 0 | 0 | 0 | 0 | 926500 | 15696 | 32550 | 104280 |  |  |  | Total | 914600 |  |  |  | Total | 0 | 11.4 | 0.2 | 0.2 | 0 | 12.8 | 0.2 | 0 | mg/L | 3.4748 | 2.5624 | 0.060664 | 1.2942 |  |  |  |  | Raw.Trb. | 6.48 | Cmb.Trb. | 0.036
6 | Pres. | 82533900 | 741666 | 1593980 | 2895670 | 98643100 | 926598 | 3047870 | 5040840 | 780700 | 105561 | 886261 | now | 945308900 |  | 0.68 | 1.03 | now | 1110 | 1328 | 13.6 | 23.7 | 1163.6 | 1418.3 | 29 | 3.9 | "/lb | 1.9375 | 7.5 | 1.625 | 8 | 0 | Raw | 11.3 | 7.48 | ef.turb.1 | 0 | ef.turb.2 | 0.043
| Prev | 82533900 | 741666 | 1593980 | 2895670 | 97862400 | 918717 | 3015360 | 4975670 |  |  |  | prev | 944388800 |  |  |  | prev | 1110 | 1318.6 | 13.4 | 23.6 | 1163.6 | 1407.9 | 28.8 | 3.9 | Lbs. | 20.8087 | 16.5 | 0.40625 | 8 |  | Trtd | 11.7 | 7.15 | AC.1 | 0 | AC.2 | 1.546
| Total | 0 | 0 | 0 | 0 | 780700 | 7881 | 32510 | 65170 |  |  |  | Total | 920100 |  |  |  | Total | 0 | 9.4 | 0.2 | 0.1 | 0 | 10.4 | 0.2 | 0 | mg/L | 3.1959 | 2.5342 | 0.062394 | 1.2287 |  |  |  |  | Raw.Trb. | 9.12 | Cmb.Trb. | 0.036
7 | Pres. | 82533900 | 741666 | 1593980 | 2895670 | 99476000 | 934442 | 3080060 | 5106960 | 832900 | 106154 | 939054 | now | 946222400 |  | 0.14 | 1.08 | now | 1110 | 1338.2 | 13.7 | 23.9 | 1163.6 | 1429.4 | 29.1 | 3.9 | "/lb | 2.125 | 8 | 1.625 | 8 | 0 | Raw | 11.3 | 7.55 | ef.turb.1 | 0 | ef.turb.2 | 0.042
| Prev | 82533900 | 741666 | 1593980 | 2895670 | 98643100 | 926598 | 3047870 | 5040840 |  |  |  | prev | 945308900 |  |  |  | prev | 1110 | 1328 | 13.6 | 23.7 | 1163.6 | 1418.3 | 29 | 3.9 | Lbs. | 22.8225 | 17.6 | 0.40625 | 8 |  | Trtd | 11.2 | 7.34 | AC.1 | 0 | AC.2 | 1.049
| Total | 0 | 0 | 0 | 0 | 832900 | 7844 | 32190 | 66120 |  |  |  | Total | 913500 |  |  |  | Total | 0 | 10.2 | 0.1 | 0.2 | 0 | 11.1 | 0.1 | 0 | mg/L | 3.2855 | 2.5337 | 0.058484 | 1.1517 |  |  |  |  | Raw.Trb. | 3.52 | Cmb.Trb. | 0.035
8 | Pres. | 82533900 | 741666 | 1593980 | 2895670 | 100293000 | 942299 | 3112430 | 5154030 | 817000 | 87297 | 904297 | now | 947135200 |  | 0.01 | 1.08 | now | 1110 | 1348.3 | 13.8 | 23.9 | 1163.6 | 1440.1 | 29.3 | 3.9 | "/lb | 1.9375 | 8 | 1.625 | 8 | 0 | Raw | 10.8 | 7.53 | ef.turb.1 | 0 | ef.turb.2 | 0.044
| Prev | 82533900 | 741666 | 1593980 | 2895670 | 99476000 | 934442 | 3080060 | 5106960 |  |  |  | prev | 946222400 |  |  |  | prev | 1110 | 1338.2 | 13.7 | 23.9 | 1163.6 | 1429.4 | 29.1 | 3.9 | Lbs. | 20.8087 | 17.6 | 0.40625 | 8 |  | Trtd | 11 | 7.44 | AC.1 | 0 | AC.2 | 0.814
| Total | 0 | 0 | 0 | 0 | 817000 | 7857 | 32370 | 47070 |  |  |  | Total | 912800 |  |  |  | Total | 0 | 10.1 | 0.1 | 0 | 0 | 10.7 | 0.2 | 0 | mg/L | 3.0539 | 2.583 | 0.059622 | 1.1741 |  |  |  |  | Raw.Trb. | 3.3 | Cmb.Trb. | 0.035
9 | Pres. | 82533900 | 741666 | 1593980 | 2895670 | 101104000 | 957431 | 3112430 | 5162120 | 811000 | 23222 | 834222 | now | 948052900 |  | 0.15 | 1.1 | now | 1110 | 1358.2 | 13.8 | 24.2 | 1163.6 | 1450.3 | 29.3 | 3.9 | "/lb | 1.5 | 7.9375 | 1.5 | 8 | 0 | Raw | 9.9 | 7.62 | ef.turb.1 | 0 | ef.turb.2 | 0.042
| Prev | 82533900 | 741666 | 1593980 | 2895670 | 100293000 | 942299 | 3112430 | 5154030 |  |  |  | prev | 947135200 |  |  |  | prev | 1110 | 1348.3 | 13.8 | 23.9 | 1163.6 | 1440.1 | 29.3 | 3.9 | Lbs. | 16.11 | 17.4625 | 0.375 | 8 |  | Trtd | 10.1 | 7.51 | AC.1 | 0 | AC.2 | 0.838
| Total | 0 | 0 | 0 | 0 | 811000 | 15132 | 0 | 8090 |  |  |  | Total | 917700 |  |  |  | Total | 0 | 9.9 | 0 | 0.3 | 0 | 10.2 | 0 | 0 | mg/L | 2.3818 | 2.5818 | 0.055443 | 1.1828 |  |  |  |  | Raw.Trb. | 2.87 | Cmb.Trb. | 0.037
10 | Pres. | 82533900 | 741666 | 1593980 | 2895670 | 102045000 | 965824 | 3144770 | 5162120 | 941000 | 40733 | 981733 | now | 948933700 |  | 0.02 | 1.05 | now | 1110 | 1369.7 | 14 | 24.2 | 1163.6 | 1462.8 | 29.5 | 3.9 | "/lb | 1.75 | 9 | 1.875 | 10 | 0 | Raw | 11 | 7.58 | ef.turb.1 | 0 | ef.turb.2 | 0.042
| Prev | 82533900 | 741666 | 1593980 | 2895670 | 101104000 | 957431 | 3112430 | 5162120 |  |  |  | prev | 948052900 |  |  |  | prev | 1110 | 1358.2 | 13.8 | 24.2 | 1163.6 | 1450.3 | 29.3 | 3.9 | Lbs. | 18.795 | 19.8 | 0.46875 | 10 |  | Trtd | 9.9 | 7.52 | AC.1 | 0 | AC.2 | 0.777
| Total | 0 | 0 | 0 | 0 | 941000 | 8393 | 32340 | 0 |  |  |  | Total | 880800 |  |  |  | Total | 0 | 11.5 | 0.2 | 0 | 0 | 12.5 | 0.2 | 0 | mg/L | 2.3949 | 2.523 | 0.059729 | 1.2742 |  |  |  |  | Raw.Trb. | 2.96 | Cmb.Trb. | 0.033
11 | Pres. | 82533900 | 741666 | 1593980 | 2895670 | 102865000 | 973686 | 3177170 | 5300930 | 820000 | 179072 | 999072 | now | 949763900 |  | 0.3 | 1.07 | now | 1110 | 1379.8 | 14.1 | 24.4 | 1163.6 | 1473.7 | 29.7 | 3.9 | "/lb | 1.75 | 8.25 | 1.75 | 7 | 0 | Raw | 11.1 | 7.61 | ef.turb.1 | 0 | ef.turb.2 | 0.039
| Prev | 82533900 | 741666 | 1593980 | 2895670 | 102045000 | 965824 | 3144770 | 5162120 |  |  |  | prev | 948933700 |  |  |  | prev | 1110 | 1369.7 | 14 | 24.2 | 1163.6 | 1462.8 | 29.5 | 3.9 | Lbs. | 18.795 | 18.15 | 0.4375 | 7 |  | Trtd | 9 | 7.64 | AC.1 | 0 | AC.2 | 0.888
| Total | 0 | 0 | 0 | 0 | 820000 | 7862 | 32400 | 138810 |  |  |  | Total | 830200 |  |  |  | Total | 0 | 10.1 | 0.1 | 0.2 | 0 | 10.9 | 0.2 | 0 | mg/L | 2.7483 | 2.654 | 0.063973 | 1.0236 |  |  |  |  | Raw.Trb. | 2.42 | Cmb.Trb. | 0.032
12 | Pres. | 82673200 | 749636 | 1593980 | 2905010 | 103549000 | 1012230 | 3206010 | 5368990 | 823300 | 152754 | 976054 | now | 950637600 |  | 0.86 | 1.06 | now | 1112.2 | 1390.2 | 14.5 | 24.8 | 1166.1 | 1485.7 | 29.9 | 3.9 | "/lb | 3.5 | 8.5 | 2.25 | 7 | 1 | Raw | 11.9 | 7.59 | ef.turb.1 | 0.048 | ef.turb.2 | 0.041
| Prev | 82533900 | 741666 | 1593980 | 2895670 | 102865000 | 973686 | 3177170 | 5300930 |  |  |  | prev | 949763900 |  |  |  | prev | 1110 | 1379.8 | 14.1 | 24.4 | 1163.6 | 1473.7 | 29.7 | 3.9 | Lbs. | 37.59 | 18.7 | 0.5625 | 8 |  | Trtd | 10.7 | 7.75 | AC.1 | 1.271 | AC.2 | 2.156
| Total | 139300 | 7970 | 0 | 9340 | 684000 | 38544 | 28840 | 68060 |  |  |  | Total | 873700 |  |  |  | Total | 2.2 | 10.4 | 0.4 | 0.4 | 2.5 | 12 | 0.2 | 0 | mg/L | 5.4745 | 2.7234 | 0.081922 | 1.1651 |  |  |  |  | Raw.Trb. | 11.86 | Cmb.Trb. | 0.045
13 | Pres. | 82673200 | 749636 | 1593980 | 2905010 | 104318000 | 1020050 | 3234810 | 5419980 | 769000 | 87610 | 856610 | now | 951475900 |  | 0 | 0.98 | now | 1112.2 | 1402.3 | 14.7 | 24.9 | 1166.1 | 1498.6 | 30 | 3.9 | "/lb | 1.625 | 9.5 | 2.0625 | 9 | 0 | Raw | 13.3 | 6.78 | ef.turb.1 | 0 | ef.turb.2 | 0.044
| Prev | 82673200 | 749636 | 1593980 | 2905010 | 103549000 | 1012230 | 3206010 | 5368990 |  |  |  | prev | 950637600 |  |  |  | prev | 1112.2 | 1390.2 | 14.5 | 24.8 | 1166.1 | 1485.7 | 29.9 | 3.9 | Lbs. | 17.4525 | 20.9 | 0.51562 | 9 |  | Trtd | 11.7 | 7.37 | AC.1 | 0 | AC.2 | 2.702
| Total | 0 | 0 | 0 | 0 | 769000 | 7820 | 28800 | 50990 |  |  |  | Total | 838300 |  |  |  | Total | 0 | 12.1 | 0.2 | 0.1 | 0 | 12.9 | 0.1 | 0 | mg/L | 2.7212 | 3.2588 | 0.080397 | 1.4033 |  |  |  |  | Raw.Trb. | 13.44 | Cmb.Trb. | 0.04
14 | Pres. | 82673200 | 749636 | 1593980 | 2905010 | 105091000 | 1074480 | 3267120 | 5472100 | 773000 | 138860 | 911860 | now | 952353600 |  | 0.2 | 0.99 | now | 1112.2 | 1412.2 | 14.9 | 25.7 | 1166.1 | 1509.9 | 30.2 | 3.9 | "/lb | 1.75 | 7.5 | 1.75 | 7 | 0 | Raw | 12 | 6.78 | ef.turb.1 | 0 | ef.turb.2 | 0.048
| Prev | 82673200 | 749636 | 1593980 | 2905010 | 104318000 | 1020050 | 3234810 | 5419980 |  |  |  | prev | 951475900 |  |  |  | prev | 1112.2 | 1402.3 | 14.7 | 24.9 | 1166.1 | 1498.6 | 30 | 3.9 | Lbs. | 18.795 | 16.5 | 0.4375 | 7 |  | Trtd | 10.5 | 7.11 | AC.1 | 0 | AC.2 | 0.433
| Total | 0 | 0 | 0 | 0 | 773000 | 54430 | 32310 | 52120 |  |  |  | Total | 877700 |  |  |  | Total | 0 | 9.9 | 0.2 | 0.8 | 0 | 11.3 | 0.2 | 0 | mg/L | 2.9154 | 2.5594 | 0.067863 | 1.0858 |  |  |  |  | Raw.Trb. | 1.75 | Cmb.Trb. | 0.045
15 | Pres. | 82673200 | 749636 | 1593980 | 2905010 | 105841000 | 1090010 | 3267120 | 5488310 | 750000 | 31740 | 781740 | now | 953403300 |  | 0.01 | 1.03 | now | 1112.2 | 1421.3 | 15.1 | 25.7 | 1166.1 | 1519.4 | 30.2 | 3.9 | "/lb | 1.875 | 7.75 | 1.8125 | 7 | 0 | Raw | 10.7 | 7.36 | ef.turb.1 | 0 | ef.turb.2 | 0.055
| Prev | 82673200 | 749636 | 1593980 | 2905010 | 105091000 | 1074480 | 3267120 | 5472100 |  |  |  | prev | 952353600 |  |  |  | prev | 1112.2 | 1412.2 | 14.9 | 25.7 | 1166.1 | 1509.9 | 30.2 | 3.9 | Lbs. | 20.1375 | 17.05 | 0.45312 | 7 |  | Trtd | 10.6 | 7.13 | AC.1 | 0 | AC.2 | 1.603
| Total | 0 | 0 | 0 | 0 | 750000 | 15530 | 0 | 16210 |  |  |  | Total | 1049700 |  |  |  | Total | 0 | 9.1 | 0.2 | 0 | 0 | 9.5 | 0 | 0 | mg/L | 3.2194 | 2.7258 | 0.072442 | 1.1191 |  |  |  |  | Raw.Trb. | 7.51 | Cmb.Trb. | 0.049
16 | Pres. | 82673200 | 749636 | 1593980 | 2905010 | 106683000 | 1097840 | 3299560 | 5564280 | 842000 | 116240 | 958240 | now | 954193400 |  | 0.1 | 1.01 | now | 1112.2 | 1431.6 | 15.3 | 25.7 | 1166.1 | 1530.8 | 30.2 | 3.9 | "/lb | 1.625 | 8.25 | 1.75 | 9 | 0 | Raw | 10.9 | 7.57 | ef.turb.1 | 0 | ef.turb.2 | 0.038
| Prev | 82673200 | 749636 | 1593980 | 2905010 | 105841000 | 1090010 | 3267120 | 5488310 |  |  |  | prev | 953403300 |  |  |  | prev | 1112.2 | 1421.3 | 15.1 | 25.7 | 1166.1 | 1519.4 | 30.2 | 3.9 | Lbs. | 17.4525 | 18.15 | 0.4375 | 9 |  | Trtd | 9.6 | 7.34 | AC.1 | 0 | AC.2 | 0.807
| Total | 0 | 0 | 0 | 0 | 842000 | 7830 | 32440 | 75970 |  |  |  | Total | 790100 |  |  |  | Total | 0 | 10.3 | 0.2 | 0 | 0 | 11.4 | 0 | 0 | mg/L | 2.4853 | 2.5846 | 0.062302 | 1.2816 |  |  |  |  | Raw.Trb. | 3.59 | Cmb.Trb. | 0.033
17 | Pres. | 82673200 | 749636 | 1593980 | 2905010 | 107391000 | 1105650 | 3299560 | 5572330 | 708000 | 15860 | 723860 | now | 955057400 |  | 0 | 0.98 | now | 1112.2 | 1440.2 | 15.3 | 25.9 | 1166.1 | 1539.6 | 30.4 | 3.9 | "/lb | 1.25 | 6.75 | 1.375 | 6 | 0 | Raw | 10.4 | 7.46 | ef.turb.1 | 0 | ef.turb.2 | 0.042
| Prev | 82673200 | 749636 | 1593980 | 2905010 | 106683000 | 1097840 | 3299560 | 5564280 |  |  |  | prev | 954193400 |  |  |  | prev | 1112.2 | 1431.6 | 15.3 | 25.7 | 1166.1 | 1530.8 | 30.2 | 3.9 | Lbs. | 13.425 | 14.85 | 0.34375 | 6 |  | Trtd | 9.8 | 7.33 | AC.1 | 0 | AC.2 | 0.869
| Total | 0 | 0 | 0 | 0 | 708000 | 7810 | 0 | 8050 |  |  |  | Total | 864000 |  |  |  | Total | 0 | 8.6 | 0 | 0.2 | 0 | 8.8 | 0.2 | 0 | mg/L | 2.2736 | 2.5149 | 0.058216 | 1.0161 |  |  |  |  | Raw.Trb. | 3.16 | Cmb.Trb. | 0.037
18 | Pres. | 82673200 | 749636 | 1593980 | 2905010 | 108312000 | 1115680 | 3299560 | 5580390 | 921000 | 18090 | 939090 | now | 955904600 |  | 0 | 0.99 | now | 1112.2 | 1451.3 | 15.3 | 26 | 1166.1 | 1551 | 30.4 | 3.9 | "/lb | 1.625 | 9 | 1.875 | 9 | 0 | Raw | 10.3 | 7.48 | ef.turb.1 | 0 | ef.turb.2 | 0.041
| Prev | 82673200 | 749636 | 1593980 | 2905010 | 107391000 | 1105650 | 3299560 | 5572330 |  |  |  | prev | 955057400 |  |  |  | prev | 1112.2 | 1440.2 | 15.3 | 25.9 | 1166.1 | 1539.6 | 30.4 | 3.9 | Lbs. | 17.4525 | 19.8 | 0.46875 | 9 |  | Trtd | 9.4 | 7.38 | AC.1 | 0 | AC.2 | 0.904
| Total | 0 | 0 | 0 | 0 | 921000 | 10030 | 0 | 8060 |  |  |  | Total | 847200 |  |  |  | Total | 0 | 11.1 | 0 | 0.1 | 0 | 11.4 | 0 | 0 | mg/L | 2.2721 | 2.5777 | 0.061026 | 1.1717 |  |  |  |  | Raw.Trb. | 2.85 | Cmb.Trb. | 0.036
19 | Pres. | 82814100 | 757486 | 1593980 | 2913180 | 109023000 | 1129190 | 3364060 | 5677300 | 851900 | 190940 | 1042840 | now | 956816900 |  | 0 | 1.02 | now | 1114.2 | 1460.4 | 15.6 | 26.2 | 1168.4 | 1561.4 | 30.8 | 3.9 | "/lb | 1.75 | 8.75 | 1.875 | 7 | 0 | Raw | 9.3 | 7.49 | ef.turb.1 | 0 | ef.turb.2 | 0.04
| Prev | 82673200 | 749636 | 1593980 | 2905010 | 108312000 | 1115680 | 3299560 | 5580390 |  |  |  | prev | 955904600 |  |  |  | prev | 1112.2 | 1451.3 | 15.3 | 26 | 1166.1 | 1551 | 30.4 | 3.9 | Lbs. | 18.795 | 19.25 | 0.46875 | 7 |  | Trtd | 8.6 | 7.49 | AC.1 | 0 | AC.2 | 0.71
| Total | 140900 | 7850 | 0 | 8170 | 711000 | 13510 | 64500 | 96910 |  |  |  | Total | 912300 |  |  |  | Total | 2 | 9.1 | 0.3 | 0.2 | 2.3 | 10.4 | 0.4 | 0 | mg/L | 2.6454 | 2.7094 | 0.065976 | 0.98524 |  |  |  |  | Raw.Trb. | 2.91 | Cmb.Trb. | 0.032
20 | Pres. | 82942400 | 757486 | 1666580 | 2966200 | 110013000 | 1144180 | 3428610 | 5756760 | 1118300 | 284620 | 1402920 | now | 957862500 |  | 0.06 | 0.98 | now | 1116.4 | 1472.7 | 15.8 | 26.6 | 1171.4 | 1575.5 | 31.5 | 4 | "/lb | 2.125 | 11.375 | 2.5 | 10 | 1 | Raw | 8.7 | 7.62 | ef.turb.1 | 0 | ef.turb.2 | 0.048
| Prev | 82814100 | 757486 | 1593980 | 2913180 | 109023000 | 1129190 | 3364060 | 5677300 |  |  |  | prev | 956816900 |  |  |  | prev | 1114.2 | 1460.4 | 15.6 | 26.2 | 1168.4 | 1561.4 | 30.8 | 3.9 | Lbs. | 22.8225 | 25.025 | 0.625 | 11 |  | Trtd | 9.3 | 7.42 | AC.1 | 0 | AC.2 | 0.702
| Total | 128300 | 0 | 72600 | 53020 | 990000 | 14990 | 64550 | 79460 |  |  |  | Total | 1045600 |  |  |  | Total | 2.2 | 12.3 | 0.2 | 0.4 | 3 | 14.1 | 0.7 | 0.1 | mg/L | 2.447 | 2.6832 | 0.067012 | 1.1794 |  |  |  |  | Raw.Trb. | 2.28 | Cmb.Trb. | 0.039
21 | Pres. | 82985700 | 757486 | 1666580 | 2966200 | 110486000 | 1151970 | 3428610 | 5764810 | 516300 | 15840 | 532140 | now | 958554900 |  | 0 | 0.97 | now | 1117.2 | 1478.4 | 15.8 | 26.7 | 1172.2 | 1581.4 | 31.5 | 4 | "/lb | 0.875 | 5.25 | 1 | 5 | 1 | Raw | 10.7 | 7.43 | ef.turb.1 | 0.046 | ef.turb.2 | 0.045
| Prev | 82942400 | 757486 | 1666580 | 2966200 | 110013000 | 1144180 | 3428610 | 5756760 |  |  |  | prev | 957862500 |  |  |  | prev | 1116.4 | 1472.7 | 15.8 | 26.6 | 1171.4 | 1575.5 | 31.5 | 4 | Lbs. | 9.3975 | 11.55 | 0.25 | 6 |  | Trtd | 10.5 | 7.7 | AC.1 | 0.791 | AC.2 | 0.764
| Total | 43300 | 0 | 0 | 0 | 473000 | 7790 | 0 | 8050 |  |  |  | Total | 692400 |  |  |  | Total | 0.8 | 5.7 | 0 | 0.1 | 0.8 | 5.9 | 0 | 0 | mg/L | 2.1824 | 2.6823 | 0.058059 | 1.3934 |  |  |  |  | Raw.Trb. | 1.34 | Cmb.Trb. | 0.042
22 | Pres. | 82985700 | 757486 | 1666580 | 2966200 | 111371000 | 1159810 | 3460620 | 5801030 | 885000 | 76070 | 961070 | now | 959500900 |  | 0 | 1.02 | now | 1117.2 | 1489.2 | 16 | 26.8 | 1172.2 | 1592.8 | 31.7 | 4 | "/lb | 1.5 | 8.5 | 2.25 | 8 | 0 | Raw | 10.5 | 7.42 | ef.turb.1 | 0 | ef.turb.2 | 0.041
| Prev | 82985700 | 757486 | 1666580 | 2966200 | 110486000 | 1151970 | 3428610 | 5764810 |  |  |  | prev | 958554900 |  |  |  | prev | 1117.2 | 1478.4 | 15.8 | 26.7 | 1172.2 | 1581.4 | 31.5 | 4 | Lbs. | 16.11 | 18.7 | 0.5625 | 8 |  | Trtd | 11.3 | 7.69 | AC.1 | 0 | AC.2 | 0.785
| Total | 0 | 0 | 0 | 0 | 885000 | 7840 | 32010 | 36220 |  |  |  | Total | 946000 |  |  |  | Total | 0 | 10.8 | 0.2 | 0.1 | 0 | 11.4 | 0.2 | 0 | mg/L | 2.1827 | 2.5336 | 0.07621 | 1.0839 |  |  |  |  | Raw.Trb. | 2.03 | Cmb.Trb. | 0.036
23 | Pres. | 82985700 | 757486 | 1666580 | 2966200 | 112249000 | 1167640 | 3460620 | 5809040 | 878000 | 15840 | 893840 | now | 960416100 |  | 0.02 | 1.04 | now | 1117.2 | 1499.2 | 16.1 | 26.8 | 1172.2 | 1603.7 | 31.7 | 4 | "/lb | 1.25 | 8.5 | 1.75 | 8 | 0 | Raw | 8.7 | 7.15 | ef.turb.1 | 0 | ef.turb.2 | 0.048
| Prev | 82985700 | 757486 | 1666580 | 2966200 | 111371000 | 1159810 | 3460620 | 5801030 |  |  |  | prev | 959500900 |  |  |  | prev | 1117.2 | 1489.2 | 16 | 26.8 | 1172.2 | 1592.8 | 31.7 | 4 | Lbs. | 13.425 | 18.7 | 0.4375 | 8 |  | Trtd | 10.1 | 7.39 | AC.1 | 0 | AC.2 | 0.812
| Total | 0 | 0 | 0 | 0 | 878000 | 7830 | 0 | 8010 |  |  |  | Total | 915200 |  |  |  | Total | 0 | 10 | 0.1 | 0 | 0 | 10.9 | 0 | 0 | mg/L | 1.8334 | 2.5538 | 0.059747 | 1.0925 |  |  |  |  | Raw.Trb. | 1.99 | Cmb.Trb. | 0.042
24 | Pres. | 82985700 | 757486 | 1666580 | 2966200 | 113194000 | 1175460 | 3492610 | 5881620 | 945000 | 112390 | 1057390 | now | 961323900 |  | 0.3 | 1.08 | now | 1117.2 | 1511.5 | 16.1 | 26.9 | 1172.2 | 1616.2 | 31.8 | 4 | "/lb | 1.625 | 9.25 | 2 | 9 | 0 | Raw | 8.9 | 7.56 | ef.turb.1 | 0 | ef.turb.2 | 0.038
| Prev | 82985700 | 757486 | 1666580 | 2966200 | 112249000 | 1167640 | 3460620 | 5809040 |  |  |  | prev | 960416100 |  |  |  | prev | 1117.2 | 1499.2 | 16.1 | 26.8 | 1172.2 | 1603.7 | 31.7 | 4 | Lbs. | 17.4525 | 20.35 | 0.5 | 9 |  | Trtd | 9.1 | 7.84 | AC.1 | 0 | AC.2 | 0.614
| Total | 0 | 0 | 0 | 0 | 945000 | 7820 | 31990 | 72580 |  |  |  | Total | 907800 |  |  |  | Total | 0 | 12.3 | 0 | 0.1 | 0 | 12.5 | 0.1 | 0 | mg/L | 2.2144 | 2.5821 | 0.063441 | 1.1419 |  |  |  |  | Raw.Trb. | 1.63 | Cmb.Trb. | 0.032
25 | Pres. | 82985700 | 757486 | 1666580 | 2966200 | 113866000 | 1183300 | 3524980 | 5937280 | 672000 | 95870 | 767870 | now | 962147700 |  | 0 | 1.17 | now | 1117.2 | 1519.7 | 16.1 | 27.1 | 1172.2 | 1625.2 | 32 | 4 | "/lb | 1.25 | 7.25 | 1.5 | 7 | 0 | Raw | 8.4 | 7.56 | ef.turb.1 | 0 | ef.turb.2 | 0.037
| Prev | 82985700 | 757486 | 1666580 | 2966200 | 113194000 | 1175460 | 3492610 | 5881620 |  |  |  | prev | 961323900 |  |  |  | prev | 1117.2 | 1511.5 | 16.1 | 26.9 | 1172.2 | 1616.2 | 31.8 | 4 | Lbs. | 13.425 | 15.95 | 0.375 | 7 |  | Trtd | 7.1 | 7.79 | AC.1 | 0 | AC.2 | 0.723
| Total | 0 | 0 | 0 | 0 | 672000 | 7840 | 32370 | 55660 |  |  |  | Total | 823800 |  |  |  | Total | 0 | 8.2 | 0 | 0.2 | 0 | 9 | 0.2 | 0 | mg/L | 2.3954 | 2.8459 | 0.066911 | 1.249 |  |  |  |  | Raw.Trb. | 2.01 | Cmb.Trb. | 0.034
26 | Pres. | 84053900 | 765631 | 1702980 | 3045860 | 113866000 | 1183300 | 3524980 | 5937280 | 1068200 | 124205 | 1192405 | now | 963065300 |  | 0.19 | 1.09 | now | 1130.2 | 1519.7 | 16.3 | 27.1 | 1186.3 | 1625.2 | 32.2 | 4.1 | "/lb | 1.75 | 10 | 2 | 0 | 9 | Raw | 8.7 | 7.61 | ef.turb.1 | 0.05 | ef.turb.2 | 0
| Prev | 82985700 | 757486 | 1666580 | 2966200 | 113866000 | 1183300 | 3524980 | 5937280 |  |  |  | prev | 962147700 |  |  |  | prev | 1117.2 | 1519.7 | 16.1 | 27.1 | 1172.2 | 1625.2 | 32 | 4 | Lbs. | 18.795 | 22 | 0.5 | 9 |  | Trtd | 7 | 7.78 | AC.1 | 0.795 | AC.2 | 0
| Total | 1068200 | 8145 | 36400 | 79660 | 0 | 0 | 0 | 0 |  |  |  | Total | 917600 |  |  |  | Total | 13 | 0 | 0.2 | 0 | 14.1 | 0 | 0.2 | 0.1 | mg/L | 2.1097 | 2.4695 | 0.056124 | 1.0102 |  |  |  |  | Raw.Trb. | 1.89 | Cmb.Trb. | 0.05
27 | Pres. | 84053900 | 765631 | 1702980 | 3045860 | 114576000 | 1198950 | 3557380 | 5997400 | 710000 | 108170 | 818170 | now | 963957200 |  | 0.06 | 1.07 | now | 1130.2 | 1528.4 | 16.6 | 27.2 | 1186.3 | 1634.8 | 32.4 | 4.1 | "/lb | 0.875 | 6.625 | 1.625 | 6 | 0 | Raw | 9.2 | 7.41 | ef.turb.1 | 0 | ef.turb.2 | 0.045
| Prev | 84053900 | 765631 | 1702980 | 3045860 | 113866000 | 1183300 | 3524980 | 5937280 |  |  |  | prev | 963065300 |  |  |  | prev | 1130.2 | 1519.7 | 16.3 | 27.1 | 1186.3 | 1625.2 | 32.2 | 4.1 | Lbs. | 9.3975 | 14.575 | 0.40625 | 6 |  | Trtd | 8.7 | 7.74 | AC.1 | 0 | AC.2 | 0.783
| Total | 0 | 0 | 0 | 0 | 710000 | 15650 | 32400 | 60120 |  |  |  | Total | 891900 |  |  |  | Total | 0 | 8.7 | 0.3 | 0.1 | 0 | 9.6 | 0.2 | 0 | mg/L | 1.587 | 2.4614 | 0.068607 | 1.0133 |  |  |  |  | Raw.Trb. | 1.91 | Cmb.Trb. | 0.043
28 | Pres. | 84053900 | 765631 | 1702980 | 3045860 | 115388000 | 1206770 | 3557380 | 6005530 | 812000 | 15950 | 827950 | now | 964849800 |  | 0.04 | 1.06 | now | 1130.2 | 1538.3 | 16.6 | 27.3 | 1186.3 | 1644.8 | 32.4 | 4.1 | "/lb | 1.625 | 8 | 1.625 | 7 | 0 | Raw | 9.9 | 7.62 | ef.turb.1 | 0 | ef.turb.2 | 0.04
| Prev | 84053900 | 765631 | 1702980 | 3045860 | 114576000 | 1198950 | 3557380 | 5997400 |  |  |  | prev | 963957200 |  |  |  | prev | 1130.2 | 1528.4 | 16.6 | 27.2 | 1186.3 | 1634.8 | 32.4 | 4.1 | Lbs. | 17.4525 | 17.6 | 0.40625 | 7 |  | Trtd | 9.2 | 7.77 | AC.1 | 0 | AC.2 | 0.857
| Total | 0 | 0 | 0 | 0 | 812000 | 7820 | 0 | 8130 |  |  |  | Total | 892600 |  |  |  | Total | 0 | 9.9 | 0 | 0.1 | 0 | 10 | 0 | 0 | mg/L | 2.5771 | 2.5989 | 0.059989 | 1.0337 |  |  |  |  | Raw.Trb. | 1.73 | Cmb.Trb. | 0.037
29 | Pres. | 84053900 | 765631 | 1702980 | 3045860 | 116250000 | 1214620 | 3589650 | 6049400 | 862000 | 83990 | 945990 | now | 965692900 |  | 0.04 | 1.08 | now | 1130.2 | 1548.8 | 16.8 | 27.4 | 1186.3 | 1656 | 32.6 | 4.1 | "/lb | 1.75 | 8.25 | 2.25 | 7 | 0 | Raw | 10.3 | 7.64 | ef.turb.1 | 0 | ef.turb.2 | 0.037
| Prev | 84053900 | 765631 | 1702980 | 3045860 | 115388000 | 1206770 | 3557380 | 6005530 |  |  |  | prev | 964849800 |  |  |  | prev | 1130.2 | 1538.3 | 16.6 | 27.3 | 1186.3 | 1644.8 | 32.4 | 4.1 | Lbs. | 18.795 | 18.15 | 0.5625 | 7 |  | Trtd | 9.4 | 7.72 | AC.1 | 0 | AC.2 | 0.711
| Total | 0 | 0 | 0 | 0 | 862000 | 7850 | 32270 | 43870 |  |  |  | Total | 843100 |  |  |  | Total | 0 | 10.5 | 0.2 | 0.1 | 0 | 11.2 | 0.2 | 0 | mg/L | 2.6144 | 2.5247 | 0.078244 | 0.9737 |  |  |  |  | Raw.Trb. | 1.71 | Cmb.Trb. | 0.033
30 | Pres. | 84053900 | 765631 | 1702980 | 3045860 | 116978000 | 1214620 | 3589650 | 6057520 | 728000 | 8120 | 736120 | now | 966601900 |  | 0.12 | 1.01 | now | 1130.2 | 1557.7 | 16.8 | 27.4 | 1186.3 | 1664.9 | 32.6 | 4.1 | "/lb | 1.125 | 7 | 1.625 | 6 | 0 | Raw | 10.4 | 7.52 | ef.turb.1 | 0 | ef.turb.2 | 0.045
| Prev | 84053900 | 765631 | 1702980 | 3045860 | 116250000 | 1214620 | 3589650 | 6049400 |  |  |  | prev | 965692900 |  |  |  | prev | 1130.2 | 1548.8 | 16.8 | 27.4 | 1186.3 | 1656 | 32.6 | 4.1 | Lbs. | 12.0825 | 15.4 | 0.40625 | 6 |  | Trtd | 7.3 | 7.87 | AC.1 | 0 | AC.2 | 0.778
| Total | 0 | 0 | 0 | 0 | 728000 | 0 | 0 | 8120 |  |  |  | Total | 909000 |  |  |  | Total | 0 | 8.9 | 0 | 0 | 0 | 8.9 | 0 | 0 | mg/L | 1.99 | 2.5364 | 0.066911 | 0.98822 |  |  |  |  | Raw.Trb. | 1.69 | Cmb.Trb. | 0.045
31 | Pres. | 84053900 | 765631 | 1702980 | 3045860 | 118015000 | 1222440 | 3654230 | 6109890 | 1037000 | 124770 | 1161770 | now | 967445500 |  | 0.07 | 1.01 | now | 1130.2 | 1570.4 | 17 | 27.5 | 1186.3 | 1678.3 | 32.9 | 4.1 | "/lb | 2.25 | 9.875 | 2.5 | 9 | 0 | Raw | 10.2 | 7.67 | ef.turb.1 | 0 | ef.turb.2 | 0.035
| Prev | 84053900 | 765631 | 1702980 | 3045860 | 116978000 | 1214620 | 3589650 | 6057520 |  |  |  | prev | 966601900 |  |  |  | prev | 1130.2 | 1557.7 | 16.8 | 27.4 | 1186.3 | 1664.9 | 32.6 | 4.1 | Lbs. | 24.165 | 21.725 | 0.625 | 9 |  | Trtd | 8.8 | 7.71 | AC.1 | 0 | AC.2 | 0.881
| Total | 0 | 0 | 0 | 0 | 1037000 | 7820 | 64580 | 52370 |  |  |  | Total | 843600 |  |  |  | Total | 0 | 12.7 | 0.2 | 0.1 | 0 | 13.4 | 0.3 | 0 | mg/L | 2.7941 | 2.512 | 0.072266 | 1.0406 |  |  |  |  | Raw.Trb. | 2.17 | Cmb.Trb. | 0.032
[10 empty] | Totals | [6 empty] | AVG | [10 empty] | totals | [5 empty] | AVG TRTD |  |  |  | Avg.Cmb.Trb.
[10 empty] | 25854500 | 2847695 | 28702195 |  | 27472200 |  | 5.93 | 1.0387 | [5 empty] | 22.7 | 329.9 |  |  |  | 573.2475 | 559.4875 | 14 | 250 |  |  | 9.6581 | 7.5332 |  |  | 0.037935
[22 empty] | total- | 352.6

## Feb, 2021
February, 2021
Filters | [15 empty] | Rain | Cl2 | Pump Hours | [8 empty] | Chemicals | [5 empty] | Misc. |  |  | Turbidity
Day |  | CW.Tot.1 | Cla.Wst.1 | BW.Wst.1 | FTWst.1 | CW.Tot.2 | Cla.Wst.2 | BW.Wst.2 | FTWst.2 | Treated Total | Wastewater | Total Influent | Totalizer |  |  | Inches | Resid | Pump | Ef.Pmp.1 | Ef.Pmp.2 | Blo.1 | Blo.2 | URT.1 | URT.2 | BWP | SWP | Chem | ACH | SA | Poly | Cl2.1 | Cl2.2 | water | Temp | pH | F1 |  | F2
1 | Pres. | 84053900 | 765631 | 1702980 | 3045860 | 118820000 | 1230270 | 3712320 | 6173550 | 805000 | 129580 | 934580 | now | 968362000 |  | 0.46 | 0.99 | now | 1130.2 | 1580.4 | 17.3 | 27.6 | 1186.3 | 1689.1 | 33.3 | 4.1 | "/lb | 1.875 | 7.75 | 1.875 | 7 | 0 | Raw | 10.9 | 7.6 | ef.turb.1 | 0 | ef.turb.2 | 0.053
| Prev | 84053900 | 765631 | 1702980 | 3045860 | 118015000 | 1222440 | 3654230 | 6109890 |  |  |  | prev | 967445500 |  |  |  | prev | 1130.2 | 1570.4 | 17 | 27.5 | 1186.3 | 1678.3 | 32.9 | 4.1 | Lbs. | 20.1375 | 17.05 | 0.46875 | 7 |  | Trtd | 8.5 | 7.91 | AC.1 | 0 | AC.2 | 0.558
| Total | 0 | 0 | 0 | 0 | 805000 | 7830 | 58090 | 63660 |  |  |  | Total | 916500 |  |  |  | Total | 0 | 10 | 0.3 | 0.1 | 0 | 10.8 | 0.4 | 0 | mg/L | 2.9995 | 2.5396 | 0.06982 | 1.0426 |  |  |  |  | Raw.Trb. | 1.91 | Cmb.Trb. | 0.055
2 | Pres. | 84053900 | 765631 | 1702980 | 3045860 | 119504000 | 1238140 | 3712320 | 6181580 | 684000 | 15900 | 699900 | now | 969129600 |  | 0.37 | 1 | now | 1130.2 | 1588.6 | 17.4 | 27.6 | 1186.3 | 1697.6 | 33.3 | 4.1 | "/lb | 1.875 | 6.9375 | 1.5 | 7 | 0 | Raw | 10.2 | 7.48 | ef.turb.1 | 0 | ef.turb.2 | 0.045
| Prev | 84053900 | 765631 | 1702980 | 3045860 | 118820000 | 1230270 | 3712320 | 6173550 |  |  |  | prev | 968362000 |  |  |  | prev | 1130.2 | 1580.4 | 17.3 | 27.6 | 1186.3 | 1689.1 | 33.3 | 4.1 | Lbs. | 20.1375 | 15.2625 | 0.375 | 7 |  | Trtd | 9.9 | 7.64 | AC.1 | 0 | AC.2 | 0.894
| Total | 0 | 0 | 0 | 0 | 684000 | 7870 | 0 | 8030 |  |  |  | Total | 767600 |  |  |  | Total | 0 | 8.2 | 0.1 | 0 | 0 | 8.5 | 0 | 0 | mg/L | 3.5301 | 2.6755 | 0.065737 | 1.2271 |  |  |  |  | Raw.Trb. | 3.43 | Cmb.Trb. | 0.042
10.6
3 | Pres. | 84053900 | 765631 | 1702980 | 3045860 | 120345000 | 1245510 | 3744750 | 6234790 | 841000 | 93010 | 934010 | now | 970003700 |  | 0 | 1.07 | now | 1130.2 | 1598.9 | 17.5 | 27.8 | 1186.3 | 1708.6 | 33.4 | 4.1 | "/lb | 2.375 | 8.125 | 1.875 | 9 | 0 | Raw | 9.3 | 7.67 | ef.turb.1 | 0 | ef.turb.2 | 0.038
| Prev | 84053900 | 765631 | 1702980 | 3045860 | 119504000 | 1238140 | 3712320 | 6181580 |  |  |  | prev | 969129600 |  |  |  | prev | 1130.2 | 1588.6 | 17.4 | 27.6 | 1186.3 | 1697.6 | 33.3 | 4.1 | Lbs. | 25.5075 | 17.875 | 0.46875 | 9 |  | Trtd | 9.6 | 7.8 | AC.1 | 0 | AC.2 | 1.272
| Total | 0 | 0 | 0 | 0 | 841000 | 7370 | 32430 | 53210 |  |  |  | Total | 874100 |  |  |  | Total | 0 | 10.3 | 0.1 | 0.2 | 0 | 11 | 0.1 | 0 | mg/L | 3.6367 | 2.5485 | 0.066831 | 1.2832 |  |  |  |  | Raw.Trb. | 5.37 | Cmb.Trb. | 0.034
4 | Pres. | 84053900 | 765631 | 1702980 | 3045860 | 120982000 | 1253380 | 3744750 | 6242920 | 637000 | 16000 | 653000 | now | 970838600 |  | 0.02 | 1.11 | now | 1130.2 | 1606.7 | 17.6 | 27.9 | 1186.3 | 1716.7 | 33.4 | 4.1 | "/lb | 1.25 | 6.125 | 1.75 | 6 | 0 | Raw | 11 | 7.72 | ef.turb.1 | 0 | ef.turb.2 | 0.041
| Prev | 84053900 | 765631 | 1702980 | 3045860 | 120345000 | 1245510 | 3744750 | 6234790 |  |  |  | prev | 970003700 |  |  |  | prev | 1130.2 | 1598.9 | 17.5 | 27.8 | 1186.3 | 1708.6 | 33.4 | 4.1 | Lbs. | 13.425 | 13.475 | 0.4375 | 6 |  | Trtd | 9.7 | 7.68 | AC.1 | 0 | AC.2 | 1.463
| Total | 0 | 0 | 0 | 0 | 637000 | 7870 | 0 | 8130 |  |  |  | Total | 834900 |  |  |  | Total | 0 | 7.8 | 0.1 | 0.1 | 0 | 8.1 | 0 | 0 | mg/L | 2.527 | 2.5364 | 0.082352 | 1.1294 |  |  |  |  | Raw.Trb. | 3.35 | Cmb.Trb. | 0.036
5 | Pres. | 84053900 | 765631 | 1702980 | 3045860 | 121854000 | 1261230 | 3777110 | 6301430 | 872000 | 98720 | 970720 | now | 971697500 | 0 | 0 | 1.1 | now | 1130.2 | 1617.3 | 17.6 | 28.1 | 1186.3 | 1728.2 | 33.6 | 4.1 | "/lb | 1.875 | 8.19 | 2.0625 | 8 | 0 | Raw | 10.1 | 7.66 | ef.turb.1 | 0 | ef.turb.2 | 0.037
| Prev | 84053900 | 765631 | 1702980 | 3045860 | 120982000 | 1253380 | 3744750 | 6242920 |  |  |  | prev | 970838600 |  |  |  | prev | 1130.2 | 1606.7 | 17.6 | 27.9 | 1186.3 | 1716.7 | 33.4 | 4.1 | Lbs. | 20.1375 | 18.018 | 0.51562 | 8 |  | Trtd | 9.7 | 7.83 | AC.1 | 0 | AC.2 | 1.299
| Total | 0 | 0 | 0 | 0 | 872000 | 7850 | 32360 | 58510 |  |  |  | Total | 858900 |  |  |  | Total | 0 | 10.6 | 0 | 0.2 | 0 | 11.5 | 0.2 | 0 | mg/L | 2.769 | 2.4776 | 0.070901 | 1.1 |  |  |  |  | Raw.Trb. | 2.66 | Cmb.Trb. | 0.033
6 | Pres. | 84053900 | 765631 | 1702980 | 3045860 | 122778000 | 1269100 | 3809390 | 6346790 | 924000 | 85510 | 1009510 | now | 972618700 |  | 0.03 | 1.07 | now | 1130.2 | 1628.7 | 17.8 | 28.2 | 1186.3 | 1740.1 | 33.8 | 4.1 | "/lb | 1.875 | 8.9375 | 2 | 9 | 0 | Raw | 10.4 | 7.67 | ef.turb.1 | 0 | ef.turb.2 | 0.04
| Prev | 84053900 | 765631 | 1702980 | 3045860 | 121854000 | 1261230 | 3777110 | 6301430 |  |  |  | prev | 971697500 |  |  |  | prev | 1130.2 | 1617.3 | 17.6 | 28.1 | 1186.3 | 1728.2 | 33.6 | 4.1 | Lbs. | 20.1375 | 19.6625 | 0.5 | 9 |  | Trtd | 8.9 | 7.97 | AC.1 | 0 | AC.2 | 0.987
| Total | 0 | 0 | 0 | 0 | 924000 | 7870 | 32280 | 45360 |  |  |  | Total | 921200 |  |  |  | Total | 0 | 11.4 | 0.2 | 0.1 | 0 | 11.9 | 0.2 | 0 | mg/L | 2.6132 | 2.5515 | 0.064883 | 1.1679 |  |  |  |  | Raw.Trb. | 2.8 | Cmb.Trb. | 0.036
7 | Pres. | 84053900 | 765631 | 1702980 | 3045860 | 123577000 | 1276950 | 3841450 | 6392080 | 799000 | 85200 | 884200 | now | 973429400 |  | 0 | 1.11 | now | 1130.2 | 1638.5 | 17.9 | 28.3 | 1186.3 | 1750.5 | 34 | 4.1 | "/lb | 1.625 | 7.75 | 1.625 | 7 | 0 | Raw | 10.3 | 7.68 | ef.turb.1 | 0 | ef.turb.2 | 0.038
| Prev | 84053900 | 765631 | 1702980 | 3045860 | 122778000 | 1269100 | 3809390 | 6346790 |  |  |  | prev | 972618700 |  |  |  | prev | 1130.2 | 1628.7 | 17.8 | 28.2 | 1186.3 | 1740.1 | 33.8 | 4.1 | Lbs. | 17.4525 | 17.05 | 0.40625 | 7 |  | Trtd | 9.2 | 7.76 | AC.1 | 0 | AC.2 | 0.817
| Total | 0 | 0 | 0 | 0 | 799000 | 7850 | 32060 | 45290 |  |  |  | Total | 810700 |  |  |  | Total | 0 | 9.8 | 0.1 | 0.1 | 0 | 10.4 | 0.2 | 0 | mg/L | 2.6191 | 2.5587 | 0.060965 | 1.0505 |  |  |  |  | Raw.Trb. | 1.95 | Cmb.Trb. | 0.033
8 | Pres. | 84053900 | 765631 | 1702980 | 3045860 | 124174000 | 1284110 | 3841450 | 6407400 | 597000 | 22480 | 619480 | now | 974310000 |  | 0 | 1.07 | now | 1130.2 | 1645.7 | 17.9 | 28.5 | 1186.3 | 1758.1 | 34 | 4.1 | "/lb | 1.25 | 7.375 | 1.625 | 6 | 0 | Raw | 9.6 | 7.62 | ef.turb.1 | 0 | ef.turb.2 | 0.038
| Prev | 84053900 | 765631 | 1702980 | 3045860 | 123577000 | 1276950 | 3841450 | 6392080 |  |  |  | prev | 973429400 |  |  |  | prev | 1130.2 | 1638.5 | 17.9 | 28.3 | 1186.3 | 1750.5 | 34 | 4.1 | Lbs. | 13.425 | 16.225 | 0.40625 | 6 |  | Trtd | 8.1 | 7.99 | AC.1 | 0 | AC.2 | 0.621
| Total | 0 | 0 | 0 | 0 | 597000 | 7160 | 0 | 15320 |  |  |  | Total | 880600 |  |  |  | Total | 0 | 7.2 | 0 | 0.2 | 0 | 7.6 | 0 | 0 | mg/L | 2.6963 | 3.2587 | 0.081593 | 1.2051 |  |  |  |  | Raw.Trb. | 1.84 | Cmb.Trb. | 0.032
9 | Pres. | 84428800 | 773362 | 1702980 | 3089340 | 125001000 | 1284110 | 3873300 | 6454310 | 1201900 | 129971 | 1331871 | now | 975207000 |  | 0 | 1.03 | now | 1135.5 | 1655.8 | 18.1 | 28.5 | 1192.3 | 1768.8 | 34.2 | 4.1 | "/lb | 1.625 | 10.5 | 2.25 | 9 | 1 | Raw | 8.9 | 7.72 | ef.turb.1 | 0 | ef.turb.2 | 0.037
| Prev | 84053900 | 765631 | 1702980 | 3045860 | 124174000 | 1284110 | 3841450 | 6407400 |  |  |  | prev | 974310000 |  |  |  | prev | 1130.2 | 1645.7 | 17.9 | 28.5 | 1186.3 | 1758.1 | 34 | 4.1 | Lbs. | 17.4525 | 23.1 | 0.5625 | 10 |  | Trtd | 9.1 | 7.87 | AC.1 | 0 | AC.2 | 0.763
| Total | 374900 | 7731 | 0 | 43480 | 827000 | 0 | 31850 | 46910 |  |  |  | Total | 897000 |  |  |  | Total | 5.3 | 10.1 | 0.2 | 0 | 6 | 10.7 | 0.2 | 0 | mg/L | 1.7411 | 2.3045 | 0.056116 | 0.99762 |  |  |  |  | Raw.Trb. | 1.89 | Cmb.Trb. | 0.032
10 | Pres. | 84672900 | 773362 | 1739770 | 3101850 | 125772000 | 1291930 | 3905460 | 6528610 | 1015100 | 163580 | 1178680 | now | 976209300 |  | 0.02 | 1.06 | now | 1138.4 | 1665.2 | 18.2 | 28.5 | 1195.4 | 1779.4 | 34.5 | 4.1 | "/lb | 1.625 | 9.75 | 2.25 | 9 | 0 | Raw | 8.9 | 7.65 | ef.turb.1 | 0.035 | ef.turb.2 | 0
| Prev | 84428800 | 773362 | 1702980 | 3089340 | 125001000 | 1284110 | 3873300 | 6454310 |  |  |  | prev | 975207000 |  |  |  | prev | 1135.5 | 1655.8 | 18.1 | 28.5 | 1192.3 | 1768.8 | 34.2 | 4.1 | Lbs. | 17.4525 | 21.45 | 0.5625 | 9 |  | Trtd | 9.2 | 7.87 | AC.1 | 0.787 | AC.2 | 0
| Total | 244100 | 0 | 36790 | 12510 | 771000 | 7820 | 32160 | 74300 |  |  |  | Total | 1002300 |  |  |  | Total | 2.9 | 9.4 | 0.1 | 0 | 3.1 | 10.6 | 0.3 | 0 | mg/L | 2.0615 | 2.5337 | 0.066443 | 1.0631 |  |  |  |  | Raw.Trb. | 1.61 | Cmb.Trb. | 0.034
11 | Pres. | 84672900 | 773362 | 1739770 | 3101850 | 126534000 | 1299750 | 3938090 | 6591360 | 762000 | 103200 | 865200 | now | 977026600 |  | 0.37 | 1.06 | now | 1138.4 | 1674.6 | 18.4 | 28.6 | 1195.4 | 1789.6 | 34.7 | 4.1 | "/lb | 1.375 | 7.25 | 2 | 7 | 0 | Raw | 9.7 | 7.7 | ef.turb.1 | 0 | ef.turb.2 | 0.039
| Prev | 84672900 | 773362 | 1739770 | 3101850 | 125772000 | 1291930 | 3905460 | 6528610 |  |  |  | prev | 976209300 |  |  |  | prev | 1138.4 | 1665.2 | 18.2 | 28.5 | 1195.4 | 1779.4 | 34.5 | 4.1 | Lbs. | 14.7675 | 15.95 | 0.5 | 7 |  | Trtd | 9.4 | 7.66 | AC.1 | 0 | AC.2 | 0.67
| Total | 0 | 0 | 0 | 0 | 762000 | 7820 | 32630 | 62750 |  |  |  | Total | 817300 |  |  |  | Total | 0 | 9.4 | 0.2 | 0.1 | 0 | 10.2 | 0.2 | 0 | mg/L | 2.3237 | 2.5098 | 0.078677 | 1.1015 |  |  |  |  | Raw.Trb. | 2.15 | Cmb.Trb. | 0.035
12 | Pres. | 84672900 | 773362 | 1739770 | 3101850 | 127303000 | 1307610 | 3938090 | 6599150 | 769000 | 15650 | 784650 | now | 977739900 |  | 0.63 | 1.07 | now | 1138.4 | 1683.9 | 18.4 | 28.7 | 1195.4 | 1799.2 | 34.7 | 4.1 | "/lb | 1.125 | 7.5 | 1.5 | 7 | 0 | Raw | 9.5 | 7.68 | ef.turb.1 | 0 | ef.turb.2 | 0.037
| Prev | 84672900 | 773362 | 1739770 | 3101850 | 126534000 | 1299750 | 3938090 | 6591360 |  |  |  | prev | 977026600 |  |  |  | prev | 1138.4 | 1674.6 | 18.4 | 28.6 | 1195.4 | 1789.6 | 34.7 | 4.1 | Lbs. | 12.0825 | 16.5 | 0.375 | 7 |  | Trtd | 8.3 | 7.94 | AC.1 | 0 | AC.2 | 0.649
| Total | 0 | 0 | 0 | 0 | 769000 | 7860 | 0 | 7790 |  |  |  | Total | 713300 |  |  |  | Total | 0 | 9.3 | 0 | 0.1 | 0 | 9.6 | 0 | 0 | mg/L | 1.8839 | 2.5727 | 0.058471 | 1.0915 |  |  |  |  | Raw.Trb. | 1.65 | Cmb.Trb. | 0.037
13 | Pres. | 84747500 | 773362 | 1739770 | 3109260 | 127908000 | 1307610 | 3968950 | 6656400 | 679600 | 95520 | 775120 | now | 978417400 |  | 0.4 | 1.09 | now | 1139.4 | 1691.4 | 18.5 | 28.8 | 1196.5 | 1807.3 | 34.9 | 4.1 | "/lb | 2.5 | 6.5 | 1.5 | 5 | 0 | Raw | 8.2 | 7.61 | ef.turb.1 | 0.062 | ef.turb.2 | 0.043
| Prev | 84672900 | 773362 | 1739770 | 3101850 | 127303000 | 1307610 | 3938090 | 6599150 |  |  |  | prev | 977739900 |  |  |  | prev | 1138.4 | 1683.9 | 18.4 | 28.7 | 1195.4 | 1799.2 | 34.7 | 4.1 | Lbs. | 26.85 | 14.3 | 0.375 | 5 |  | Trtd | 6.7 | 7.91 | AC.1 | 2.9 | AC.2 | 3.8
| Total | 74600 | 0 | 0 | 7410 | 605000 | 0 | 30860 | 57250 |  |  |  | Total | 677500 |  |  |  | Total | 1 | 7.5 | 0.1 | 0.1 | 1.1 | 8.1 | 0.2 | 0 | mg/L | 4.7372 | 2.523 | 0.066162 | 0.88217 |  |  |  |  | Raw.Trb. | 14 | Cmb.Trb. | 0.058
14 | Pres. | 84747500 | 773362 | 1739770 | 3109260 | 128390000 | 1315480 | 3968950 | 6672500 | 482000 | 23970 | 505970 | now | 979096500 |  | 0.28 | 1.01 | now | 1139.4 | 1699.6 | 18.5 | 28.8 | 1196.5 | 1815.9 | 34.9 | 4.1 | "/lb | 1.75 | 6.5 | 1.5 | 6 | 0 | Raw | 8.2 | 7.55 | ef.turb.1 | 0 | ef.turb.2 | 0.056
| Prev | 84747500 | 773362 | 1739770 | 3109260 | 127908000 | 1307610 | 3968950 | 6656400 |  |  |  | prev | 978417400 |  |  |  | prev | 1139.4 | 1691.4 | 18.5 | 28.8 | 1196.5 | 1807.3 | 34.9 | 4.1 | Lbs. | 18.795 | 14.3 | 0.375 | 6 |  | Trtd | 6.5 | 8 | AC.1 | 0 | AC.2 | 2.968
| Total | 0 | 0 | 0 | 0 | 482000 | 7870 | 0 | 16100 |  |  |  | Total | 679100 |  |  |  | Total | 0 | 8.2 | 0 | 0 | 0 | 8.6 | 0 | 0 | mg/L | 4.6755 | 3.5573 | 0.093286 | 1.4926 |  |  |  |  | Raw.Trb. | 8.06 | Cmb.Trb. | 0.05
15 | Pres. | 85145500 | 773362 | 1739770 | 3133170 | 128705000 | 1331000 | 3968950 | 6680480 | 713000 | 47410 | 760410 | now | 980104360 |  | 0.1 | 1.04 | now | 1145.6 | 1705.3 | 18.8 | 28.8 | 1203 | 1821.9 | 34.9 | 4.1 | "/lb | 1.3875 | 9.62 | 2.125 | 10 | 0 | Raw | 9.4 | 7.61 | ef.turb.1 | 0 | ef.turb.2 | 0.038
| Prev | 84747500 | 773362 | 1739770 | 3109260 | 128390000 | 1315480 | 3968950 | 6672500 |  |  |  | prev | 979096500 |  |  |  | prev | 1139.4 | 1699.6 | 18.5 | 28.8 | 1196.5 | 1815.9 | 34.9 | 4.1 | Lbs. | 14.9017 | 21.164 | 0.53125 | 10 |  | Trtd | 8.2 | 7.93 | AC.1 | 0 | AC.2 | 1.33
| Total | 398000 | 0 | 0 | 23910 | 315000 | 15520 | 0 | 7980 |  |  |  | Total | 1007860 |  |  |  | Total | 6.2 | 5.7 | 0.3 | 0 | 6.5 | 6 | 0 | 0 | mg/L | 2.506 | 3.5591 | 0.089339 | 1.6817 |  |  |  |  | Raw.Trb. | 6.68 | Cmb.Trb. | 0.033
16 | Pres. | 85371600 | 780549 | 1802670 | 3156120 | 129214000 | 1338680 | 3999600 | 6709290 | 735100 | 160177 | 895277 | now | 981087300 |  | 0 | 1.11 | now | 1148.6 | 1714.6 | 19 | 28.9 | 1206.5 | 1831.8 | 35.4 | 4.3 | "/lb | 2.0625 | 11.25 | 2.125 | 9 | 0 | Raw | 11 | 6.76 | ef.turb.1 | 0.04 | ef.turb.2 | 0
| Prev | 85145500 | 773362 | 1739770 | 3133170 | 128705000 | 1331000 | 3968950 | 6680480 |  |  |  | prev | 980104360 |  |  |  | prev | 1145.6 | 1705.3 | 18.8 | 28.8 | 1203 | 1821.9 | 34.9 | 4.1 | Lbs. | 22.1513 | 24.75 | 0.53125 | 9 |  | Trtd | 7.7 | 7.3 | AC.1 | 0.295 | AC.2 | 0
| Total | 226100 | 7187 | 62900 | 22950 | 509000 | 7680 | 30650 | 28810 |  |  |  | Total | 982940 |  |  |  | Total | 3 | 9.3 | 0.2 | 0.1 | 3.5 | 9.9 | 0.5 | 0.2 | mg/L | 3.6131 | 4.037 | 0.086654 | 1.468 |  |  |  |  | Raw.Trb. | 1.19 | Cmb.Trb. | 0.038
17 | Pres. | 85426300 | 780549 | 1802670 | 3156120 | 129736000 | 1354270 | 4031570 | 6759990 | 576700 | 98260 | 674960 | now | 982068200 |  | 0 | 1.11 | now | 1149.6 | 1724.2 | 19.2 | 29.1 | 1207.5 | 1842.1 | 35.6 | 4.3 | "/lb | 1.5 | 8.625 | 1.875 | 8 | 0 | Raw | 8.6 | 6.61 | ef.turb.1 | 0.068 | ef.turb.2 | 0.038
| Prev | 85371600 | 780549 | 1802670 | 3156120 | 129214000 | 1338680 | 3999600 | 6709290 |  |  |  | prev | 981087300 |  |  |  | prev | 1148.6 | 1714.6 | 19 | 28.9 | 1206.5 | 1831.8 | 35.4 | 4.3 | Lbs. | 16.11 | 18.975 | 0.46875 | 8 |  | Trtd | 9.8 | 7.43 | AC.1 | 1.381 | AC.2 | 1.104
| Total | 54700 | 0 | 0 | 0 | 522000 | 15590 | 31970 | 50700 |  |  |  | Total | 980900 |  |  |  | Total | 1 | 9.6 | 0.2 | 0.2 | 1 | 10.3 | 0.2 | 0 | mg/L | 3.3495 | 3.9452 | 0.09746 | 1.6633 |  |  |  |  | Raw.Trb. | 4.57 | Cmb.Trb. | 0.046
18 | Pres. | 85426300 | 780549 | 1802670 | 3156120 | 130296000 | 1362110 | 4062650 | 6809370 | 560000 | 88300 | 648300 | now | 982996800 |  | 0.42 | 1.05 | now | 1149.6 | 1734.5 | 19.4 | 29.2 | 1207.5 | 1853.1 | 35.8 | 4.3 | "/lb | 1.75 | 8.25 | 1.875 | 8 | 0 | Raw | 10.1 | 7.65 | ef.turb.1 | 0 | ef.turb.2 | 0.039
| Prev | 85426300 | 780549 | 1802670 | 3156120 | 129736000 | 1354270 | 4031570 | 6759990 |  |  |  | prev | 982068200 |  |  |  | prev | 1149.6 | 1724.2 | 19.2 | 29.1 | 1207.5 | 1842.1 | 35.6 | 4.3 | Lbs. | 18.795 | 18.15 | 0.46875 | 8 |  | Trtd | 9.2 | 7.28 | AC.1 | 0 | AC.2 | 0.92
| Total | 0 | 0 | 0 | 0 | 560000 | 7840 | 31080 | 49380 |  |  |  | Total | 928600 |  |  |  | Total | 0 | 10.3 | 0.2 | 0.1 | 0 | 11 | 0.2 | 0 | mg/L | 4.0243 | 3.8862 | 0.10037 | 1.7129 |  |  |  |  | Raw.Trb. | 2.88 | Cmb.Trb. | 0.034
19 | Pres. | 85426300 | 780549 | 1802670 | 3156120 | 130981000 | 1369820 | 4062650 | 6816560 | 685000 | 14900 | 699900 | now | 983964700 |  | 0.31 | 1.08 | now | 1149.6 | 1747 | 19.4 | 29.3 | 1207.5 | 1865.8 | 35.8 | 4.3 | "/lb | 2.25 | 9.9375 | 2.625 | 9 | 0 | Raw | 9.4 | 7.66 | ef.turb.1 | 0 | ef.turb.2 | 0.039
| Prev | 85426300 | 780549 | 1802670 | 3156120 | 130296000 | 1362110 | 4062650 | 6809370 |  |  |  | prev | 982996800 |  |  |  | prev | 1149.6 | 1734.5 | 19.4 | 29.2 | 1207.5 | 1853.1 | 35.8 | 4.3 | Lbs. | 24.165 | 21.8625 | 0.65625 | 9 |  | Trtd | 9.5 | 7.36 | AC.1 | 0 | AC.2 | 1.013
| Total | 0 | 0 | 0 | 0 | 685000 | 7710 | 0 | 7190 |  |  |  | Total | 967900 |  |  |  | Total | 0 | 12.5 | 0 | 0.1 | 0 | 12.7 | 0 | 0 | mg/L | 4.2299 | 3.8269 | 0.11487 | 1.5754 |  |  |  |  | Raw.Trb. | 4.55 | Cmb.Trb. | 0.034
20 | Pres. | 85426300 | 780549 | 1802670 | 3156120 | 131626000 | 1377710 | 4093680 | 6854450 | 645000 | 76810 | 721810 | now | 984857500 |  | 0 | 1.11 | now | 1149.6 | 1758.8 | 19.6 | 29.4 | 1207.5 | 1878.2 | 35.9 | 4.3 | "/lb | 1.625 | 9.375 | 2 | 8 | 0 | Raw | 10.5 | 7.78 | ef.turb.1 | 0 | ef.turb.2 | 0.037
| Prev | 85426300 | 780549 | 1802670 | 3156120 | 130981000 | 1369820 | 4062650 | 6816560 |  |  |  | prev | 983964700 |  |  |  | prev | 1149.6 | 1747 | 19.4 | 29.3 | 1207.5 | 1865.8 | 35.8 | 4.3 | Lbs. | 17.4525 | 20.625 | 0.5 | 8 |  | Trtd | 8.4 | 7.52 | AC.1 | 0 | AC.2 | 0.756
| Total | 0 | 0 | 0 | 0 | 645000 | 7890 | 31030 | 37890 |  |  |  | Total | 892800 |  |  |  | Total | 0 | 11.8 | 0.2 | 0.1 | 0 | 12.4 | 0.1 | 0 | mg/L | 3.2444 | 3.8341 | 0.092949 | 1.4872 |  |  |  |  | Raw.Trb. | 3.47 | Cmb.Trb. | 0.032
21 | Pres. | 85426300 | 780549 | 1802670 | 3156120 | 132317000 | 1385570 | 4124650 | 6897200 | 691000 | 81580 | 772580 | now | 985774300 |  | 0 | 1.06 | now | 1149.6 | 1771.5 | 19.6 | 29.5 | 1207.5 | 1891.5 | 36.1 | 4.3 | "/lb | 2.625 | 9.875 | 2.12 | 9 | 0 | Raw | 9.8 | 7.45 | ef.turb.1 | 0 | ef.turb.2 | 0.036
| Prev | 85426300 | 780549 | 1802670 | 3156120 | 131626000 | 1377710 | 4093680 | 6854450 |  |  |  | prev | 984857500 |  |  |  | prev | 1149.6 | 1758.8 | 19.6 | 29.4 | 1207.5 | 1878.2 | 35.9 | 4.3 | Lbs. | 28.1925 | 21.725 | 0.53 | 9 |  | Trtd | 8.8 | 7.84 | AC.1 | 0 | AC.2 | 0.896
| Total | 0 | 0 | 0 | 0 | 691000 | 7860 | 30970 | 42750 |  |  |  | Total | 916800 |  |  |  | Total | 0 | 12.7 | 0 | 0.1 | 0 | 13.3 | 0.2 | 0 | mg/L | 4.892 | 3.7698 | 0.091967 | 1.5617 |  |  |  |  | Raw.Trb. | 2.84 | Cmb.Trb. | 0.033
22 | Pres. | 85426300 | 780549 | 1802670 | 3156120 | 132856000 | 1385570 | 4124650 | 6912820 | 539000 | 15620 | 554620 | now | 986613300 |  | 0.09 | 1.06 | now | 1149.6 | 1781.3 | 19.6 | 29.5 | 1207.5 | 1901.5 | 36.1 | 4.3 | "/lb | 1.5 | 7.9375 | 1.75 | 7 | 0 | Raw | 10.5 | 7.54 | ef.turb.1 | 0 | ef.turb.2 | 0.038
| Prev | 85426300 | 780549 | 1802670 | 3156120 | 132317000 | 1385570 | 4124650 | 6897200 |  |  |  | prev | 985774300 |  |  |  | prev | 1149.6 | 1771.5 | 19.6 | 29.5 | 1207.5 | 1891.5 | 36.1 | 4.3 | Lbs. | 16.11 | 17.4625 | 0.4375 | 7 |  | Trtd | 8.4 | 7.69 | AC.1 | 0 | AC.2 | 0.57
| Total | 0 | 0 | 0 | 0 | 539000 | 0 | 0 | 15620 |  |  |  | Total | 839000 |  |  |  | Total | 0 | 9.8 | 0 | 0 | 0 | 10 | 0 | 0 | mg/L | 3.5838 | 3.8846 | 0.097325 | 1.5572 |  |  |  |  | Raw.Trb. | 2.58 | Cmb.Trb. | 0.032
23 | Pres. | 85504600 | 780549 | 1826980 | 3161700 | 133395000 | 1393430 | 4155550 | 6942130 | 617300 | 97960 | 715260 | now | 987440300 |  | 0.05 | 1.04 | now | 1150.6 | 1791.2 | 19.8 | 29.6 | 1208.7 | 1911.9 | 36.4 | 4.3 | "/lb | 1.5 | 9 | 1.9375 | 8 | 0 | Raw | 9.4 | 7.35 | ef.turb.1 | 0 | ef.turb.2 | 0.038
| Prev | 85426300 | 780549 | 1802670 | 3156120 | 132856000 | 1385570 | 4124650 | 6912820 |  |  |  | prev | 986613300 |  |  |  | prev | 1149.6 | 1781.3 | 19.6 | 29.5 | 1207.5 | 1901.5 | 36.1 | 4.3 | Lbs. | 16.11 | 19.8 | 0.48438 | 8 |  | Trtd | 10.1 | 7.49 | AC.1 | 0 | AC.2 | 0.943
| Total | 78300 | 0 | 24310 | 5580 | 539000 | 7860 | 30900 | 29310 |  |  |  | Total | 827000 |  |  |  | Total | 1 | 9.9 | 0.2 | 0.1 | 1.2 | 10.4 | 0.3 | 0 | mg/L | 3.1292 | 3.8459 | 0.094085 | 1.5539 |  |  |  |  | Raw.Trb. | 5.24 | Cmb.Trb. | 0.032
24 | Pres. | 85504600 | 780549 | 1826980 | 3161700 | 134046000 | 1401280 | 4208500 | 7021820 | 651000 | 140490 | 791490 | now | 988273600 |  | 0.03 | 1.07 | now | 1150.6 | 1803.2 | 20 | 29.7 | 1208.7 | 1924.9 | 36.7 | 4.3 | "/lb | 1.625 | 9.25 | 2.125 | 8 | 0 | Raw | 9.7 | 7.49 | ef.turb.1 | 0 | ef.turb.2 | 0.038
| Prev | 85504600 | 780549 | 1826980 | 3161700 | 133395000 | 1393430 | 4155550 | 6942130 |  |  |  | prev | 987440300 |  |  |  | prev | 1150.6 | 1791.2 | 19.8 | 29.6 | 1208.7 | 1911.9 | 36.4 | 4.3 | Lbs. | 17.4525 | 20.35 | 0.53125 | 8 |  | Trtd | 9.4 | 7.51 | AC.1 | 0 | AC.2 | 0.766
| Total | 0 | 0 | 0 | 0 | 651000 | 7850 | 52950 | 79690 |  |  |  | Total | 833300 |  |  |  | Total | 0 | 12 | 0.2 | 0.1 | 0 | 13 | 0.3 | 0 | mg/L | 3.2145 | 3.7482 | 0.097848 | 1.4735 |  |  |  |  | Raw.Trb. | 2.36 | Cmb.Trb. | 0.033
25 | Pres. | 85504600 | 780549 | 1826980 | 3161700 | 134543000 | 1401280 | 4208500 | 7021820 | 497000 | 0 | 497000 | now | 989134900 |  | 0.19 | 1.03 | now | 1150.6 | 1812.4 | 20.1 | 29.8 | 1208.7 | 1935.9 | 36.9 | 4.3 | "/lb | 1.25 | 7.5 | 1.75 | 7 | 0 | Raw | 9.6 | 7.58 | ef.turb.1 | 0 | ef.turb.2 | 0.038
| Prev | 85504600 | 780549 | 1826980 | 3161700 | 134046000 | 1401280 | 4208500 | 7021820 |  |  |  | prev | 988273600 |  |  |  | prev | 1150.6 | 1803.2 | 20 | 29.7 | 1208.7 | 1924.9 | 36.7 | 4.3 | Lbs. | 13.425 | 16.5 | 0.4375 | 7 |  | Trtd | 9.3 | 7.38 | AC.1 | 0 | AC.2 | 0.674
| Total | 0 | 0 | 0 | 0 | 497000 | 0 | 0 | 0 |  |  |  | Total | 861300 |  |  |  | Total | 0 | 9.2 | 0.1 | 0.1 | 0 | 11 | 0.2 | 0 | mg/L | 3.2389 | 3.9807 | 0.10555 | 1.6888 |  |  |  |  | Raw.Trb. | 1.69 | Cmb.Trb. | 0.032
26 | Pres. | 85504600 | 780549 | 1826980 | 3161700 | 135166000 | 1409150 | 4239880 | 7174770 | 623000 | 192200 | 815200 | now | 989997300 |  | 0.02 | 1.03 | now | 1150.6 | 1823.7 | 20.1 | 29.9 | 1208.7 | 1947.5 | 36.9 | 4.3 | "/lb | 1.625 | 9 | 1.875 | 8 | 0 | Raw | 10.4 | 7.6 | ef.turb.1 | 0 | ef.turb.2 | 0.039
| Prev | 85504600 | 780549 | 1826980 | 3161700 | 134543000 | 1401280 | 4208500 | 7021820 |  |  |  | prev | 989134900 |  |  |  | prev | 1150.6 | 1812.4 | 20.1 | 29.8 | 1208.7 | 1935.9 | 36.9 | 4.3 | Lbs. | 17.4525 | 19.8 | 0.46875 | 8 |  | Trtd | 9.9 | 7.46 | AC.1 | 0 | AC.2 | 0.628
| Total | 0 | 0 | 0 | 0 | 623000 | 7870 | 31380 | 152950 |  |  |  | Total | 862400 |  |  |  | Total | 0 | 11.3 | 0 | 0.1 | 0 | 11.6 | 0 | 0 | mg/L | 3.359 | 3.8108 | 0.090217 | 1.5397 |  |  |  |  | Raw.Trb. | 2.32 | Cmb.Trb. | 0.035
27 | Pres. | 85504600 | 780549 | 1826980 | 3161700 | 135694000 | 1416970 | 4271250 | 7248410 | 528000 | 112830 | 640830 | now | 990838300 |  | 0 | 1 | now | 1150.6 | 1833.4 | 20.3 | 30 | 1208.7 | 1958.2 | 37.1 | 4.3 | "/lb | 1.5 | 7.625 | 1.5625 | 7 | 0 | Raw | 9.7 | 7.46 | ef.turb.1 | 0 | ef.turb.2 | 0.038
| Prev | 85504600 | 780549 | 1826980 | 3161700 | 135166000 | 1409150 | 4239880 | 7174770 |  |  |  | prev | 989997300 |  |  |  | prev | 1150.6 | 1823.7 | 20.1 | 29.9 | 1208.7 | 1947.5 | 36.9 | 4.3 | Lbs. | 16.11 | 16.775 | 0.39062 | 7 |  | Trtd | 8.1 | 7.7 | AC.1 | 0 | AC.2 | 0.671
| Total | 0 | 0 | 0 | 0 | 528000 | 7820 | 31370 | 73640 |  |  |  | Total | 841000 |  |  |  | Total | 0 | 9.7 | 0.2 | 0.1 | 0 | 10.7 | 0.2 | 0 | mg/L | 3.6584 | 3.8095 | 0.088707 | 1.5896 |  |  |  |  | Raw.Trb. | 2.34 | Cmb.Trb. | 0.032
28 | Pres. | 85504600 | 780549 | 1826980 | 3161700 | 136181000 | 1416970 | 4271250 | 7248410 | 487000 | 0 | 487000 | now | 991612960 |  | 0 | 0.98 | now | 1150.6 | 1842 | 20.3 | 30 | 1208.7 | 1967 | 37.1 | 4.3 | "/lb | 1 | 6.75 | 1 | 7 | 0 | Raw | 10 | 7.42 | ef.turb.1 | 0 | ef.turb.2 | 0.041
| Prev | 85504600 | 780549 | 1826980 | 3161700 | 135694000 | 1416970 | 4271250 | 7248410 |  |  |  | prev | 990838300 |  |  |  | prev | 1150.6 | 1833.4 | 20.3 | 30 | 1208.7 | 1958.2 | 37.1 | 4.3 | Lbs. | 10.74 | 14.85 | 0.25 | 7 |  | Trtd | 8.3 | 7.66 | AC.1 | 0 | AC.2 | 0.799
| Total | 0 | 0 | 0 | 0 | 487000 | 0 | 0 | 0 |  |  |  | Total | 774660 |  |  |  | Total | 0 | 8.6 | 0 | 0 | 0 | 8.8 | 0 | 0 | mg/L | 2.6443 | 3.6562 | 0.061552 | 1.7235 |  |  |  |  | Raw.Trb. | 2.14 | Cmb.Trb. | 0.034
[10 empty] | Totals | [6 empty] | Avg. | [10 empty] | Totals | [5 empty] | Avg. Trtd.
[10 empty] | 19616700 | 2204828 | 21821528 |  | 24167460 |  | 3.79 | 1.0575 | [5 empty] | 22.4 | 288.7 |  |  |  | 506.928 | 513.007 | 13.0144 | 216 |  |  | 8.8536 | 7.6921 |  | Avg.Cmb.Trb |  | 0.036679
[22 empty] | Total: | 311.1

## Mar, 2021
March, 2021
Filters | [15 empty] | Rain | Cl2 | Pump Hours | [8 empty] | Chemicals | [5 empty] | Misc. |  |  | Turbidity
Day |  | CW.Tot.1 | Cla.Wst.1 | BW.Wst.1 | FTWst.1 | CW.Tot.2 | Cla.Wst.2 | BW.Wst.2 | FTWst.2 | Treated Total | Wastewater | Total Influent | Totalizer |  |  | Inches | Resid | Pump | Ef.Pmp.1 | Ef.Pmp.2 | Blo.1 | Blo.2 | URT.1 | URT.2 | BWP | SWP | Chem | ACH | SA | Poly | Cl2.1 | Cl2.2 | water | Temp | pH | F1 |  | F2
1 | Pres. | 86358900 | 788757 | 1826980 | 3178770 | 136181000 | 1416970 | 4271250 | 7248410 | 854300 | 25278 | 879578 | now | 992498200 |  | 0 | 1 | now | 1161 | 1842 | 20.4 | 30 | 1219.3 | 1967 | 37.1 | 4.3 | "/lb | 1.375 | 8.25 | 1.75 | 8 | 0 | Raw | 10.5 | 7.41 | ef.turb.1 | 0.045 | ef.turb.2 | 0
| Prev | 85504600 | 780549 | 1826980 | 3161700 | 136181000 | 1416970 | 4271250 | 7248410 |  |  |  | prev | 991612960 |  |  |  | prev | 1150.6 | 1842 | 20.3 | 30 | 1208.7 | 1967 | 37.1 | 4.3 | Lbs. | 14.7675 | 18.15 | 0.4375 | 8 |  | Trtd | 8.5 | 7.79 | AC.1 | 0.36 | AC.2 | 0
| Total | 854300 | 8208 | 0 | 17070 | 0 | 0 | 0 | 0 |  |  |  | Total | 885240 |  |  |  | Total | 10.4 | 0 | 0.1 | 0 | 10.6 | 0 | 0 | 0 | mg/L | 2.0727 | 2.5474 | 0.061405 | 1.1228 |  |  |  |  | Raw.Trb. | 1.92 | Cmb.Trb. | 0.033
2 | Pres. | 87286300 | 788757 | 1862070 | 3250130 | 136181000 | 1416970 | 4271250 | 7248410 | 927400 | 106450 | 1033850 | now | 993318200 |  | 0 | 1.03 | now | 1172.2 | 1842 | 20.4 | 30 | 1231.5 | 1967 | 37.3 | 4.4 | "/lb | 1.5 | 9 | 2 | 9 | 0 | Raw | 9.9 | 7.33 | ef.turb.1 | 0.04 | ef.turb.2 | 0
| Prev | 86358900 | 788757 | 1826980 | 3178770 | 136181000 | 1416970 | 4271250 | 7248410 |  |  |  | prev | 992498200 |  |  |  | prev | 1161 | 1842 | 20.4 | 30 | 1219.3 | 1967 | 37.1 | 4.3 | Lbs. | 16.11 | 19.8 | 0.5 | 9 |  | Trtd | 9.1 | 7.75 | AC.1 | 0.896 | AC.2 | 0
| Total | 927400 | 0 | 35090 | 71360 | 0 | 0 | 0 | 0 |  |  |  | Total | 820000 |  |  |  | Total | 11.2 | 0 | 0 | 0 | 12.2 | 0 | 0.2 | 0.1 | mg/L | 2.0829 | 2.56 | 0.064645 | 1.1636 |  |  |  |  | Raw.Trb. | 1.81 | Cmb.Trb. | 0.034
10.6
3 | Pres. | 88115100 | 796981 | 1862070 | 3258550 | 136181000 | 1416970 | 4271250 | 7248410 | 828800 | 16644 | 845444 | now | 994141600 |  | 0 | 1.06 | now | 1182.3 | 1842 | 20.5 | 30 | 1241.8 | 1967 | 37.3 | 4.4 | "/lb | 1.25 | 8 | 1.75 | 8 | 0 | Raw | 9 | 7.42 | ef.turb.1 | 0.055 | ef.turb.2 | 0
| Prev | 87286300 | 788757 | 1862070 | 3250130 | 136181000 | 1416970 | 4271250 | 7248410 |  |  |  | prev | 993318200 |  |  |  | prev | 1172.2 | 1842 | 20.4 | 30 | 1231.5 | 1967 | 37.3 | 4.4 | Lbs. | 13.425 | 17.6 | 0.4375 | 8 |  | Trtd | 9.1 | 7.86 | AC.1 | 0.501 | AC.2 | 0
| Total | 828800 | 8224 | 0 | 8420 | 0 | 0 | 0 | 0 |  |  |  | Total | 823400 |  |  |  | Total | 10.1 | 0 | 0.1 | 0 | 10.3 | 0 | 0 | 0 | mg/L | 1.9422 | 2.5462 | 0.063294 | 1.1574 |  |  |  |  | Raw.Trb. | 1.85 | Cmb.Trb. | 0.056
4 | Pres. | 89035300 | 805216 | 1897180 | 3337630 | 136181000 | 1416970 | 4271250 | 7248410 | 920200 | 122425 | 1042625 | now | 994974100 |  | 0 | 1.07 | now | 1193.4 | 1842 | 20.6 | 30 | 1254.1 | 1967 | 37.3 | 4.4 | "/lb | 1.5 | 8.9375 | 1.9375 | 9 | 0 | Raw | 8.9 | 7.42 | ef.turb.1 | 0.039 | ef.turb.2 | 0
| Prev | 88115100 | 796981 | 1862070 | 3258550 | 136181000 | 1416970 | 4271250 | 7248410 |  |  |  | prev | 994141600 |  |  |  | prev | 1182.3 | 1842 | 20.5 | 30 | 1241.8 | 1967 | 37.3 | 4.4 | Lbs. | 16.11 | 19.6625 | 0.48438 | 9 |  | Trtd | 9.9 | 7.67 | AC.1 | 0.595 | AC.2 | 0
| Total | 920200 | 8235 | 35110 | 79080 | 0 | 0 | 0 | 0 |  |  |  | Total | 832500 |  |  |  | Total | 11.1 | 0 | 0.1 | 0 | 12.3 | 0 | 0 | 0 | mg/L | 2.0992 | 2.5621 | 0.063115 | 1.1727 |  |  |  |  | Raw.Trb. | 1.57 | Cmb.Trb. | 0.033
5 | Pres. | 89743700 | 813461 | 1897180 | 3346110 | 136181000 | 1416970 | 4271250 | 7248410 | 708400 | 16725 | 725125 | now | 995792800 | 0 | 0.33 | 1.04 | now | 1202 | 1842 | 20.8 | 30 | 1262.9 | 1967 | 37.5 | 4.4 | "/lb | 1 | 7 | 1.875 | 7 | 0 | Raw | 9.7 | 7.38 | ef.turb.1 | 0.041 | ef.turb.2 | 0
| Prev | 89035300 | 805216 | 1897180 | 3337630 | 136181000 | 1416970 | 4271250 | 7248410 |  |  |  | prev | 994974100 |  |  |  | prev | 1193.4 | 1842 | 20.6 | 30 | 1254.1 | 1967 | 37.3 | 4.4 | Lbs. | 10.74 | 15.4 | 0.46875 | 7 |  | Trtd | 9.9 | 7.54 | AC.1 | 0.569 | AC.2 | 0
| Total | 708400 | 8245 | 0 | 8480 | 0 | 0 | 0 | 0 |  |  |  | Total | 818700 |  |  |  | Total | 8.6 | 0 | 0.2 | 0 | 8.8 | 0 | 0.2 | 0 | mg/L | 1.8179 | 2.6066 | 0.079341 | 1.1848 |  |  |  |  | Raw.Trb. | 1.52 | Cmb.Trb. | 0.036
6 | Pres. | 90547500 | 813461 | 1897180 | 3354650 | 136181000 | 1416970 | 4271250 | 7248410 | 803800 | 8540 | 812340 | now | 996613700 |  | 0.11 | 1.03 | now | 1211.8 | 1842 | 20.8 | 30 | 1272.7 | 1967 | 37.5 | 4.5 | "/lb | 1.75 | 7.875 | 1.625 | 7 | 0 | Raw | 8.1 | 7.57 | ef.turb.1 | 0.038 | ef.turb.2 | 0
| Prev | 89743700 | 813461 | 1897180 | 3346110 | 136181000 | 1416970 | 4271250 | 7248410 |  |  |  | prev | 995792800 |  |  |  | prev | 1202 | 1842 | 20.8 | 30 | 1262.9 | 1967 | 37.5 | 4.4 | Lbs. | 18.795 | 17.325 | 0.40625 | 7 |  | Trtd | 8.9 | 7.83 | AC.1 | 0.755 | AC.2 | 0
| Total | 803800 | 0 | 0 | 8540 | 0 | 0 | 0 | 0 |  |  |  | Total | 820900 |  |  |  | Total | 9.8 | 0 | 0 | 0 | 9.8 | 0 | 0 | 0.1 | mg/L | 2.8037 | 2.5844 | 0.060601 | 1.0442 |  |  |  |  | Raw.Trb. | 1.74 | Cmb.Trb. | 0.032
7 | Pres. | 91534300 | 821708 | 1932180 | 3422980 | 136181000 | 1416970 | 4271250 | 7248410 | 986800 | 111577 | 1098377 | now | 997408100 |  | 0.04 | 1.07 | now | 1223.8 | 1842 | 20.9 | 30 | 1285.7 | 1967 | 37.6 | 4.5 | "/lb | 1.625 | 9.625 | 1.875 | 9 | 0 | Raw | 8.6 | 7.44 | ef.turb.1 | 0.037 | ef.turb.2 | 0
| Prev | 90547500 | 813461 | 1897180 | 3354650 | 136181000 | 1416970 | 4271250 | 7248410 |  |  |  | prev | 996613700 |  |  |  | prev | 1211.8 | 1842 | 20.8 | 30 | 1272.7 | 1967 | 37.5 | 4.5 | Lbs. | 17.4525 | 21.175 | 0.46875 | 9 |  | Trtd | 9.7 | 7.94 | AC.1 | 0.476 | AC.2 | 0
| Total | 986800 | 8247 | 35000 | 68330 | 0 | 0 | 0 | 0 |  |  |  | Total | 794400 |  |  |  | Total | 12 | 0 | 0.1 | 0 | 13 | 0 | 0.1 | 0 | mg/L | 2.1206 | 2.5729 | 0.056957 | 1.0936 |  |  |  |  | Raw.Trb. | 1.59 | Cmb.Trb. | 0.031
8 | Pres. | 92359800 | 829942 | 1932180 | 3431500 | 136181000 | 1416970 | 4271250 | 7248410 | 825500 | 16754 | 842254 | now | 998311100 |  | 0.04 | 1.07 | now | 1233.8 | 1842 | 21 | 30 | 1296 | 1967 | 37.6 | 4.5 | "/lb | 1.125 | 8 | 1.75 | 7 | 0 | Raw | 9.3 | 7.57 | ef.turb.1 | 0.039 | ef.turb.2 | 0
| Prev | 91534300 | 821708 | 1932180 | 3422980 | 136181000 | 1416970 | 4271250 | 7248410 |  |  |  | prev | 997408100 |  |  |  | prev | 1223.8 | 1842 | 20.9 | 30 | 1285.7 | 1967 | 37.6 | 4.5 | Lbs. | 12.0825 | 17.6 | 0.4375 | 7 |  | Trtd | 8.3 | 7.91 | AC.1 | 0.54 | AC.2 | 0
| Total | 825500 | 8234 | 0 | 8520 | 0 | 0 | 0 | 0 |  |  |  | Total | 903000 |  |  |  | Total | 10 | 0 | 0.1 | 0 | 10.3 | 0 | 0 | 0 | mg/L | 1.755 | 2.5564 | 0.063547 | 1.0168 |  |  |  |  | Raw.Trb. | 1.52 | Cmb.Trb. | 0.033
9 | Pres. | 93450300 | 838137 | 1967270 | 3499960 | 136181000 | 1416970 | 4271250 | 7248410 | 1090500 | 111745 | 1202245 | now | 999176200 |  | 0.12 | 1.03 | now | 1247 | 1842 | 21.1 | 30 | 1310.3 | 1967 | 37.8 | 4.6 | "/lb | 1.875 | 10.875 | 2.5 | 10 | 0 | Raw | 9.4 | 7.48 | ef.turb.1 | 0.037 | ef.turb.2 | 0
| Prev | 92359800 | 829942 | 1932180 | 3431500 | 136181000 | 1416970 | 4271250 | 7248410 |  |  |  | prev | 998311100 |  |  |  | prev | 1233.8 | 1842 | 21 | 30 | 1296 | 1967 | 37.6 | 4.5 | Lbs. | 20.1375 | 23.925 | 0.625 | 10 |  | Trtd | 8.2 | 7.84 | AC.1 | 0.727 | AC.2 | 0
| Total | 1090500 | 8195 | 35090 | 68460 | 0 | 0 | 0 | 0 |  |  |  | Total | 865100 |  |  |  | Total | 13.2 | 0 | 0.1 | 0 | 14.3 | 0 | 0.2 | 0.1 | mg/L | 2.2142 | 2.6306 | 0.068721 | 1.0995 |  |  |  |  | Raw.Trb. | 1.81 | Cmb.Trb. | 0.032
10 | Pres. | 94078100 | 846349 | 2002320 | 3583560 | 136181000 | 1416970 | 4271250 | 7248410 | 627800 | 126862 | 754662 | now | 999989800 |  | 0.1 | 1.01 | now | 1254.7 | 1842 | 21.2 | 30 | 1319.2 | 1967 | 38 | 4.6 | "/lb | 1.125 | 6.5 | 1.625 | 6 | 0 | Raw | 8.8 | 7.51 | ef.turb.1 | 0.039 | ef.turb.2 | 0
| Prev | 93450300 | 838137 | 1967270 | 3499960 | 136181000 | 1416970 | 4271250 | 7248410 |  |  |  | prev | 999176200 |  |  |  | prev | 1247 | 1842 | 21.1 | 30 | 1310.3 | 1967 | 37.8 | 4.6 | Lbs. | 12.0825 | 14.3 | 0.40625 | 6 |  | Trtd | 9.7 | 7.55 | AC.1 | 0.746 | AC.2 | 0
| Total | 627800 | 8212 | 35050 | 83600 | 0 | 0 | 0 | 0 |  |  |  | Total | 813600 |  |  |  | Total | 7.7 | 0 | 0.1 | 0 | 8.9 | 0 | 0.2 | 0 | mg/L | 2.3076 | 2.7312 | 0.07759 | 1.1459 |  |  |  |  | Raw.Trb. | 2.7 | Cmb.Trb. | 0.036
11 | Pres. | 94078100 | 846349 | 2002320 | 3583560 | 136816000 | 1424810 | 4307420 | 7322630 | 635000 | 118230 | 753230 | now | 1000800400 |  | 0 | 1.03 | now | 1254.7 | 1853.9 | 21.4 | 30 | 1319.2 | 1979.8 | 38.2 | 4.6 | "/lb | 1.5 | 8.875 | 1.9375 | 9 | 0 | Raw | 9.1 | 7.47 | ef.turb.1 | 0.065 | ef.turb.2 | 0.038
| Prev | 94078100 | 846349 | 2002320 | 3583560 | 136181000 | 1416970 | 4271250 | 7248410 |  |  |  | prev | 999989800 |  |  |  | prev | 1254.7 | 1842 | 21.2 | 30 | 1319.2 | 1967 | 38 | 4.6 | Lbs. | 16.11 | 19.525 | 0.48438 | 9 |  | Trtd | 8.9 | 7.9 | AC.1 | 1.131 | AC.2 | 0.912
| Total | 0 | 0 | 0 | 0 | 635000 | 7840 | 36170 | 74220 |  |  |  | Total | 810600 |  |  |  | Total | 0 | 11.9 | 0.2 | 0 | 0 | 12.8 | 0.2 | 0 | mg/L | 3.042 | 3.6868 | 0.091462 | 1.6994 |  |  |  |  | Raw.Trb. | 3.68 | Cmb.Trb. | 0.043
12 | Pres. | 94078100 | 846349 | 2002320 | 3583560 | 137266000 | 1432650 | 4343610 | 7387590 | 450000 | 108990 | 558990 | now | 1001653800 |  | 0 | 1.03 | now | 1254.7 | 1862.2 | 21.6 | 30.1 | 1319.2 | 1988.9 | 38.2 | 4.6 | "/lb | 1 | 6.625 | 2 | 6 | 0 | Raw | 9.2 | 7.42 | ef.turb.1 | 0 | ef.turb.2 | 0.048
| Prev | 94078100 | 846349 | 2002320 | 3583560 | 136816000 | 1424810 | 4307420 | 7322630 |  |  |  | prev | 1000800400 |  |  |  | prev | 1254.7 | 1853.9 | 21.4 | 30 | 1319.2 | 1979.8 | 38.2 | 4.6 | Lbs. | 10.74 | 14.575 | 0.5 | 6 |  | Trtd | 9.6 | 7.55 | AC.1 | 0 | AC.2 | 0.703
| Total | 0 | 0 | 0 | 0 | 450000 | 7840 | 36190 | 64960 |  |  |  | Total | 853400 |  |  |  | Total | 0 | 8.3 | 0.2 | 0.1 | 0 | 9.1 | 0 | 0 | mg/L | 2.8617 | 3.8836 | 0.13323 | 1.5987 |  |  |  |  | Raw.Trb. | 1.89 | Cmb.Trb. | 0.049
13 | Pres. | 94078100 | 846349 | 2002320 | 3583560 | 137841000 | 1432650 | 4343610 | 7395880 | 575000 | 8290 | 583290 | now | 1002544592 |  | 0 | 0.96 | now | 1254.7 | 1872.7 | 21.6 | 30.1 | 1319.2 | 1995.5 | 38.4 | 4.6 | "/lb | 1.375 | 9 | 1.5 | 8 | 0 | Raw | 10.7 | 7.59 | ef.turb.1 | 0 | ef.turb.2 | 0.037
| Prev | 94078100 | 846349 | 2002320 | 3583560 | 137266000 | 1432650 | 4343610 | 7387590 |  |  |  | prev | 1001653800 |  |  |  | prev | 1254.7 | 1862.2 | 21.6 | 30.1 | 1319.2 | 1988.9 | 38.2 | 4.6 | Lbs. | 14.7675 | 19.8 | 0.375 | 8 |  | Trtd | 9.3 | 7.69 | AC.1 | 0 | AC.2 | 0.634
| Total | 0 | 0 | 0 | 0 | 575000 | 0 | 0 | 8290 |  |  |  | Total | 890792 |  |  |  | Total | 0 | 10.5 | 0 | 0 | 0 | 6.6 | 0.2 | 0 | mg/L | 3.0794 | 4.1289 | 0.078198 | 1.6682 |  |  |  |  | Raw.Trb. | 1.69 | Cmb.Trb. | 0.036
14 | Pres. | 94078100 | 846349 | 2002320 | 3583560 | 138511000 | 1440420 | 4379680 | 7477140 | 670000 | 125100 | 795100 | now | 1003227368 |  | 0.41 | 0.95 | now | 1254.7 | 1885 | 21.8 | 30.2 | 1319.2 | 2012.9 | 38.6 | 4.6 | "/lb | 1.875 | 9.125 | 2 | 9 | 0 | Raw | 10.4 | 7.58 | ef.turb.1 | 0 | ef.turb.2 | 0.037
| Prev | 94078100 | 846349 | 2002320 | 3583560 | 137841000 | 1432650 | 4343610 | 7395880 |  |  |  | prev | 1002544592 |  |  |  | prev | 1254.7 | 1872.7 | 21.6 | 30.1 | 1319.2 | 1995.5 | 38.4 | 4.6 | Lbs. | 20.1375 | 20.075 | 0.5 | 9 |  | Trtd | 8.7 | 7.82 | AC.1 | 0 | AC.2 | 0.491
| Total | 0 | 0 | 0 | 0 | 670000 | 7770 | 36070 | 81260 |  |  |  | Total | 682776 |  |  |  | Total | 0 | 12.3 | 0.2 | 0.1 | 0 | 17.4 | 0.2 | 0 | mg/L | 3.6038 | 3.5926 | 0.089481 | 1.6107 |  |  |  |  | Raw.Trb. | 1.54 | Cmb.Trb. | 0.037
15 | Pres. | 94078100 | 846349 | 2002320 | 3583560 | 139055000 | 1440420 | 4379680 | 7485140 | 544000 | 8000 | 552000 | now | 1004073300 |  | 0 | 0.97 | now | 1254.7 | 1892.4 | 21.8 | 30.2 | 1319.2 | 2020.3 | 38.6 | 4.6 | "/lb | 1 | 6 | 1.25 | 6 | 0 | Raw | 9.3 | 7.55 | ef.turb.1 | 0 | ef.turb.2 | 0.038
| Prev | 94078100 | 846349 | 2002320 | 3583560 | 138511000 | 1440420 | 4379680 | 7477140 |  |  |  | prev | 1003227368 |  |  |  | prev | 1254.7 | 1885 | 21.8 | 30.2 | 1319.2 | 2012.9 | 38.6 | 4.6 | Lbs. | 10.74 | 13.2 | 0.3125 | 6 |  | Trtd | 7.8 | 7.87 | AC.1 | 0 | AC.2 | 0.662
| Total | 0 | 0 | 0 | 0 | 544000 | 0 | 0 | 8000 |  |  |  | Total | 845932 |  |  |  | Total | 0 | 7.4 | 0 | 0 | 0 | 7.4 | 0 | 0 | mg/L | 2.3672 | 2.9094 | 0.068879 | 1.3225 |  |  |  |  | Raw.Trb. | 1.77 | Cmb.Trb. | 0.035
16 | Pres. | 94078100 | 846349 | 2002320 | 3583560 | 139898000 | 1447420 | 4415670 | 7560130 | 843000 | 117980 | 960980 | now | 1004895500 |  | 0 | 1.05 | now | 1254.7 | 1902.9 | 21.8 | 30.3 | 1319.2 | 2031.8 | 38.8 | 4.6 | "/lb | 1.375 | 8.25 | 1.9375 | 9 | 0 | Raw | 8.8 | 7.69 | ef.turb.1 | 0 | ef.turb.2 | 0.036
| Prev | 94078100 | 846349 | 2002320 | 3583560 | 139055000 | 1440420 | 4379680 | 7485140 |  |  |  | prev | 1004073300 |  |  |  | prev | 1254.7 | 1892.4 | 21.8 | 30.2 | 1319.2 | 2020.3 | 38.6 | 4.6 | Lbs. | 14.7675 | 18.15 | 0.48438 | 9 |  | Trtd | 8.7 | 7.59 | AC.1 | 0 | AC.2 | 0.481
| Total | 0 | 0 | 0 | 0 | 843000 | 7000 | 35990 | 74990 |  |  |  | Total | 822200 |  |  |  | Total | 0 | 10.5 | 0 | 0.1 | 0 | 11.5 | 0.2 | 0 | mg/L | 2.1005 | 2.5816 | 0.068895 | 1.2801 |  |  |  |  | Raw.Trb. | 1.48 | Cmb.Trb. | 0.033
17 | Pres. | 94078100 | 846349 | 2002320 | 3583560 | 140600000 | 1455420 | 4415670 | 7577130 | 702000 | 25000 | 727000 | now | 1005707400 |  | 0.02 | 1.02 | now | 1254.7 | 1911.6 | 22 | 30.3 | 1319.2 | 2040.8 | 38.8 | 4.6 | "/lb | 1.125 | 7 | 1.25 | 7 | 0 | Raw | 8.7 | 7.61 | ef.turb.1 | 0 | ef.turb.2 | 0.039
| Prev | 94078100 | 846349 | 2002320 | 3583560 | 139898000 | 1447420 | 4415670 | 7560130 |  |  |  | prev | 1004895500 |  |  |  | prev | 1254.7 | 1902.9 | 21.8 | 30.3 | 1319.2 | 2031.8 | 38.8 | 4.6 | Lbs. | 12.0825 | 15.4 | 0.3125 | 7 |  | Trtd | 9.3 | 7.6 | AC.1 | 0 | AC.2 | 0.536
| Total | 0 | 0 | 0 | 0 | 702000 | 8000 | 0 | 17000 |  |  |  | Total | 811900 |  |  |  | Total | 0 | 8.7 | 0.2 | 0 | 0 | 9 | 0 | 0 | mg/L | 2.0637 | 2.6304 | 0.053376 | 1.1956 |  |  |  |  | Raw.Trb. | 1.43 | Cmb.Trb. | 0.037
18 | Pres. | 94078100 | 846349 | 2002320 | 3583560 | 141400000 | 1463420 | 4451670 | 7661120 | 800000 | 127990 | 927990 | now | 1006518900 |  | 0.19 | 1 | now | 1254.7 | 1921.6 | 22 | 30.5 | 1319.2 | 2051.9 | 39 | 4.6 | "/lb | 1.5 | 7.9375 | 1.875 | 8 | 0 | Raw | 10.2 | 7.61 | ef.turb.1 | 0 | ef.turb.2 | 0.037
| Prev | 94078100 | 846349 | 2002320 | 3583560 | 140600000 | 1455420 | 4415670 | 7577130 |  |  |  | prev | 1005707400 |  |  |  | prev | 1254.7 | 1911.6 | 22 | 30.3 | 1319.2 | 2040.8 | 38.8 | 4.6 | Lbs. | 16.11 | 17.4625 | 0.46875 | 8 |  | Trtd | 8.6 | 7.89 | AC.1 | 0 | AC.2 | 0.605
| Total | 0 | 0 | 0 | 0 | 800000 | 8000 | 36000 | 83990 |  |  |  | Total | 811500 |  |  |  | Total | 0 | 10 | 0 | 0.2 | 0 | 11.1 | 0.2 | 0 | mg/L | 2.4146 | 2.6173 | 0.070256 | 1.199 |  |  |  |  | Raw.Trb. | 1.39 | Cmb.Trb. | 0.033
19 | Pres. | 94078100 | 846349 | 2002320 | 3583560 | 142100000 | 1463420 | 4487670 | 7731120 | 700000 | 106000 | 806000 | now | 1007318500 |  | 0.05 | 1.02 | now | 1254.7 | 1930.3 | 22.1 | 30.6 | 1319.2 | 2061.5 | 39.2 | 4.6 | "/lb | 1.75 | 7 | 1.75 | 7 | 0 | Raw | 10.6 | 7.73 | ef.turb.1 | 0 | ef.turb.2 | 0.035
| Prev | 94078100 | 846349 | 2002320 | 3583560 | 141400000 | 1463420 | 4451670 | 7661120 |  |  |  | prev | 1006518900 |  |  |  | prev | 1254.7 | 1921.6 | 22 | 30.5 | 1319.2 | 2051.9 | 39 | 4.6 | Lbs. | 18.795 | 15.4 | 0.4375 | 7 |  | Trtd | 9 | 7.95 | AC.1 | 0 | AC.2 | 0.536
| Total | 0 | 0 | 0 | 0 | 700000 | 0 | 36000 | 70000 |  |  |  | Total | 799600 |  |  |  | Total | 0 | 8.7 | 0.1 | 0.1 | 0 | 9.6 | 0.2 | 0 | mg/L | 3.2194 | 2.6379 | 0.07494 | 1.199 |  |  |  |  | Raw.Trb. | 1.78 | Cmb.Trb. | 0.034
20 | Pres. | 94078100 | 846349 | 2002320 | 3583560 | 142837000 | 1471420 | 4487670 | 7739120 | 737000 | 16000 | 753000 | now | 1008130700 |  | 0 | 0.97 | now | 1254.7 | 1939.4 | 22.2 | 30.6 | 1319.2 | 2070.8 | 39.2 | 4.6 | "/lb | 1.25 | 7.25 | 1.75 | 8 | 0 | Raw | 9.9 | 7.43 | ef.turb.1 | 0 | ef.turb.2 | 0.038
| Prev | 94078100 | 846349 | 2002320 | 3583560 | 142100000 | 1463420 | 4487670 | 7731120 |  |  |  | prev | 1007318500 |  |  |  | prev | 1254.7 | 1930.3 | 22.1 | 30.6 | 1319.2 | 2061.5 | 39.2 | 4.6 | Lbs. | 13.425 | 15.95 | 0.4375 | 8 |  | Trtd | 9.2 | 7.73 | AC.1 | 0 | AC.2 | 0.49
| Total | 0 | 0 | 0 | 0 | 737000 | 8000 | 0 | 8000 |  |  |  | Total | 812200 |  |  |  | Total | 0 | 9.1 | 0.1 | 0 | 0 | 9.3 | 0 | 0 | mg/L | 2.1841 | 2.5949 | 0.071178 | 1.3015 |  |  |  |  | Raw.Trb. | 1.48 | Cmb.Trb. | 0.034
21 | Pres. | 94078100 | 846349 | 2002320 | 3583560 | 143808000 | 1478420 | 4524670 | 7792110 | 971000 | 96990 | 1067990 | now | 1008919200 |  | 0.13 | 1.04 | now | 1254.7 | 1951.5 | 22.3 | 30.8 | 1319.2 | 2083.7 | 39.4 | 4.6 | "/lb | 1.875 | 9.625 | 1.875 | 11 | 0 | Raw | 10.3 | 7.65 | ef.turb.1 | 0 | ef.turb.2 | 0.037
| Prev | 94078100 | 846349 | 2002320 | 3583560 | 142837000 | 1471420 | 4487670 | 7739120 |  |  |  | prev | 1008130700 |  |  |  | prev | 1254.7 | 1939.4 | 22.2 | 30.6 | 1319.2 | 2070.8 | 39.2 | 4.6 | Lbs. | 20.1375 | 21.175 | 0.46875 | 11 |  | Trtd | 9.2 | 7.79 | AC.1 | 0 | AC.2 | 0.501
| Total | 0 | 0 | 0 | 0 | 971000 | 7000 | 37000 | 52990 |  |  |  | Total | 788500 |  |  |  | Total | 0 | 12.1 | 0.1 | 0.2 | 0 | 12.9 | 0.2 | 0 | mg/L | 2.4867 | 2.6148 | 0.057884 | 1.3583 |  |  |  |  | Raw.Trb. | 1.47 | Cmb.Trb. | 0.034
22 | Pres. | 94078100 | 846349 | 2002320 | 3583560 | 144406000 | 1486420 | 4524670 | 7809110 | 598000 | 25000 | 623000 | now | 1009743500 |  | 0.08 | 1.04 | now | 1254.7 | 1958.9 | 22.3 | 30.9 | 1319.2 | 2091.4 | 39.4 | 4.6 | "/lb | 1.0625 | 5.9375 | 1.25 | 6 | 0 | Raw | 8.8 | 7.56 | ef.turb.1 | 0 | ef.turb.2 | 0.04
| Prev | 94078100 | 846349 | 2002320 | 3583560 | 143808000 | 1478420 | 4524670 | 7792110 |  |  |  | prev | 1008919200 |  |  |  | prev | 1254.7 | 1951.5 | 22.3 | 30.8 | 1319.2 | 2083.7 | 39.4 | 4.6 | Lbs. | 11.4113 | 13.0625 | 0.3125 | 6 |  | Trtd | 8.1 | 7.93 | AC.1 | 0 | AC.2 | 0.66
| Total | 0 | 0 | 0 | 0 | 598000 | 8000 | 0 | 17000 |  |  |  | Total | 824300 |  |  |  | Total | 0 | 7.4 | 0 | 0.1 | 0 | 7.7 | 0 | 0 | mg/L | 2.2881 | 2.6191 | 0.062659 | 1.2031 |  |  |  |  | Raw.Trb. | 1.44 | Cmb.Trb. | 0.03
23 | Pres. | 94078100 | 846349 | 2002320 | 3583560 | 145241000 | 1486420 | 4560660 | 7863110 | 835000 | 89990 | 924990 | now | 1010562500 |  | 0 | 1.07 | now | 1254.7 | 1969.3 | 22.3 | 30.9 | 1319.2 | 2102.4 | 39.5 | 4.6 | "/lb | 1.9375 | 8.125 | 1.25 | 9 | 0 | Raw | 9.4 | 7.4 | ef.turb.1 | 0 | ef.turb.2 | 0.059
| Prev | 94078100 | 846349 | 2002320 | 3583560 | 144406000 | 1486420 | 4524670 | 7809110 |  |  |  | prev | 1009743500 |  |  |  | prev | 1254.7 | 1958.9 | 22.3 | 30.9 | 1319.2 | 2091.4 | 39.4 | 4.6 | Lbs. | 20.8087 | 17.875 | 0.3125 | 9 |  | Trtd | 9.6 | 7.71 | AC.1 | 0 | AC.2 | 0.847
| Total | 0 | 0 | 0 | 0 | 835000 | 0 | 35990 | 54000 |  |  |  | Total | 819000 |  |  |  | Total | 0 | 10.4 | 0 | 0 | 0 | 11 | 0.1 | 0 | mg/L | 2.9881 | 2.5668 | 0.044874 | 1.2924 |  |  |  |  | Raw.Trb. | 1.78 | Cmb.Trb. | 0.032
24 | Pres. | 94078100 | 846349 | 2002320 | 3583560 | 146272000 | 1494420 | 4596660 | 7922100 | 1031000 | 102990 | 1133990 | now | 1011410000 |  | 0.03 | 1.1 | now | 1254.7 | 1982.2 | 22.5 | 31 | 1319.2 | 2116 | 39.7 | 4.6 | "/lb | 2 | 10 | 2 | 11 | 0 | Raw | 9.6 | 7.57 | ef.turb.1 | 0 | ef.turb.2 | 0.039
| Prev | 94078100 | 846349 | 2002320 | 3583560 | 145241000 | 1486420 | 4560660 | 7863110 |  |  |  | prev | 1010562500 |  |  |  | prev | 1254.7 | 1969.3 | 22.3 | 30.9 | 1319.2 | 2102.4 | 39.5 | 4.6 | Lbs. | 21.48 | 22 | 0.5 | 11 |  | Trtd | 10.2 | 7.65 | AC.1 | 0 | AC.2 | 0.548
| Total | 0 | 0 | 0 | 0 | 1031000 | 8000 | 36000 | 58990 |  |  |  | Total | 847500 |  |  |  | Total | 0 | 12.9 | 0.2 | 0.1 | 0 | 13.6 | 0.2 | 0 | mg/L | 2.4981 | 2.5586 | 0.058149 | 1.2793 |  |  |  |  | Raw.Trb. | 1.5 | Cmb.Trb. | 0.034
25 | Pres. | 94078100 | 846349 | 2002320 | 3583560 | 146605000 | 1494420 | 4596660 | 7922100 | 333000 | 0 | 333000 | now | 1012151800 |  | 0 | 1.07 | now | 1254.7 | 1986.3 | 22.5 | 31 | 1319.2 | 2120.2 | 39.7 | 4.6 | "/lb | 0.75 | 3.25 | 0.75 | 3 | 0 | Raw | 10.2 | 7.5 | ef.turb.1 | 0 | ef.turb.2 | 0.05
| Prev | 94078100 | 846349 | 2002320 | 3583560 | 146272000 | 1494420 | 4596660 | 7922100 |  |  |  | prev | 1011410000 |  |  |  | prev | 1254.7 | 1982.2 | 22.5 | 31 | 1319.2 | 2116 | 39.7 | 4.6 | Lbs. | 8.055 | 7.15 | 0.1875 | 3 |  | Trtd | 10.5 | 7.66 | AC.1 | 0 | AC.2 | 0.589
| Total | 0 | 0 | 0 | 0 | 333000 | 0 | 0 | 0 |  |  |  | Total | 741800 |  |  |  | Total | 0 | 4.1 | 0 | 0 | 0 | 4.2 | 0 | 0 | mg/L | 2.9004 | 2.5745 | 0.067514 | 1.0802 |  |  |  |  | Raw.Trb. | 1.45 | Cmb.Trb. | 0.048
26 | Pres. | 94078100 | 846349 | 2002320 | 3583560 | 147354000 | 1502420 | 4596660 | 7938100 | 749000 | 24000 | 773000 | now | 1012986800 |  | 0 | 1 | now | 1254.7 | 1995.5 | 22.5 | 31.1 | 1319.2 | 2129.7 | 39.7 | 4.6 | "/lb | 1.375 | 7.375 | 2 | 8 | 0 | Raw | 10.3 | 7.67 | ef.turb.1 | 0 | ef.turb.2 | 0.043
| Prev | 94078100 | 846349 | 2002320 | 3583560 | 146605000 | 1494420 | 4596660 | 7922100 |  |  |  | prev | 1012151800 |  |  |  | prev | 1254.7 | 1986.3 | 22.5 | 31 | 1319.2 | 2120.2 | 39.7 | 4.6 | Lbs. | 14.7675 | 16.225 | 0.5 | 8 |  | Trtd | 10.4 | 7.73 | AC.1 | 0 | AC.2 | 0.45
| Total | 0 | 0 | 0 | 0 | 749000 | 8000 | 0 | 16000 |  |  |  | Total | 835000 |  |  |  | Total | 0 | 9.2 | 0 | 0.1 | 0 | 9.5 | 0 | 0 | mg/L | 2.3641 | 2.5974 | 0.080043 | 1.2807 |  |  |  |  | Raw.Trb. | 1.47 | Cmb.Trb. | 0.04
27 | Pres. | 94078100 | 846349 | 2002320 | 3583560 | 148324000 | 1509420 | 4632660 | 8011100 | 970000 | 116000 | 1086000 | now | 1013873000 |  | 0 | 0.97 | now | 1254.7 | 2007.6 | 22.7 | 31.2 | 1319.2 | 2142.7 | 39.9 | 4.6 | "/lb | 1.875 | 9.75 | 2 | 10 | 0 | Raw | 9.6 | 7.62 | ef.turb.1 | 0 | ef.turb.2 | 0.06
| Prev | 94078100 | 846349 | 2002320 | 3583560 | 147354000 | 1502420 | 4596660 | 7938100 |  |  |  | prev | 1012986800 |  |  |  | prev | 1254.7 | 1995.5 | 22.5 | 31.1 | 1319.2 | 2129.7 | 39.7 | 4.6 | Lbs. | 20.1375 | 21.45 | 0.5 | 10 |  | Trtd | 8.3 | 7.94 | AC.1 | 0 | AC.2 | 0.43
| Total | 0 | 0 | 0 | 0 | 970000 | 7000 | 36000 | 73000 |  |  |  | Total | 886200 |  |  |  | Total | 0 | 12.1 | 0.2 | 0.1 | 0 | 13 | 0.2 | 0 | mg/L | 2.4892 | 2.6515 | 0.061806 | 1.2361 |  |  |  |  | Raw.Trb. | 1.33 | Cmb.Trb. | 0.03
28 | Pres. | 94078100 | 846349 | 2002320 | 3583560 | 149182000 | 1509420 | 4632660 | 8019110 | 858000 | 8010 | 866010 | now | 1014622800 |  | 0.13 | 0.98 | now | 1254.7 | 2018.3 | 22.7 | 31.2 | 1319.2 | 2153.6 | 39.9 | 4.6 | "/lb | 1.5 | 8.5 | 1.5 | 9 | 0 | Raw | 10.4 | 7.53 | ef.turb.1 | 0 | ef.turb.2 | 0.04
| Prev | 94078100 | 846349 | 2002320 | 3583560 | 148324000 | 1509420 | 4632660 | 8011100 |  |  |  | prev | 1013873000 |  |  |  | prev | 1254.7 | 2007.6 | 22.7 | 31.2 | 1319.2 | 2142.7 | 39.9 | 4.6 | Lbs. | 16.11 | 18.7 | 0.375 | 9 |  | Trtd | 8.9 | 7.87 | AC.1 | 0 | AC.2 | 0.59
| Total | 0 | 0 | 0 | 0 | 858000 | 0 | 0 | 8010 |  |  |  | Total | 749800 |  |  |  | Total | 0 | 10.7 | 0 | 0 | 0 | 10.9 | 0 | 0 | mg/L | 2.2513 | 2.6133 | 0.052406 | 1.2577 |  |  |  |  | Raw.Trb. | 1.43 | Cmb.Trb. | 0.04
29 | Pres. | 94078100 | 846349 | 2002320 | 3583560 | 149701000 | 1517420 | 4668650 | 8079130 | 519000 | 104010 | 623010 | now | 1015435900 |  | 0.01 | 1.01 | now | 1254.7 | 2025 | 22.9 | 31.3 | 1319.2 | 2160.9 | 40.1 | 4.6 | "/lb | 0.875 | 5.125 | 1.25 | 5 | 0 | Raw | 8.5 | 7.39 | ef.turb.1 | 0 | ef.turb.2 | 0.04
| Prev | 94078100 | 846349 | 2002320 | 3583560 | 149182000 | 1509420 | 4632660 | 8019110 |  |  |  | prev | 1014622800 |  |  |  | prev | 1254.7 | 2018.3 | 22.7 | 31.2 | 1319.2 | 2153.6 | 39.9 | 4.6 | Lbs. | 9.3975 | 11.275 | 0.3125 | 5 |  | Trtd | 8.4 | 7.94 | AC.1 | 0 | AC.2 | 0.54
| Total | 0 | 0 | 0 | 0 | 519000 | 8000 | 35990 | 60020 |  |  |  | Total | 813100 |  |  |  | Total | 0 | 6.7 | 0.2 | 0.1 | 0 | 7.3 | 0.2 | 0 | mg/L | 2.1711 | 2.6049 | 0.072197 | 1.1551 |  |  |  |  | Raw.Trb. | 1.71 | Cmb.Trb. | 0.03
30 | Pres. | 94878700 | 846349 | 2038320 | 3605550 | 149838000 | 1517420 | 4668650 | 8079130 | 937600 | 57990 | 995590 | now | 1016261000 |  | 0 | 0.96 | now | 1265 | 2026.5 | 22.9 | 31.3 | 1329.8 | 2162.6 | 40.3 | 4.7 | "/lb | 1.75 | 9.9375 | 1.9375 | 9 | 1 | Raw | 8.8 | 7.21 | ef.turb.1 | 0 | ef.turb.2 | 0.04
| Prev | 94078100 | 846349 | 2002320 | 3583560 | 149701000 | 1517420 | 4668650 | 8079130 |  |  |  | prev | 1015435900 |  |  |  | prev | 1254.7 | 2025 | 22.9 | 31.3 | 1319.2 | 2160.9 | 40.1 | 4.6 | Lbs. | 18.795 | 21.8625 | 0.48438 | 10 |  | Trtd | 8.5 | 7.68 | AC.1 | 0 | AC.2 | 0.49
| Total | 800600 | 0 | 36000 | 21990 | 137000 | 0 | 0 | 0 |  |  |  | Total | 825100 |  |  |  | Total | 10.3 | 1.5 | 0 | 0 | 10.6 | 1.7 | 0.2 | 0.1 | mg/L | 2.4036 | 2.7959 | 0.061944 | 1.2788 |  |  |  |  | Raw.Trb. | 1.51 | Cmb.Trb. | 0.04
31 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 150250000 | 1517420 | 4668650 | 8095140 | 753800 | 23010 | 776810 | now | 1017069700 |  | 0 | 0.99 | now | 1269.4 | 2031.5 | 22.9 | 31.4 | 1334.3 | 2167.9 | 40.3 | 4.7 | "/lb | 1.25 | 7.5 | 1.5 | 8 | 0 | Raw | 9 | 7.27 | ef.turb.1 | 0.038 | ef.turb.2 | 0
| Prev | 94878700 | 846349 | 2038320 | 3605550 | 149838000 | 1517420 | 4668650 | 8079130 |  |  |  | prev | 1016261000 |  |  |  | prev | 1265 | 2026.5 | 22.9 | 31.3 | 1329.8 | 2162.6 | 40.3 | 4.7 | Lbs. | 13.425 | 16.5 | 0.375 | 8 |  | Trtd | 9.8 | 7.56 | AC.1 | 0.385 | AC.2 | 0
| Total | 341800 | 7000 | 0 | 0 | 412000 | 0 | 0 | 16010 |  |  |  | Total | 808700 |  |  |  | Total | 4.4 | 5 | 0 | 0.1 | 4.5 | 5.3 | 0 | 0 | mg/L | 2.1355 | 2.6246 | 0.05965 | 1.2725 |  |  |  |  | Raw.Trb. | 1.38 | Cmb.Trb. | 0.035
[10 empty] | Totals | [6 empty] | AVG | [10 empty] | totals | [5 empty] | AVG TRTD |  |  |  | Avg.Cmb.Trb.
[10 empty] | 23784900 | 2072570 | 25857470 |  | 25456740 |  | 1.79 | 1.0206 | [5 empty] | 125.6 | 200.9 |  |  |  | 473.9025 | 541.75 | 13.3125 | 247 |  |  | 9.1065 | 7.7655 |  |  | 0.036129
[22 empty] | total- | 326.5

## Apr, 2021
April, 2021
Filters | [15 empty] | Rain | Cl2 | Pump Hours | [8 empty] | Chemicals | [5 empty] | Misc. |  |  | Turbidity
Day |  | CW.Tot.1 | Cla.Wst.1 | BW.Wst.1 | FTWst.1 | CW.Tot.2 | Cla.Wst.2 | BW.Wst.2 | FTWst.2 | Treated Total | Wastewater | Total Influent | Totalizer |  |  | Inches | Resid | Pump | Ef.Pmp.1 | Ef.Pmp.2 | Blo.1 | Blo.2 | URT.1 | URT.2 | BWP | SWP | Chem | ACH | SA | Poly | Cl2.1 | Cl2.2 | water | Temp | pH | F1 |  | F2
1 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 151024000 | 1525430 | 4668650 | 8112140 | 774000 | 25010 | 799010 | now | 1017910400 |  | 0 | 1.08 | now | 1269.4 | 2041 | 22.9 | 31.5 | 1334.3 | 2177.8 | 40.3 | 4.7 | "/lb | 1.4375 | 7.25 | 1.5 | 0 | 8 | Raw | 10.8 | 7.31 | ef.turb.1 | 0 | ef.turb.2 | 0.041
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 150250000 | 1517420 | 4668650 | 8095140 |  |  |  | prev | 1017069700 |  |  |  | prev | 1269.4 | 2031.5 | 22.9 | 31.4 | 1334.3 | 2167.9 | 40.3 | 4.7 | Lbs. | 15.4388 | 15.95 | 0.375 | 8 |  | Trtd | 10.5 | 7.64 | AC.1 | 0 | AC.2 | 0.438
| Total | 0 | 0 | 0 | 0 | 774000 | 8010 | 0 | 17000 |  |  |  | Total | 840700 |  |  |  | Total | 0 | 9.5 | 0 | 0.1 | 0 | 9.9 | 0 | 0 | mg/L | 2.3917 | 2.4709 | 0.058093 | 1.2393 |  |  |  |  | Raw.Trb. | 1.12 | Cmb.Trb. | 0.036
2 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 151807000 | 1533430 | 4704650 | 8155160 | 783000 | 87020 | 870020 | now | 1018705900 |  | 0 | 1.01 | now | 1269.4 | 2050.8 | 23.1 | 31.6 | 1334.3 | 2188.1 | 40.5 | 4.7 | "/lb | 1.5 | 7.9375 | 2 | 0 | 8 | Raw | 10.9 | 7.29 | ef.turb.1 | 0 | ef.turb.2 | 0.038
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 151024000 | 1525430 | 4668650 | 8112140 |  |  |  | prev | 1017910400 |  |  |  | prev | 1269.4 | 2041 | 22.9 | 31.5 | 1334.3 | 2177.8 | 40.3 | 4.7 | Lbs. | 16.11 | 17.4625 | 0.5 | 8 |  | Trtd | 10.3 | 7.78 | AC.1 | 0 | AC.2 | 0.484
| Total | 0 | 0 | 0 | 0 | 783000 | 8000 | 36000 | 43020 |  |  |  | Total | 795500 |  |  |  | Total | 0 | 9.8 | 0.2 | 0.1 | 0 | 10.3 | 0.2 | 0 | mg/L | 2.467 | 2.6741 | 0.076567 | 1.2251 |  |  |  |  | Raw.Trb. | 1.27 | Cmb.Trb. | 0.032
10.6
3 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 152503000 | 1533430 | 4704650 | 8163170 | 696000 | 8010 | 704010 | now | 1019474600 |  | 0 | 1 | now | 1269.4 | 2059.5 | 23.1 | 31.6 | 1334.3 | 2196.8 | 40.5 | 4.7 | "/lb | 1.5 | 6.875 | 1.375 | 0 | 8 | Raw | 9.9 | 7.38 | ef.turb.1 | 0 | ef.turb.2 | 0.039
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 151807000 | 1533430 | 4704650 | 8155160 |  |  |  | prev | 1018705900 |  |  |  | prev | 1269.4 | 2050.8 | 23.1 | 31.6 | 1334.3 | 2188.1 | 40.5 | 4.7 | Lbs. | 16.11 | 15.125 | 0.34375 | 8 |  | Trtd | 10 | 7.96 | AC.1 | 0 | AC.2 | 0.332
| Total | 0 | 0 | 0 | 0 | 696000 | 0 | 0 | 8010 |  |  |  | Total | 768700 |  |  |  | Total | 0 | 8.7 | 0 | 0 | 0 | 8.7 | 0 | 0 | mg/L | 2.7754 | 2.6057 | 0.05922 | 1.3782 |  |  |  |  | Raw.Trb. | 1.21 | Cmb.Trb. | 0.033
4 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 153297000 | 1533430 | 4740650 | 8186170 | 794000 | 59000 | 853000 | now | 1020152500 |  | 0 | 1.05 | now | 1269.4 | 2069.4 | 23.1 | 31.6 | 1334.3 | 2206 | 40.7 | 4.7 | "/lb | 1.25 | 7.625 | 1.75 | 8 | 0 | Raw | 11.7 | 7.4 | ef.turb.1 | 0 | ef.turb.2 | 0.036
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 152503000 | 1533430 | 4704650 | 8163170 |  |  |  | prev | 1019474600 |  |  |  | prev | 1269.4 | 2059.5 | 23.1 | 31.6 | 1334.3 | 2196.8 | 40.5 | 4.7 | Lbs. | 13.425 | 16.775 | 0.4375 | 8 |  | Trtd | 10.3 | 7.79 | AC.1 | 0 | AC.2 | 0.387
| Total | 0 | 0 | 0 | 0 | 794000 | 0 | 36000 | 23000 |  |  |  | Total | 677900 |  |  |  | Total | 0 | 9.9 | 0 | 0 | 0 | 9.2 | 0.2 | 0 | mg/L | 2.0273 | 2.5332 | 0.066068 | 1.2081 |  |  |  |  | Raw.Trb. | 1.17 | Cmb.Trb. | 0.032
5 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 153914000 | 1540430 | 4740650 | 8202180 | 617000 | 23010 | 640010 | now | 1020983650 | 0 | 0 | 1.05 | now | 1269.4 | 2077.1 | 23.1 | 31.7 | 1334.3 | 2214.9 | 40.7 | 4.7 | "/lb | 1.25 | 6.3125 | 1.25 | 6 | 0 | Raw | 9.8 | 7.49 | ef.turb.1 | 0 | ef.turb.2 | 0.04
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 153297000 | 1533430 | 4740650 | 8186170 |  |  |  | prev | 1020152500 |  |  |  | prev | 1269.4 | 2069.4 | 23.1 | 31.6 | 1334.3 | 2206 | 40.7 | 4.7 | Lbs. | 13.425 | 13.8875 | 0.3125 | 6 |  | Trtd | 9.2 | 8.04 | AC.1 | 0 | AC.2 | 0.306
| Total | 0 | 0 | 0 | 0 | 617000 | 7000 | 0 | 16010 |  |  |  | Total | 831150 |  |  |  | Total | 0 | 7.7 | 0 | 0.1 | 0 | 8.9 | 0 | 0 | mg/L | 2.6089 | 2.6988 | 0.060729 | 1.166 |  |  |  |  | Raw.Trb. | 1.18 | Cmb.Trb. | 0.03
6 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 154781000 | 1540430 | 4776650 | 8225190 | 867000 | 59010 | 926010 | now | 1021817800 |  | 0 | 0.98 | now | 1269.4 | 2087.9 | 23.2 | 31.8 | 1334.3 | 2226 | 40.9 | 4.7 | "/lb | 1.5 | 7.125 | 1.75 | 0 | 9 | Raw | 10 | 7.41 | ef.turb.1 | 0 | ef.turb.2 | 0.04
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 153914000 | 1540430 | 4740650 | 8202180 |  |  |  | prev | 1020983650 |  |  |  | prev | 1269.4 | 2077.1 | 23.1 | 31.7 | 1334.3 | 2214.9 | 40.7 | 4.7 | Lbs. | 16.11 | 15.675 | 0.4375 | 9 |  | Trtd | 9.2 | 7.99 | AC.1 | 0 | AC.2 | 0.38
| Total | 0 | 0 | 0 | 0 | 867000 | 0 | 36000 | 23010 |  |  |  | Total | 834150 |  |  |  | Total | 0 | 10.8 | 0.1 | 0.1 | 0 | 11.1 | 0.2 | 0 | mg/L | 2.228 | 2.1678 | 0.060505 | 1.2447 |  |  |  |  | Raw.Trb. | 1.31 | Cmb.Trb. | 0.04
7 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 155491000 | 1548430 | 4776650 | 8233190 | 710000 | 16000 | 726000 | now | 1022623800 |  | 0.11 | 1 | now | 1269.4 | 2096.7 | 23.3 | 31.8 | 1334.3 | 2235 | 40.9 | 4.7 | "/lb | 1.5 | 6.9375 | 1.625 | 0 | 7 | Raw | 10.1 | 7.43 | ef.turb.1 | 0 | ef.turb.2 | 0.042
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 154781000 | 1540430 | 4776650 | 8225190 |  |  |  | prev | 1021817800 |  |  |  | prev | 1269.4 | 2087.9 | 23.2 | 31.8 | 1334.3 | 2226 | 40.9 | 4.7 | Lbs. | 16.11 | 15.2625 | 0.40625 | 7 |  | Trtd | 10.6 | 7.73 | AC.1 | 0 | AC.2 | 0.336
| Total | 0 | 0 | 0 | 0 | 710000 | 8000 | 0 | 8000 |  |  |  | Total | 806000 |  |  |  | Total | 0 | 8.8 | 0.1 | 0 | 0 | 9 | 0 | 0 | mg/L | 2.7206 | 2.5775 | 0.068607 | 1.1822 |  |  |  |  | Raw.Trb. | 1.29 | Cmb.Trb. | 0.039
8 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 156212000 | 1548430 | 4816640 | 8255200 | 721000 | 62000 | 783000 | now | 1023377200 |  | 0 | 1.02 | now | 1269.4 | 2105.7 | 23.4 | 31.9 | 1334.3 | 2244.2 | 41.1 | 4.7 | "/lb | 1.25 | 6.5 | 1.75 | 0 | 8 | Raw | 10.8 | 7.48 | ef.turb.1 | 0 | ef.turb.2 | 0.04
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 155491000 | 1548430 | 4776650 | 8233190 |  |  |  | prev | 1022623800 |  |  |  | prev | 1269.4 | 2096.7 | 23.3 | 31.8 | 1334.3 | 2235 | 40.9 | 4.7 | Lbs. | 13.425 | 14.3 | 0.4375 | 8 |  | Trtd | 10.6 | 7.66 | AC.1 | 0 | AC.2 | 0.396
| Total | 0 | 0 | 0 | 0 | 721000 | 0 | 39990 | 22010 |  |  |  | Total | 753400 |  |  |  | Total | 0 | 9 | 0.1 | 0.1 | 0 | 9.2 | 0.2 | 0 | mg/L | 2.2326 | 2.3781 | 0.072757 | 1.3304 |  |  |  |  | Raw.Trb. | 1.25 | Cmb.Trb. | 0.035
9 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 156889000 | 1556430 | 4816640 | 8264210 | 677000 | 17010 | 694010 | now | 1024197900 |  | 0.05 | 1.01 | now | 1269.4 | 2114 | 23.4 | 32 | 1334.3 | 2252.8 | 41.1 | 4.7 | "/lb | 1.375 | 5.5 | 1.75 | 0 | 7 | Raw | 11.1 | 7.52 | ef.turb.1 | 0 | ef.turb.2 | 0.063
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 156212000 | 1548430 | 4816640 | 8255200 |  |  |  | prev | 1023377200 |  |  |  | prev | 1269.4 | 2105.7 | 23.4 | 31.9 | 1334.3 | 2244.2 | 41.1 | 4.7 | Lbs. | 14.7675 | 12.1 | 0.4375 | 7 |  | Trtd | 11.4 | 7.9 | AC.1 | 0 | AC.2 | 0.301
| Total | 0 | 0 | 0 | 0 | 677000 | 8000 | 0 | 9010 |  |  |  | Total | 820700 |  |  |  | Total | 0 | 8.3 | 0 | 0.1 | 0 | 8.6 | 0 | 0 | mg/L | 2.6155 | 2.143 | 0.077486 | 1.2398 |  |  |  |  | Raw.Trb. | 1.4 | Cmb.Trb. | 0.06
10 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 157633000 | 1556430 | 4816640 | 8267210 | 744000 | 3000 | 747000 | now | 1024978400 |  | 0 | 0.97 | now | 1269.4 | 2123.2 | 23.4 | 32 | 1334.3 | 2262.1 | 41.1 | 4.7 | "/lb | 1.375 | 7.625 | 1.5 | 0 | 8 | Raw | 10.8 | 7.58 | ef.turb.1 | 0 | ef.turb.2 | 0.04
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 156889000 | 1556430 | 4816640 | 8264210 |  |  |  | prev | 1024197900 |  |  |  | prev | 1269.4 | 2114 | 23.4 | 32 | 1334.3 | 2252.8 | 41.1 | 4.7 | Lbs. | 14.7675 | 16.775 | 0.375 | 8 |  | Trtd | 9.5 | 8.02 | AC.1 | 0 | AC.2 | 0.36
| Total | 0 | 0 | 0 | 0 | 744000 | 0 | 0 | 3000 |  |  |  | Total | 780500 |  |  |  | Total | 0 | 9.2 | 0 | 0 | 0 | 9.3 | 0 | 0 | mg/L | 2.38 | 2.7035 | 0.060436 | 1.2893 |  |  |  |  | Raw.Trb. | 1.32 | Cmb.Trb. | 0.03
11 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 158637000 | 1564430 | 4849640 | 8328230 | 1004000 | 102020 | 1106020 | now | 1025744200 |  | 0 | 0.97 | now | 1269.4 | 2135.8 | 23.4 | 32.2 | 1334.3 | 2275.5 | 41.1 | 4.7 | "/lb | 1.75 | 8.875 | 2 | 11 | 0 | Raw | 11.2 | 7.5 | ef.turb.1 | 0 | ef.turb.2 | 0.04
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 157633000 | 1556430 | 4816640 | 8267210 |  |  |  | prev | 1024978400 |  |  |  | prev | 1269.4 | 2123.2 | 23.4 | 32 | 1334.3 | 2262.1 | 41.1 | 4.7 | Lbs. | 18.795 | 19.525 | 0.5 | 11 |  | Trtd | 9.6 | 7.97 | AC.1 | 0 | AC.2 | 0.44
| Total | 0 | 0 | 0 | 0 | 1004000 | 8000 | 33000 | 61020 |  |  |  | Total | 765800 |  |  |  | Total | 0 | 12.6 | 0 | 0.2 | 0 | 13.4 | 0 | 0 | mg/L | 2.2446 | 2.3318 | 0.059713 | 1.3137 |  |  |  |  | Raw.Trb. | 1.35 | Cmb.Trb. | 0.03
12 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 159165000 | 1571430 | 4849640 | 8344240 | 528000 | 23010 | 551010 | now | 1026574100 |  | 0 | 1.05 | now | 1269.4 | 2142.4 | 23.6 | 32.2 | 1334.3 | 2282.4 | 41.3 | 4.7 | "/lb | 1 | 5.125 | 0.875 | 0 | 6 | Raw | 8.7 | 7.45 | ef.turb.1 | 0 | ef.turb.2 | 0.05
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 158637000 | 1564430 | 4849640 | 8328230 |  |  |  | prev | 1025744200 |  |  |  | prev | 1269.4 | 2135.8 | 23.4 | 32.2 | 1334.3 | 2275.5 | 41.1 | 4.7 | Lbs. | 10.74 | 11.275 | 0.21875 | 6 |  | Trtd | 8.7 | 7.89 | AC.1 | 0 | AC.2 | 0.39
| Total | 0 | 0 | 0 | 0 | 528000 | 7000 | 0 | 16010 |  |  |  | Total | 829900 |  |  |  | Total | 0 | 6.6 | 0.2 | 0 | 0 | 6.9 | 0.2 | 0 | mg/L | 2.439 | 2.5605 | 0.049676 | 1.3625 |  |  |  |  | Raw.Trb. | 1.37 | Cmb.Trb. | 0.04
13 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 160115000 | 1579430 | 4881640 | 8398260 | 950000 | 94020 | 1044020 | now | 1027429000 |  | 0 | 1.05 | now | 1269.4 | 2154.3 | 23.7 | 32.2 | 1334.3 | 2295 | 41.5 | 4.7 | "/lb | 1.75 | 9 | 1.875 | 0 | 11 | Raw | 9.8 | 7.28 | ef.turb.1 | 0 | ef.turb.2 | 0.049
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 159165000 | 1571430 | 4849640 | 8344240 |  |  |  | prev | 1026574100 |  |  |  | prev | 1269.4 | 2142.4 | 23.6 | 32.2 | 1334.3 | 2282.4 | 41.3 | 4.7 | Lbs. | 18.795 | 19.8 | 0.46875 | 11 |  | Trtd | 9.8 | 7.68 | AC.1 | 0 | AC.2 | 0.478
| Total | 0 | 0 | 0 | 0 | 950000 | 8000 | 32000 | 54020 |  |  |  | Total | 854900 |  |  |  | Total | 0 | 11.9 | 0.1 | 0 | 0 | 12.6 | 0.2 | 0 | mg/L | 2.3722 | 2.4991 | 0.059163 | 1.3884 |  |  |  |  | Raw.Trb. | 1.32 | Cmb.Trb. | 0.028
14 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 160972000 | 1587430 | 4914640 | 8451280 | 857000 | 94020 | 951020 | now | 1028295400 |  | 0 | 1.03 | now | 1269.4 | 2165 | 23.8 | 32.4 | 1334.3 | 2306.4 | 41.7 | 4.7 | "/lb | 1.75 | 7.9375 | 1.5 | 0 | 10 | Raw | 11 | 7.25 | ef.turb.1 | 0 | ef.turb.2 | 0.05
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 160115000 | 1579430 | 4881640 | 8398260 |  |  |  | prev | 1027429000 |  |  |  | prev | 1269.4 | 2154.3 | 23.7 | 32.2 | 1334.3 | 2295 | 41.5 | 4.7 | Lbs. | 18.795 | 17.4625 | 0.375 | 10 |  | Trtd | 10.4 | 7.79 | AC.1 | 0 | AC.2 | 0.411
| Total | 0 | 0 | 0 | 0 | 857000 | 8000 | 33000 | 53020 |  |  |  | Total | 866400 |  |  |  | Total | 0 | 10.7 | 0.1 | 0.2 | 0 | 11.4 | 0.2 | 0 | mg/L | 2.6296 | 2.4432 | 0.052467 | 1.3991 |  |  |  |  | Raw.Trb. | 1.19 | Cmb.Trb. | 0.029
15 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 161715000 | 1595430 | 4914640 | 8468290 | 743000 | 25010 | 768010 | now | 1029186800 |  | 0 | 1 | now | 1269.4 | 2174.2 | 23.9 | 32.4 | 1334.3 | 2315.9 | 41.7 | 4.7 | "/lb | 1.5 | 6.5 | 1.25 | 0 | 8 | Raw | 12 | 7.47 | ef.turb.1 | 0 | ef.turb.2 | 0.04
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 160972000 | 1587430 | 4914640 | 8451280 |  |  |  | prev | 1028295400 |  |  |  | prev | 1269.4 | 2165 | 23.8 | 32.4 | 1334.3 | 2306.4 | 41.7 | 4.7 | Lbs. | 16.11 | 14.3 | 0.3125 | 8 |  | Trtd | 11.2 | 7.7 | AC.1 | 0 | AC.2 | 0.377
| Total | 0 | 0 | 0 | 0 | 743000 | 8000 | 0 | 17010 |  |  |  | Total | 891400 |  |  |  | Total | 0 | 9.2 | 0.1 | 0 | 0 | 9.5 | 0 | 0 | mg/L | 2.5998 | 2.3077 | 0.050431 | 1.291 |  |  |  |  | Raw.Trb. | 2.17 | Cmb.Trb. | 0.023
16 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 162743000 | 1595430 | 4946630 | 8529310 | 1028000 | 93010 | 1121010 | now | 1030169500 |  | 0 | 1.01 | now | 1269.4 | 2187 | 24 | 32.5 | 1334.3 | 2329.4 | 41.8 | 4.7 | "/lb | 2.125 | 10.125 | 2.125 | 0 | 15 | Raw | 11.6 | 7.77 | ef.turb.1 | 0 | ef.turb.2 | 0.042
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 161715000 | 1595430 | 4914640 | 8468290 |  |  |  | prev | 1029186800 |  |  |  | prev | 1269.4 | 2174.2 | 23.9 | 32.4 | 1334.3 | 2315.9 | 41.7 | 4.7 | Lbs. | 22.8225 | 22.275 | 0.53125 | 15 |  | Trtd | 10.6 | 7.49 | AC.1 | 0 | AC.2 | 0.39
| Total | 0 | 0 | 0 | 0 | 1028000 | 0 | 31990 | 61020 |  |  |  | Total | 982700 |  |  |  | Total | 0 | 12.8 | 0.1 | 0.1 | 0 | 13.5 | 0.1 | 0 | mg/L | 2.662 | 2.5981 | 0.061964 | 1.7496 |  |  |  |  | Raw.Trb. | 1.33 | Cmb.Trb. | 0.026
17 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 163572000 | 1603430 | 4946630 | 8537320 | 829000 | 16010 | 845010 | now | 1031114800 |  | 0 | 1.1 | now | 1269.4 | 2197.3 | 24 | 32.6 | 1334.3 | 2339.8 | 41.8 | 4.7 | "/lb | 1.5 | 8 | 1.5 | 0 | 11 | Raw | 12.4 | 7.55 | ef.turb.1 | 0 | ef.turb.2 | 0.039
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 162743000 | 1595430 | 4946630 | 8529310 |  |  |  | prev | 1030169500 |  |  |  | prev | 1269.4 | 2187 | 24 | 32.5 | 1334.3 | 2329.4 | 41.8 | 4.7 | Lbs. | 16.11 | 17.6 | 0.375 | 11 |  | Trtd | 11.4 | 7.89 | AC.1 | 0 | AC.2 | 0.279
| Total | 0 | 0 | 0 | 0 | 829000 | 8000 | 0 | 8010 |  |  |  | Total | 945300 |  |  |  | Total | 0 | 10.3 | 0 | 0.1 | 0 | 10.4 | 0 | 0 | mg/L | 2.3301 | 2.5456 | 0.054239 | 1.591 |  |  |  |  | Raw.Trb. | 1.49 | Cmb.Trb. | 0.024
18 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 164642000 | 1610430 | 4979630 | 8586340 | 1070000 | 89020 | 1159020 | now | 1032135300 |  | 0 | 1.11 | now | 1269.4 | 2210.5 | 24.2 | 32.7 | 1334.3 | 2353.9 | 42 | 4.7 | "/lb | 1.375 | 9.75 | 1.34 | 0 | 14 | Raw | 12 | 7.53 | ef.turb.1 | 0 | ef.turb.2 | 0.037
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 163572000 | 1603430 | 4946630 | 8537320 |  |  |  | prev | 1031114800 |  |  |  | prev | 1269.4 | 2197.3 | 24 | 32.6 | 1334.3 | 2339.8 | 41.8 | 4.7 | Lbs. | 14.7675 | 21.45 | 0.335 | 14 |  | Trtd | 11.6 | 8.01 | AC.1 | 0 | AC.2 | 0.346
| Total | 0 | 0 | 0 | 0 | 1070000 | 7000 | 33000 | 49020 |  |  |  | Total | 1020500 |  |  |  | Total | 0 | 13.2 | 0.2 | 0.1 | 0 | 14.1 | 0.2 | 0 | mg/L | 1.6548 | 2.4037 | 0.03754 | 1.5688 |  |  |  |  | Raw.Trb. | 1.69 | Cmb.Trb. | 0.022
19 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 165614000 | 1610430 | 5007630 | 8611350 | 972000 | 53010 | 1025010 | now | 1033142300 |  | 0 | 1.1 | now | 1269.4 | 2222.8 | 24.2 | 32.7 | 1334.3 | 2366.3 | 42.2 | 4.7 | "/lb | 2 | 9 | 1.625 | 0 | 12 | Raw | 11.9 | 7.43 | ef.turb.1 | 0 | ef.turb.2 | 0.04
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 164642000 | 1610430 | 4979630 | 8586340 |  |  |  | prev | 1032135300 |  |  |  | prev | 1269.4 | 2210.5 | 24.2 | 32.7 | 1334.3 | 2353.9 | 42 | 4.7 | Lbs. | 21.48 | 19.8 | 0.40625 | 12 |  | Trtd | 11.7 | 7.85 | AC.1 | 0 | AC.2 | 0.37
| Total | 0 | 0 | 0 | 0 | 972000 | 0 | 28000 | 25010 |  |  |  | Total | 1007000 |  |  |  | Total | 0 | 12.3 | 0 | 0 | 0 | 12.4 | 0.2 | 0 | mg/L | 2.6497 | 2.4425 | 0.050114 | 1.4803 |  |  |  |  | Raw.Trb. | 1.94 | Cmb.Trb. | 0.024
20 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 166362000 | 1618430 | 5007630 | 8627350 | 748000 | 24000 | 772000 | now | 1034041900 |  | 0 | 1.07 | now | 1269.4 | 2232 | 24.2 | 32.8 | 1334.3 | 2375.9 | 42.2 | 4.7 | "/lb | 1.75 | 6.5 | 1.25 | 0 | 9 | Raw | 11.7 | 7.31 | ef.turb.1 | 0 | ef.turb.2 | 0.04
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 165614000 | 1610430 | 5007630 | 8611350 |  |  |  | prev | 1033142300 |  |  |  | prev | 1269.4 | 2222.8 | 24.2 | 32.7 | 1334.3 | 2366.3 | 42.2 | 4.7 | Lbs. | 18.795 | 14.3 | 0.3125 | 9 |  | Trtd | 11.5 | 7.88 | AC.1 | 0 | AC.2 | 0.27
| Total | 0 | 0 | 0 | 0 | 748000 | 8000 | 0 | 16000 |  |  |  | Total | 899600 |  |  |  | Total | 0 | 9.2 | 0 | 0.1 | 0 | 9.6 | 0 | 0 | mg/L | 3.0128 | 2.2923 | 0.050094 | 1.4427 |  |  |  |  | Raw.Trb. | 1.6 | Cmb.Trb. | 0.03
21 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 167499000 | 1626430 | 5036630 | 8676370 | 1137000 | 86020 | 1223020 | now | 1035093000 |  | 0 | 1.06 | now | 1269.4 | 2246.6 | 24.3 | 33 | 1334.3 | 2391.1 | 42.3 | 4.7 | "/lb | 2.25 | 10.25 | 2 | 0 | 14 | Raw | 10.6 | 7.36 | ef.turb.1 | 0 | ef.turb.2 | 0.04
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 166362000 | 1618430 | 5007630 | 8627350 |  |  |  | prev | 1034041900 |  |  |  | prev | 1269.4 | 2232 | 24.2 | 32.8 | 1334.3 | 2375.9 | 42.2 | 4.7 | Lbs. | 24.165 | 22.55 | 0.5 | 14 |  | Trtd | 12.2 | 7.51 | AC.1 | 0 | AC.2 | 0.299
| Total | 0 | 0 | 0 | 0 | 1137000 | 8000 | 29000 | 49020 |  |  |  | Total | 1051100 |  |  |  | Total | 0 | 14.6 | 0.1 | 0.2 | 0 | 15.2 | 0.1 | 0 | mg/L | 2.5484 | 2.378 | 0.052728 | 1.4764 |  |  |  |  | Raw.Trb. | 2.47 | Cmb.Trb. | 0.03
22 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 168295000 | 1633430 | 5064630 | 8727390 | 796000 | 86020 | 882020 | now | 1035945500 |  | 0 | 1.04 | now | 1269.4 | 2256.8 | 24.5 | 33.1 | 1334.3 | 2402.1 | 42.5 | 4.7 | "/lb | 1.5 | 7.25 | 1.5 | 0 | 10 | Raw | 11.7 | 7.49 | ef.turb.1 | 0 | ef.turb.2 | 0.043
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 167499000 | 1626430 | 5036630 | 8676370 |  |  |  | prev | 1035093000 |  |  |  | prev | 1269.4 | 2246.6 | 24.3 | 33 | 1334.3 | 2391.1 | 42.3 | 4.7 | Lbs. | 16.11 | 15.95 | 0.375 | 10 |  | Trtd | 12.5 | 7.77 | AC.1 | 0 | AC.2 | 0.293
| Total | 0 | 0 | 0 | 0 | 796000 | 7000 | 28000 | 51020 |  |  |  | Total | 852500 |  |  |  | Total | 0 | 10.2 | 0.2 | 0.1 | 0 | 11 | 0.2 | 0 | mg/L | 2.4267 | 2.4026 | 0.056487 | 1.5063 |  |  |  |  | Raw.Trb. | 1.25 | Cmb.Trb. | 0.035
23 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 169415000 | 1641430 | 5064630 | 8735400 | 1120000 | 16010 | 1136010 | now | 1036903900 |  | 0.07 | 1.06 | now | 1269.4 | 2271.2 | 24.5 | 33.2 | 1334.3 | 2416.6 | 42.5 | 4.7 | "/lb | 1.875 | 10.25 | 1.5 | 15 | 0 | Raw | 11.9 | 7.41 | ef.turb.1 | 0 | ef.turb.2 | 0.042
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 168295000 | 1633430 | 5064630 | 8727390 |  |  |  | prev | 1035945500 |  |  |  | prev | 1269.4 | 2256.8 | 24.5 | 33.1 | 1334.3 | 2402.1 | 42.5 | 4.7 | Lbs. | 20.1375 | 22.55 | 0.375 | 15 |  | Trtd | 12.5 | 7.75 | AC.1 | 0 | AC.2 | 0.321
| Total | 0 | 0 | 0 | 0 | 1120000 | 8000 | 0 | 8010 |  |  |  | Total | 958400 |  |  |  | Total | 0 | 14.4 | 0 | 0.1 | 0 | 14.5 | 0 | 0 | mg/L | 2.1559 | 2.4141 | 0.040146 | 1.6059 |  |  |  |  | Raw.Trb. | 1.17 | Cmb.Trb. | 0.034
24 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 169992000 | 1649430 | 5093620 | 8769410 | 577000 | 71000 | 648000 | now | 1037707400 |  | 0.14 | 1.1 | now | 1269.4 | 2278.7 | 24.7 | 33.3 | 1334.3 | 2424.5 | 42.7 | 4.7 | "/lb | 1.25 | 5 | 1.125 | 7 | 0 | Raw | 11.5 | 7.56 | ef.turb.1 | 0 | ef.turb.2 | 0.04
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 169415000 | 1641430 | 5064630 | 8735400 |  |  |  | prev | 1036903900 |  |  |  | prev | 1269.4 | 2271.2 | 24.5 | 33.2 | 1334.3 | 2416.6 | 42.5 | 4.7 | Lbs. | 13.425 | 11 | 0.28125 | 7 |  | Trtd | 10.1 | 7.8 | AC.1 | 0 | AC.2 | 0.32
| Total | 0 | 0 | 0 | 0 | 577000 | 8000 | 28990 | 34010 |  |  |  | Total | 803500 |  |  |  | Total | 0 | 7.5 | 0.2 | 0.1 | 0 | 7.9 | 0.2 | 0 | mg/L | 2.7898 | 2.2859 | 0.058445 | 1.4546 |  |  |  |  | Raw.Trb. | 1.16 | Cmb.Trb. | 0.03
25 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 170772000 | 1649430 | 5093620 | 8785420 | 780000 | 16010 | 796010 | now | 1038412400 |  | 0.18 | 1 | now | 1269.4 | 2288.6 | 24.7 | 33.3 | 1334.3 | 2434.7 | 42.7 | 4.7 | "/lb | 1.875 | 6.625 | 2.3125 | 10 | 0 | Raw | 11.9 | 7.4 | ef.turb.1 | 0 | ef.turb.2 | 0.04
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 169992000 | 1649430 | 5093620 | 8769410 |  |  |  | prev | 1037707400 |  |  |  | prev | 1269.4 | 2278.7 | 24.7 | 33.3 | 1334.3 | 2424.5 | 42.7 | 4.7 | Lbs. | 20.1375 | 14.575 | 0.57812 | 10 |  | Trtd | 9.7 | 7.75 | AC.1 | 0 | AC.2 | 0.44
| Total | 0 | 0 | 0 | 0 | 780000 | 0 | 0 | 16010 |  |  |  | Total | 705000 |  |  |  | Total | 0 | 9.9 | 0 | 0 | 0 | 10.2 | 0 | 0 | mg/L | 3.0956 | 2.2405 | 0.088871 | 1.5372 |  |  |  |  | Raw.Trb. | 1.43 | Cmb.Trb. | 0.04
26 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 171229000 | 1656430 | 5122620 | 8834440 | 457000 | 85020 | 542020 | now | 1039226800 |  | 0 | 1.01 | now | 1269.4 | 2295.4 | 24.8 | 33.3 | 1334.3 | 2442.2 | 42.8 | 4.7 | "/lb | 1.25 | 4.5 | 1 | 0 | 6 | Raw | 10.7 | 7.44 | ef.turb.1 | 0 | ef.turb.2 | 0.04
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 170772000 | 1649430 | 5093620 | 8785420 |  |  |  | prev | 1038412400 |  |  |  | prev | 1269.4 | 2288.6 | 24.7 | 33.3 | 1334.3 | 2434.7 | 42.7 | 4.7 | Lbs. | 13.425 | 9.9 | 0.25 | 6 |  | Trtd | 10.6 | 7.83 | AC.1 | 0 | AC.2 | 0.31
| Total | 0 | 0 | 0 | 0 | 457000 | 7000 | 29000 | 49020 |  |  |  | Total | 814400 |  |  |  | Total | 0 | 6.8 | 0.1 | 0 | 0 | 7.5 | 0.1 | 0 | mg/L | 3.5223 | 2.5975 | 0.065593 | 1.5742 |  |  |  |  | Raw.Trb. | 1.27 | Cmb.Trb. | 0.03
27 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 172192000 | 1664430 | 5122620 | 8842440 | 963000 | 16000 | 979000 | now | 1040122300 |  | 0 | 1.02 | now | 1269.4 | 2306.8 | 24.8 | 33.4 | 1334.3 | 2453.8 | 42.8 | 4.7 | "/lb | 1.9375 | 8.375 | 1.625 | 0 | 11 | Raw | 11.4 | 7.32 | ef.turb.1 | 0 | ef.turb.2 | 0.044
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 171229000 | 1656430 | 5122620 | 8834440 |  |  |  | prev | 1039226800 |  |  |  | prev | 1269.4 | 2295.4 | 24.8 | 33.3 | 1334.3 | 2442.2 | 42.8 | 4.7 | Lbs. | 20.8087 | 18.425 | 0.40625 | 11 |  | Trtd | 11.4 | 7.5 | AC.1 | 0 | AC.2 | 0.341
| Total | 0 | 0 | 0 | 0 | 963000 | 8000 | 0 | 8000 |  |  |  | Total | 895500 |  |  |  | Total | 0 | 11.4 | 0 | 0.1 | 0 | 11.6 | 0 | 0 | mg/L | 2.5909 | 2.2941 | 0.050583 | 1.3696 |  |  |  |  | Raw.Trb. | 1.14 | Cmb.Trb. | 0.037
28 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 173115000 | 1671430 | 5150620 | 8868450 | 923000 | 61010 | 984010 | now | 1041113300 |  | 0 | 1 | now | 1269.4 | 2318.7 | 25 | 33.5 | 1334.3 | 2466.2 | 43 | 4.7 | "/lb | 1.875 | 8.25 | 1.25 | 0 | 13 | Raw | 12.3 | 7.37 | ef.turb.1 | 0 | ef.turb.2 | 0.039
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 172192000 | 1664430 | 5122620 | 8842440 |  |  |  | prev | 1040122300 |  |  |  | prev | 1269.4 | 2306.8 | 24.8 | 33.4 | 1334.3 | 2453.8 | 42.8 | 4.7 | Lbs. | 20.1375 | 18.15 | 0.3125 | 13 |  | Trtd | 11.5 | 7.78 | AC.1 | 0 | AC.2 | 0.364
| Total | 0 | 0 | 0 | 0 | 923000 | 7000 | 28000 | 26010 |  |  |  | Total | 991000 |  |  |  | Total | 0 | 11.9 | 0.2 | 0.1 | 0 | 12.4 | 0.2 | 0 | mg/L | 2.616 | 2.3578 | 0.040596 | 1.6888 |  |  |  |  | Raw.Trb. | 1.24 | Cmb.Trb. | 0.032
29 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 174100000 | 1671430 | 5179620 | 8910470 | 985000 | 71020 | 1056020 | now | 1042133900 |  | 0 | 0.96 | now | 1269.4 | 2331.4 | 25.1 | 33.6 | 1334.3 | 2479.4 | 43.2 | 4.7 | "/lb | 2.0625 | 8.125 | 1.75 | 0 | 14 | Raw | 12.5 | 7.4 | ef.turb.1 | 0 | ef.turb.2 | 0.047
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 173115000 | 1671430 | 5150620 | 8868450 |  |  |  | prev | 1041113300 |  |  |  | prev | 1269.4 | 2318.7 | 25 | 33.5 | 1334.3 | 2466.2 | 43 | 4.7 | Lbs. | 22.1513 | 17.875 | 0.4375 | 14 |  | Trtd | 11.6 | 7.9 | AC.1 | 0 | AC.2 | 0.46
| Total | 0 | 0 | 0 | 0 | 985000 | 0 | 29000 | 42020 |  |  |  | Total | 1020600 |  |  |  | Total | 0 | 12.7 | 0.1 | 0.1 | 0 | 13.2 | 0.2 | 0 | mg/L | 2.6965 | 2.1759 | 0.053257 | 1.7042 |  |  |  |  | Raw.Trb. | 1.26 | Cmb.Trb. | 0.037
30 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 175003000 | 1679430 | 5179620 | 8918470 | 903000 | 16000 | 919000 | now | 1043072700 |  | 0.42 | 0.99 | now | 1269.4 | 2343 | 25.1 | 33.7 | 1334.3 | 2491.1 | 43.2 | 4.7 | "/lb | 1.75 | 8.5 | 2 | 0 | 13 | Raw | 12.8 | 7.38 | ef.turb.1 | 0 | ef.turb.2 | 0.048
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 174100000 | 1671430 | 5179620 | 8910470 |  |  |  | prev | 1042133900 |  |  |  | prev | 1269.4 | 2331.4 | 25.1 | 33.6 | 1334.3 | 2479.4 | 43.2 | 4.7 | Lbs. | 18.795 | 18.7 | 0.5 | 13 |  | Trtd | 12.7 | 7.75 | AC.1 | 0 | AC.2 | 0.299
| Total | 0 | 0 | 0 | 0 | 903000 | 8000 | 0 | 8000 |  |  |  | Total | 938800 |  |  |  | Total | 0 | 11.6 | 0 | 0.1 | 0 | 11.7 | 0 | 0 | mg/L | 2.4957 | 2.4831 | 0.066392 | 1.7262 |  |  |  |  | Raw.Trb. | 1.17 | Cmb.Trb. | 0.046
[10 empty] | Totals | [6 empty] | AVG | [10 empty] | totals | [5 empty] | AVG TRTD |  |  |  | Avg.Cmb.Trb.
[10 empty] | 24753000 | 1496310 | 26249310 |  | 26003000 |  | 0.97 | 1.03 | [5 empty] | 0 | 323.2 |  |  |  | 516.1913 | 500.775 | 11.9131 | 297 |  |  | 10.7633 | 7.8 |  |  | 0.033133
[22 empty] | total- | 323.2

## May, 2021
May, 2021
Filters | [15 empty] | Rain | Cl2 | Pump Hours | [8 empty] | Chemicals | [5 empty] | Misc. |  |  | Turbidity
Day |  | CW.Tot.1 | Cla.Wst.1 | BW.Wst.1 | FTWst.1 | CW.Tot.2 | Cla.Wst.2 | BW.Wst.2 | FTWst.2 | Treated Total | Wastewater | Total Influent | Totalizer |  |  | Inches | Resid | Pump | Ef.Pmp.1 | Ef.Pmp.2 | Blo.1 | Blo.2 | URT.1 | URT.2 | BWP | SWP | Chem | ACH | SA | Poly | Cl2.1 | Cl2.2 | water | Temp | pH | F1 |  | F2
1 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 175832000 | 1679430 | 5207620 | 8933480 | 829000 | 43010 | 872010 | now | 1043878900 |  | 0 | 1.02 | now | 1269.4 | 2353.8 | 25.1 | 33.8 | 1334.3 | 2502.1 | 43.3 | 4.7 | "/lb | 2.25 | 7.25 | 1.625 | 0 | 12 | Raw | 13.1 | 7.44 | ef.turb.1 | 0 | ef.turb.2 | 0.041
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 175003000 | 1679430 | 5179620 | 8918470 |  |  |  | prev | 1043072700 |  |  |  | prev | 1269.4 | 2343 | 25.1 | 33.7 | 1334.3 | 2491.1 | 43.2 | 4.7 | Lbs. | 24.165 | 15.95 | 0.40625 | 12 |  | Trtd | 13.2 | 7.89 | AC.1 | 0 | AC.2 | 0.465
| Total | 0 | 0 | 0 | 0 | 829000 | 0 | 28000 | 15010 |  |  |  | Total | 806200 |  |  |  | Total | 0 | 10.8 | 0 | 0.1 | 0 | 11 | 0.1 | 0 | mg/L | 3.4952 | 2.307 | 0.058759 | 1.7356 |  |  |  |  | Raw.Trb. | 2.3 | Cmb.Trb. | 0.033
2 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 176711000 | 1687430 | 5207620 | 8952480 | 879000 | 27000 | 906000 | now | 1044830300 |  | 0 | 0.99 | now | 1269.4 | 2365.2 | 25.3 | 33.8 | 1334.3 | 2513.7 | 43.3 | 4.7 | "/lb | 2 | 8.5 | 1.5 | 11 | 0 | Raw | 12.1 | 7.34 | ef.turb.1 | 0 | ef.turb.2 | 0.058
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 175832000 | 1679430 | 5207620 | 8933480 |  |  |  | prev | 1043878900 |  |  |  | prev | 1269.4 | 2353.8 | 25.1 | 33.8 | 1334.3 | 2502.1 | 43.3 | 4.7 | Lbs. | 21.48 | 18.7 | 0.375 | 11 |  | Trtd | 12.3 | 7.69 | AC.1 | 0 | AC.2 | 0.442
| Total | 0 | 0 | 0 | 0 | 879000 | 8000 | 0 | 19000 |  |  |  | Total | 951400 |  |  |  | Total | 0 | 11.4 | 0.2 | 0 | 0 | 11.6 | 0 | 0 | mg/L | 2.9301 | 2.5509 | 0.051154 | 1.5005 |  |  |  |  | Raw.Trb. | 1.26 | Cmb.Trb. | 0.03
10.6
3 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 177538000 | 1694430 | 5207620 | 8960490 | 827000 | 15010 | 842010 | now | 1045690800 |  | 0.14 | 0.99 | now | 1269.4 | 2375.7 | 25.4 | 33.8 | 1334.3 | 2524.6 | 43.3 | 4.7 | "/lb | 1.5 | 8 | 1.5 | 10 | 0 | Raw | 11.2 | 7.46 | ef.turb.1 | 0 | ef.turb.2 | 0.042
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 176711000 | 1687430 | 5207620 | 8952480 |  |  |  | prev | 1044830300 |  |  |  | prev | 1269.4 | 2365.2 | 25.3 | 33.8 | 1334.3 | 2513.7 | 43.3 | 4.7 | Lbs. | 16.11 | 17.6 | 0.375 | 10 |  | Trtd | 11.6 | 7.9 | AC.1 | 0 | AC.2 | 0.299
| Total | 0 | 0 | 0 | 0 | 827000 | 7000 | 0 | 8010 |  |  |  | Total | 860500 |  |  |  | Total | 0 | 10.5 | 0.1 | 0 | 0 | 10.9 | 0 | 0 | mg/L | 2.3357 | 2.5518 | 0.05437 | 1.4499 |  |  |  |  | Raw.Trb. | 1.23 | Cmb.Trb. | 0.032
4 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 178432000 | 1694430 | 5236610 | 9008510 | 894000 | 77010 | 971010 | now | 1046602900 |  | 0 | 0.95 | now | 1269.4 | 2387.4 | 25.4 | 33.8 | 1334.3 | 2536.7 | 43.5 | 4.7 | "/lb | 2.0625 | 9 | 1.5 | 0 | 12 | Raw | 12.3 | 7.38 | ef.turb.1 | 0 | ef.turb.2 | 0.04
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 177538000 | 1694430 | 5207620 | 8960490 |  |  |  | prev | 1045690800 |  |  |  | prev | 1269.4 | 2375.7 | 25.4 | 33.8 | 1334.3 | 2524.6 | 43.3 | 4.7 | Lbs. | 22.1513 | 19.8 | 0.375 | 12 |  | Trtd | 12.3 | 7.81 | AC.1 | 0 | AC.2 | 0.33
| Total | 0 | 0 | 0 | 0 | 894000 | 0 | 28990 | 48020 |  |  |  | Total | 912100 |  |  |  | Total | 0 | 11.7 | 0 | 0 | 0 | 12.1 | 0.2 | 0 | mg/L | 2.9709 | 2.6556 | 0.050295 | 1.6095 |  |  |  |  | Raw.Trb. | 1.38 | Cmb.Trb. | 0.03
5 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 179464000 | 1702430 | 5236610 | 9016510 | 1032000 | 16000 | 1048000 | now | 1047585500 | 0 | 0 | 1 | now | 1269.4 | 2400.6 | 25.4 | 33.9 | 1334.3 | 2550.1 | 43.5 | 4.7 | "/lb | 2.25 | 10 | 1.875 | 0 | 13 | Raw | 12.5 | 7.36 | ef.turb.1 | 0 | ef.turb.2 | 0.043
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 178432000 | 1694430 | 5236610 | 9008510 |  |  |  | prev | 1046602900 |  |  |  | prev | 1269.4 | 2387.4 | 25.4 | 33.8 | 1334.3 | 2536.7 | 43.5 | 4.7 | Lbs. | 24.165 | 22 | 0.46875 | 13 |  | Trtd | 12.9 | 7.72 | AC.1 | 0 | AC.2 | 0.256
| Total | 0 | 0 | 0 | 0 | 1032000 | 8000 | 0 | 8000 |  |  |  | Total | 982600 |  |  |  | Total | 0 | 13.2 | 0 | 0.1 | 0 | 13.4 | 0 | 0 | mg/L | 2.8076 | 2.5561 | 0.054462 | 1.5104 |  |  |  |  | Raw.Trb. | 1.35 | Cmb.Trb. | 0.033
6 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 180180000 | 1709430 | 5265610 | 9016510 | 716000 | 36000 | 752000 | now | 1048441500 |  | 0.18 | 0.98 | now | 1269.4 | 2409.9 | 25.6 | 34 | 1334.3 | 2559.9 | 43.7 | 4.7 | "/lb | 1.5 | 6.875 | 1.5 | 9 | 0 | Raw | 13.4 | 7.37 | ef.turb.1 | 0 | ef.turb.2 | 0.043
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 179464000 | 1702430 | 5236610 | 9016510 |  |  |  | prev | 1047585500 |  |  |  | prev | 1269.4 | 2400.6 | 25.4 | 33.9 | 1334.3 | 2550.1 | 43.5 | 4.7 | Lbs. | 16.11 | 15.125 | 0.375 | 9 |  | Trtd | 13.2 | 7.66 | AC.1 | 0 | AC.2 | 0.306
| Total | 0 | 0 | 0 | 0 | 716000 | 7000 | 29000 | 0 |  |  |  | Total | 856000 |  |  |  | Total | 0 | 9.3 | 0.2 | 0.1 | 0 | 9.8 | 0.2 | 0 | mg/L | 2.6978 | 2.5329 | 0.062799 | 1.5072 |  |  |  |  | Raw.Trb. | 1.34 | Cmb.Trb. | 0.032
7 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 181163000 | 1709430 | 5265610 | 9050520 | 983000 | 34010 | 1017010 | now | 1049386200 |  | 0.02 | 0.97 | now | 1269.4 | 2422.5 | 25.6 | 34 | 1334.3 | 2572.6 | 43.7 | 4.7 | "/lb | 2.125 | 9.75 | 1.625 | 13 | 0 | Raw | 12 | 7.3 | ef.turb.1 | 0 | ef.turb.2 | 0.044
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 180180000 | 1709430 | 5265610 | 9016510 |  |  |  | prev | 1048441500 |  |  |  | prev | 1269.4 | 2409.9 | 25.6 | 34 | 1334.3 | 2559.9 | 43.7 | 4.7 | Lbs. | 22.8225 | 21.45 | 0.40625 | 13 |  | Trtd | 12.3 | 7.78 | AC.1 | 0 | AC.2 | 0.388
| Total | 0 | 0 | 0 | 0 | 983000 | 0 | 0 | 34010 |  |  |  | Total | 944700 |  |  |  | Total | 0 | 12.6 | 0 | 0 | 0 | 12.7 | 0 | 0 | mg/L | 2.7838 | 2.6164 | 0.049553 | 1.5857 |  |  |  |  | Raw.Trb. | 1.29 | Cmb.Trb. | 0.03
8 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 181908000 | 1717430 | 5298610 | 9097540 | 745000 | 88020 | 833020 | now | 1050265600 |  | 0 | 1.04 | now | 1269.4 | 2432.1 | 25.7 | 34.2 | 1334.3 | 2582.9 | 43.8 | 4.7 | "/lb | 1.75 | 6.5 | 1.3125 | 9 | 0 | Raw | 11.7 | 7.55 | ef.turb.1 | 0 | ef.turb.2 | 0.04
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 181163000 | 1709430 | 5265610 | 9050520 |  |  |  | prev | 1049386200 |  |  |  | prev | 1269.4 | 2422.5 | 25.6 | 34 | 1334.3 | 2572.6 | 43.7 | 4.7 | Lbs. | 18.795 | 14.3 | 0.32812 | 9 |  | Trtd | 11.1 | 7.88 | AC.1 | 0 | AC.2 | 0.27
| Total | 0 | 0 | 0 | 0 | 745000 | 8000 | 33000 | 47020 |  |  |  | Total | 879400 |  |  |  | Total | 0 | 9.6 | 0.1 | 0.2 | 0 | 10.3 | 0.1 | 0 | mg/L | 3.025 | 2.3015 | 0.05281 | 1.4485 |  |  |  |  | Raw.Trb. | 1.05 | Cmb.Trb. | 0.03
9 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 182801000 | 1717430 | 5298610 | 9108550 | 893000 | 11010 | 904010 | now | 1051068700 |  | 0 | 0.93 | now | 1269.4 | 2443.5 | 25.7 | 34.2 | 1334.3 | 2594.5 | 43.8 | 4.7 | "/lb | 1.625 | 9 | 1.5 | 11 | 0 | Raw | 12.9 | 7.5 | ef.turb.1 | 0 | ef.turb.2 | 0.04
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 181908000 | 1717430 | 5298610 | 9097540 |  |  |  | prev | 1050265600 |  |  |  | prev | 1269.4 | 2432.1 | 25.7 | 34.2 | 1334.3 | 2582.9 | 43.8 | 4.7 | Lbs. | 17.4525 | 19.8 | 0.375 | 11 |  | Trtd | 11.4 | 7.9 | AC.1 | 0 | AC.2 | 0.33
| Total | 0 | 0 | 0 | 0 | 893000 | 0 | 0 | 11010 |  |  |  | Total | 803100 |  |  |  | Total | 0 | 11.4 | 0 | 0 | 0 | 11.6 | 0 | 0 | mg/L | 2.3434 | 2.6586 | 0.050352 | 1.477 |  |  |  |  | Raw.Trb. | 1.23 | Cmb.Trb. | 0.03
10 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 183748000 | 1725430 | 5330610 | 9156570 | 947000 | 88020 | 1035020 | now | 1052113400 |  | 0 | 0.9 | now | 1269.4 | 2455.3 | 25.8 | 34.4 | 1334.3 | 2606.9 | 44 | 4.7 | "/lb | 2.0625 | 9.125 | 1.875 | 0 | 12 | Raw | 12.3 | 7.43 | ef.turb.1 | 0 | ef.turb.2 | 0.048
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 182801000 | 1717430 | 5298610 | 9108550 |  |  |  | prev | 1051068700 |  |  |  | prev | 1269.4 | 2443.5 | 25.7 | 34.2 | 1334.3 | 2594.5 | 43.8 | 4.7 | Lbs. | 22.1513 | 20.075 | 0.46875 | 12 |  | Trtd | 12.3 | 7.89 | AC.1 | 0 | AC.2 | 0.324
| Total | 0 | 0 | 0 | 0 | 947000 | 8000 | 32000 | 48020 |  |  |  | Total | 1044700 |  |  |  | Total | 0 | 11.8 | 0.1 | 0.2 | 0 | 12.4 | 0.2 | 0 | mg/L | 2.8047 | 2.5418 | 0.059351 | 1.5194 |  |  |  |  | Raw.Trb. | 1.4 | Cmb.Trb. | 0.039
11 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 184822000 | 1732430 | 5330610 | 9164570 | 1074000 | 15000 | 1089000 | now | 1053248200 |  | 0 | 0.97 | now | 1269.4 | 2468.7 | 25.9 | 34.4 | 1334.3 | 2620.5 | 44 | 4.7 | "/lb | 2.125 | 9.0625 | 1.875 | 0 | 14 | Raw | 13.5 | 7.32 | ef.turb.1 | 0 | ef.turb.2 | 0.056
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 183748000 | 1725430 | 5330610 | 9156570 |  |  |  | prev | 1052113400 |  |  |  | prev | 1269.4 | 2455.3 | 25.8 | 34.4 | 1334.3 | 2606.9 | 44 | 4.7 | Lbs. | 22.8225 | 19.9375 | 0.46875 | 14 |  | Trtd | 13.3 | 7.78 | AC.1 | 0 | AC.2 | 0.315
| Total | 0 | 0 | 0 | 0 | 1074000 | 7000 | 0 | 8000 |  |  |  | Total | 1134800 |  |  |  | Total | 0 | 13.4 | 0.1 | 0 | 0 | 13.6 | 0 | 0 | mg/L | 2.548 | 2.2259 | 0.052332 | 1.563 |  |  |  |  | Raw.Trb. | 1.35 | Cmb.Trb. | 0.045
12 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 186036000 | 1740440 | 5362600 | 9219590 | 1214000 | 95020 | 1309020 | now | 1054414500 |  | 0 | 0.99 | now | 1269.4 | 2484 | 25.9 | 34.5 | 1334.3 | 2636.4 | 44.2 | 4.7 | "/lb | 2.5 | 11.5 | 2.125 | 0 | 17 | Raw | 13.4 | 7.31 | ef.turb.1 | 0 | ef.turb.2 | 0.047
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 184822000 | 1732430 | 5330610 | 9164570 |  |  |  | prev | 1053248200 |  |  |  | prev | 1269.4 | 2468.7 | 25.9 | 34.4 | 1334.3 | 2620.5 | 44 | 4.7 | Lbs. | 26.85 | 25.3 | 0.53125 | 17 |  | Trtd | 13.8 | 7.74 | AC.1 | 0 | AC.2 | 0.336
| Total | 0 | 0 | 0 | 0 | 1214000 | 8010 | 31990 | 55020 |  |  |  | Total | 1166300 |  |  |  | Total | 0 | 15.3 | 0 | 0.1 | 0 | 15.9 | 0.2 | 0 | mg/L | 2.6519 | 2.4988 | 0.05247 | 1.6791 |  |  |  |  | Raw.Trb. | 1.36 | Cmb.Trb. | 0.033
13 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 187079000 | 1748440 | 5394600 | 9299620 | 1043000 | 120030 | 1163030 | now | 1055623900 |  | 0 | 1.02 | now | 1269.4 | 2497 | 26 | 34.7 | 1334.3 | 2650.5 | 44.4 | 4.7 | "/lb | 2.25 | 8.9375 | 1.9375 | 0 | 14 | Raw | 14.1 | 7.39 | ef.turb.1 | 0 | ef.turb.2 | 0.048
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 186036000 | 1740440 | 5362600 | 9219590 |  |  |  | prev | 1054414500 |  |  |  | prev | 1269.4 | 2484 | 25.9 | 34.5 | 1334.3 | 2636.4 | 44.2 | 4.7 | Lbs. | 24.165 | 19.6625 | 0.48438 | 14 |  | Trtd | 14.7 | 7.69 | AC.1 | 0 | AC.2 | 0.411
| Total | 0 | 0 | 0 | 0 | 1043000 | 8000 | 32000 | 80030 |  |  |  | Total | 1209400 |  |  |  | Total | 0 | 13 | 0.1 | 0.2 | 0 | 14.1 | 0.2 | 0 | mg/L | 2.778 | 2.2604 | 0.055684 | 1.6095 |  |  |  |  | Raw.Trb. | 1.4 | Cmb.Trb. | 0.033
14 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 188395000 | 1756440 | 5394600 | 9307630 | 1316000 | 16010 | 1332010 | now | 1056811700 |  | 0 | 0.97 | now | 1269.4 | 2513.3 | 26.1 | 34.7 | 1334.3 | 2667.1 | 44.4 | 4.7 | "/lb | 2.5 | 11.9375 | 2.125 | 0 | 18 | Raw | 14.4 | 7.22 | ef.turb.1 | 0 | ef.turb.2 | 0.046
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 187079000 | 1748440 | 5394600 | 9299620 |  |  |  | prev | 1055623900 |  |  |  | prev | 1269.4 | 2497 | 26 | 34.7 | 1334.3 | 2650.5 | 44.4 | 4.7 | Lbs. | 26.85 | 26.2625 | 0.53125 | 18 |  | Trtd | 15.6 | 7.6 | AC.1 | 0 | AC.2 | 0.299
| Total | 0 | 0 | 0 | 0 | 1316000 | 8000 | 0 | 8010 |  |  |  | Total | 1187800 |  |  |  | Total | 0 | 16.3 | 0.1 | 0 | 0 | 16.6 | 0 | 0 | mg/L | 2.4464 | 2.3928 | 0.048404 | 1.64 |  |  |  |  | Raw.Trb. | 1.32 | Cmb.Trb. | 0.033
15 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 189529000 | 1764440 | 5426600 | 9356650 | 1134000 | 89020 | 1223020 | now | 1057976500 |  | 0 | 1.01 | now | 1269.4 | 2527.4 | 26.2 | 34.9 | 1334.3 | 2681.9 | 44.6 | 4.7 | "/lb | 2.5 | 10 | 2 | 0 | 16 | Raw | 14.9 | 7.46 | ef.turb.1 | 0 | ef.turb.2 | 0.043
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 188395000 | 1756440 | 5394600 | 9307630 |  |  |  | prev | 1056811700 |  |  |  | prev | 1269.4 | 2513.3 | 26.1 | 34.7 | 1334.3 | 2667.1 | 44.4 | 4.7 | Lbs. | 26.85 | 22 | 0.5 | 16 |  | Trtd | 15.4 | 7.77 | AC.1 | 0 | AC.2 | 0.28
| Total | 0 | 0 | 0 | 0 | 1134000 | 8000 | 32000 | 49020 |  |  |  | Total | 1164800 |  |  |  | Total | 0 | 14.1 | 0.1 | 0.2 | 0 | 14.8 | 0.2 | 0 | mg/L | 2.839 | 2.3262 | 0.052868 | 1.6918 |  |  |  |  | Raw.Trb. | 1.21 | Cmb.Trb. | 0.033
16 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 190626000 | 1771440 | 5426600 | 9364650 | 1097000 | 15000 | 1112000 | now | 1059108330 |  | 0 | 1 | now | 1269.4 | 2541 | 26.2 | 35 | 1334.3 | 2695.7 | 44.6 | 4.7 | "/lb | 2.25 | 10.625 | 1.75 | 15 | 0 | Raw | 15.2 | 7.54 | ef.turb.1 | 0 | ef.turb.2 | 0.049
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 189529000 | 1764440 | 5426600 | 9356650 |  |  |  | prev | 1057976500 |  |  |  | prev | 1269.4 | 2527.4 | 26.2 | 34.9 | 1334.3 | 2681.9 | 44.6 | 4.7 | Lbs. | 24.165 | 23.375 | 0.4375 | 15 |  | Trtd | 15.3 | 7.84 | AC.1 | 0 | AC.2 | 0.309
| Total | 0 | 0 | 0 | 0 | 1097000 | 7000 | 0 | 8000 |  |  |  | Total | 1131830 |  |  |  | Total | 0 | 13.6 | 0 | 0.1 | 0 | 13.8 | 0 | 0 | mg/L | 2.6413 | 2.5549 | 0.04782 | 1.6395 |  |  |  |  | Raw.Trb. | 1.23 | Cmb.Trb. | 0.037
17 | Pres. | 95220500 | 853349 | 2038320 | 3605550 | 191846000 | 1779440 | 5459600 | 9415670 | 1220000 | 92020 | 1312020 | now | 1060176000 |  | 0 | 0.95 | now | 1269.4 | 2556.3 | 26.4 | 35.1 | 1334.3 | 2711.7 | 44.9 | 4.7 | "/lb | 3 | 11.25 | 2.25 | 0 | 18 | Raw | 14.9 | 7.38 | ef.turb.1 | 0 | ef.turb.2 | 0.05
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 190626000 | 1771440 | 5426600 | 9364650 |  |  |  | prev | 1059108330 |  |  |  | prev | 1269.4 | 2541 | 26.2 | 35 | 1334.3 | 2695.7 | 44.6 | 4.7 | Lbs. | 32.22 | 24.75 | 0.5625 | 18 |  | Trtd | 15.4 | 7.77 | AC.1 | 0 | AC.2 | 0.39
| Total | 0 | 0 | 0 | 0 | 1220000 | 8000 | 33000 | 51020 |  |  |  | Total | 1067670 |  |  |  | Total | 0 | 15.3 | 0.2 | 0.1 | 0 | 16 | 0.3 | 0 | mg/L | 3.1666 | 2.4325 | 0.055284 | 1.7691 |  |  |  |  | Raw.Trb. | 1.24 | Cmb.Trb. | 0.03
18 | Pres. | 96128000 | 861349 | 2111310 | 3707450 | 191956000 | 1779440 | 5459600 | 9415670 | 1017500 | 182890 | 1200390 | now | 1061214900 |  | 0 | 0.95 | now | 1280.8 | 2557.6 | 26.5 | 35.1 | 1347.4 | 2713.1 | 45.1 | 4.8 | "/lb | 2.125 | 9.75 | 2 | 13 | 1 | Raw | 14.7 | 7.28 | ef.turb.1 | 0 | ef.turb.2 | 0.048
| Prev | 95220500 | 853349 | 2038320 | 3605550 | 191846000 | 1779440 | 5459600 | 9415670 |  |  |  | prev | 1060176000 |  |  |  | prev | 1269.4 | 2556.3 | 26.4 | 35.1 | 1334.3 | 2711.7 | 44.9 | 4.7 | Lbs. | 22.8225 | 21.45 | 0.5 | 14 |  | Trtd | 15.6 | 7.58 | AC.1 | 0 | AC.2 | 0.331
| Total | 907500 | 8000 | 72990 | 101900 | 110000 | 0 | 0 | 0 |  |  |  | Total | 1038900 |  |  |  | Total | 11.4 | 1.3 | 0.1 | 0 | 13.1 | 1.4 | 0.2 | 0.1 | mg/L | 2.6894 | 2.5277 | 0.058921 | 1.6498 |  |  |  |  | Raw.Trb. | 1.38 | Cmb.Trb. | 0.037
19 | Pres. | 97184400 | 869349 | 2147310 | 3745540 | 191956000 | 1779440 | 5459600 | 9415670 | 1056400 | 82090 | 1138490 | now | 1062185300 |  | 0.26 | 1.03 | now | 1294 | 2557.6 | 26.6 | 35.1 | 1361.1 | 2713.1 | 45.3 | 4.9 | "/lb | 2.25 | 10 | 2.125 | 14 | 0 | Raw | 14.1 | 7.2 | ef.turb.1 | 0.044 | ef.turb.2 | 0
| Prev | 96128000 | 861349 | 2111310 | 3707450 | 191956000 | 1779440 | 5459600 | 9415670 |  |  |  | prev | 1061214900 |  |  |  | prev | 1280.8 | 2557.6 | 26.5 | 35.1 | 1347.4 | 2713.1 | 45.1 | 4.8 | Lbs. | 24.165 | 22 | 0.53125 | 14 |  | Trtd | 15.5 | 7.62 | AC.1 | 0.449 | AC.2 | 0
| Total | 1056400 | 8000 | 36000 | 38090 | 0 | 0 | 0 | 0 |  |  |  | Total | 970400 |  |  |  | Total | 13.2 | 0 | 0.1 | 0 | 13.7 | 0 | 0.2 | 0.1 | mg/L | 2.7428 | 2.4971 | 0.060298 | 1.589 |  |  |  |  | Raw.Trb. | 1.27 | Cmb.Trb. | 0.041
20 | Pres. | 98113900 | 877349 | 2184310 | 3771540 | 191956000 | 1779440 | 5459600 | 9415670 | 929500 | 71000 | 1000500 | now | 1063116400 |  | 0.12 | 1.07 | now | 1305.5 | 2557.6 | 26.7 | 35.1 | 1373.1 | 2713.1 | 45.4 | 4.9 | "/lb | 2.125 | 8.75 | 1.875 | 12 | 0 | Raw | 12.9 | 7.36 | ef.turb.1 | 0.044 | ef.turb.2 | 0
| Prev | 97184400 | 869349 | 2147310 | 3745540 | 191956000 | 1779440 | 5459600 | 9415670 |  |  |  | prev | 1062185300 |  |  |  | prev | 1294 | 2557.6 | 26.6 | 35.1 | 1361.1 | 2713.1 | 45.3 | 4.9 | Lbs. | 22.8225 | 19.25 | 0.46875 | 12 |  | Trtd | 14.5 | 7.54 | AC.1 | 0.406 | AC.2 | 0
| Total | 929500 | 8000 | 37000 | 26000 | 0 | 0 | 0 | 0 |  |  |  | Total | 931100 |  |  |  | Total | 11.5 | 0 | 0.1 | 0 | 12 | 0 | 0.1 | 0 | mg/L | 2.9441 | 2.4832 | 0.060468 | 1.548 |  |  |  |  | Raw.Trb. | 1.31 | Cmb.Trb. | 0.041
21 | Pres. | 99218300 | 893349 | 2184310 | 3779540 | 191956000 | 1779440 | 5459600 | 9415670 | 1104400 | 24000 | 1128400 | now | 1064127200 |  | 0 | 1.02 | now | 1319.2 | 2557.6 | 26.9 | 35.1 | 1387.1 | 2713.1 | 45.4 | 4.9 | "/lb | 2.75 | 10.25 | 2.5 | 14 | 0 | Raw | 11.8 | 7.28 | ef.turb.1 | 0.039 | ef.turb.2 | 0
| Prev | 98113900 | 877349 | 2184310 | 3771540 | 191956000 | 1779440 | 5459600 | 9415670 |  |  |  | prev | 1063116400 |  |  |  | prev | 1305.5 | 2557.6 | 26.7 | 35.1 | 1373.1 | 2713.1 | 45.4 | 4.9 | Lbs. | 29.535 | 22.55 | 0.625 | 14 |  | Trtd | 13.8 | 7.75 | AC.1 | 0.502 | AC.2 | 0
| Total | 1104400 | 16000 | 0 | 8000 | 0 | 0 | 0 | 0 |  |  |  | Total | 1010800 |  |  |  | Total | 13.7 | 0 | 0.2 | 0 | 14 | 0 | 0 | 0 | mg/L | 3.2066 | 2.4482 | 0.067856 | 1.52 |  |  |  |  | Raw.Trb. | 2.03 | Cmb.Trb. | 0.036
22 | Pres. | 100183000 | 902349 | 2221300 | 3808540 | 191956000 | 1779440 | 5459600 | 9415670 | 964700 | 74990 | 1039690 | now | 1065110800 |  | 0 | 1.03 | now | 1331.2 | 2557.6 | 27.1 | 35.1 | 1399.6 | 2713.1 | 45.6 | 5 | "/lb | 2.52 | 8 | 1.875 | 12 | 0 | Raw | 12.6 | 7.41 | ef.turb.1 | 0.04 | ef.turb.2 | 0
| Prev | 99218300 | 893349 | 2184310 | 3779540 | 191956000 | 1779440 | 5459600 | 9415670 |  |  |  | prev | 1064127200 |  |  |  | prev | 1319.2 | 2557.6 | 26.9 | 35.1 | 1387.1 | 2713.1 | 45.4 | 4.9 | Lbs. | 27.0648 | 17.6 | 0.46875 | 12 |  | Trtd | 12.1 | 7.82 | AC.1 | 0.53 | AC.2 | 0
| Total | 964700 | 9000 | 36990 | 29000 | 0 | 0 | 0 | 0 |  |  |  | Total | 983600 |  |  |  | Total | 12 | 0 | 0.2 | 0 | 12.5 | 0 | 0.2 | 0.1 | mg/L | 3.3639 | 2.1875 | 0.058262 | 1.4915 |  |  |  |  | Raw.Trb. | 1.22 | Cmb.Trb. | 0.03
23 | Pres. | 100966000 | 910348 | 2221300 | 3816540 | 191956000 | 1779440 | 5459600 | 9415670 | 783000 | 15999 | 798999 | now | 1065905300 |  | 0.11 | 0.98 | now | 1340.9 | 2557.6 | 27.2 | 35.1 | 1409.6 | 2713.1 | 45.6 | 5 | "/lb | 1.5 | 7.25 | 1.625 | 10 | 0 | Raw | 13.8 | 7.6 | ef.turb.1 | 0.04 | ef.turb.2 | 0
| Prev | 100183000 | 902349 | 2221300 | 3808540 | 191956000 | 1779440 | 5459600 | 9415670 |  |  |  | prev | 1065110800 |  |  |  | prev | 1331.2 | 2557.6 | 27.1 | 35.1 | 1399.6 | 2713.1 | 45.6 | 5 | Lbs. | 16.11 | 15.95 | 0.40625 | 10 |  | Trtd | 13 | 7.86 | AC.1 | 0.39 | AC.2 | 0
| Total | 783000 | 7999 | 0 | 8000 | 0 | 0 | 0 | 0 |  |  |  | Total | 794500 |  |  |  | Total | 9.7 | 0 | 0.1 | 0 | 10 | 0 | 0 | 0 | mg/L | 2.467 | 2.4425 | 0.062211 | 1.5313 |  |  |  |  | Raw.Trb. | 1.22 | Cmb.Trb. | 0.03
24 | Pres. | 101349000 | 917348 | 2257300 | 3859530 | 192458000 | 1787440 | 5491600 | 9469690 | 885000 | 180010 | 1065010 | now | 1066794700 |  | 0.22 | 0.94 | now | 1345.8 | 2564.6 | 27.5 | 35.1 | 1415.2 | 2720.7 | 46 | 5.1 | "/lb | 2.25 | 7.5 | 1.625 | 12 | 0 | Raw | 13 | 7.48 | ef.turb.1 | 0.04 | ef.turb.2 | 0
| Prev | 100966000 | 910348 | 2221300 | 3816540 | 191956000 | 1779440 | 5459600 | 9415670 |  |  |  | prev | 1065905300 |  |  |  | prev | 1340.9 | 2557.6 | 27.2 | 35.1 | 1409.6 | 2713.1 | 45.6 | 5 | Lbs. | 24.165 | 16.5 | 0.40625 | 12 |  | Trtd | 13.2 | 7.82 | AC.1 | 0.36 | AC.2 | 0
| Total | 383000 | 7000 | 36000 | 42990 | 502000 | 8000 | 32000 | 54020 |  |  |  | Total | 889400 |  |  |  | Total | 4.9 | 7 | 0.3 | 0 | 5.6 | 7.6 | 0.4 | 0.1 | mg/L | 3.274 | 2.2355 | 0.055041 | 1.6258 |  |  |  |  | Raw.Trb. | 1.39 | Cmb.Trb. | 0.03
25 | Pres. | 102265000 | 933348 | 2257300 | 3867530 | 192458000 | 1787440 | 5491600 | 9469690 | 916000 | 24000 | 940000 | now | 1067687500 |  | 0.1 | 0.95 | now | 1357.1 | 2564.6 | 27.5 | 35.4 | 1426.9 | 2720.7 | 46 | 5.1 | "/lb | 2.75 | 7.5 | 1.5 | 12 | 0 | Raw | 13.6 | 7.2 | ef.turb.1 | 0.04 | ef.turb.2 | 0
| Prev | 101349000 | 917348 | 2257300 | 3859530 | 192458000 | 1787440 | 5491600 | 9469690 |  |  |  | prev | 1066794700 |  |  |  | prev | 1345.8 | 2564.6 | 27.5 | 35.1 | 1415.2 | 2720.7 | 46 | 5.1 | Lbs. | 29.535 | 16.5 | 0.375 | 12 |  | Trtd | 14.1 | 7.74 | AC.1 | 0.657 | AC.2 | 0
| Total | 916000 | 16000 | 0 | 8000 | 0 | 0 | 0 | 0 |  |  |  | Total | 892800 |  |  |  | Total | 11.3 | 0 | 0 | 0.3 | 11.7 | 0 | 0 | 0 | mg/L | 3.8661 | 2.1598 | 0.049087 | 1.5708 |  |  |  |  | Raw.Trb. | 2.83 | Cmb.Trb. | 0.037
26 | Pres. | 103330000 | 958348 | 2294300 | 3914530 | 192458000 | 1787440 | 5491600 | 9469690 | 1065000 | 109000 | 1174000 | now | 1068729900 |  | 0.08 | 1 | now | 1370.4 | 2564.6 | 27.5 | 35.7 | 1441 | 2720.7 | 46.1 | 5.1 | "/lb | 2.875 | 8.5 | 1.25 | 15 | 0 | Raw | 13.1 | 7.21 | ef.turb.1 | 0.038 | ef.turb.2 | 0
| Prev | 102265000 | 933348 | 2257300 | 3867530 | 192458000 | 1787440 | 5491600 | 9469690 |  |  |  | prev | 1067687500 |  |  |  | prev | 1357.1 | 2564.6 | 27.5 | 35.4 | 1426.9 | 2720.7 | 46 | 5.1 | Lbs. | 30.8775 | 18.7 | 0.3125 | 15 |  | Trtd | 13.9 | 7.58 | AC.1 | 0.639 | AC.2 | 0
| Total | 1065000 | 25000 | 37000 | 47000 | 0 | 0 | 0 | 0 |  |  |  | Total | 1042400 |  |  |  | Total | 13.3 | 0 | 0 | 0.3 | 14.1 | 0 | 0.1 | 0 | mg/L | 3.4764 | 2.1054 | 0.035183 | 1.6888 |  |  |  |  | Raw.Trb. | 2.24 | Cmb.Trb. | 0.033
27 | Pres. | 104238000 | 966348 | 2294300 | 3923530 | 192458000 | 1787440 | 5491600 | 9469690 | 908000 | 17000 | 925000 | now | 1069672500 |  | 0.04 | 1.02 | now | 1381.6 | 2564.6 | 27.5 | 35.9 | 1452.5 | 2720.7 | 46.1 | 5.1 | "/lb | 2.0625 | 7.25 | 1.125 | 13 | 0 | Raw | 13.9 | 7.3 | ef.turb.1 | 0.039 | ef.turb.2 | 0
| Prev | 103330000 | 958348 | 2294300 | 3914530 | 192458000 | 1787440 | 5491600 | 9469690 |  |  |  | prev | 1068729900 |  |  |  | prev | 1370.4 | 2564.6 | 27.5 | 35.7 | 1441 | 2720.7 | 46.1 | 5.1 | Lbs. | 22.1513 | 15.95 | 0.28125 | 13 |  | Trtd | 14.4 | 7.69 | AC.1 | 0.657 | AC.2 | 0
| Total | 908000 | 8000 | 0 | 9000 | 0 | 0 | 0 | 0 |  |  |  | Total | 942600 |  |  |  | Total | 11.2 | 0 | 0 | 0.2 | 11.5 | 0 | 0 | 0 | mg/L | 2.9251 | 2.1062 | 0.03714 | 1.7167 |  |  |  |  | Raw.Trb. | 1.81 | Cmb.Trb. | 0.035
28 | Pres. | 105439000 | 982347 | 2330300 | 3951530 | 192458000 | 1787440 | 5491600 | 9469690 | 1201000 | 79999 | 1280999 | now | 1070683800 |  | 0 | 1.03 | now | 1396.5 | 2564.6 | 27.5 | 36.1 | 1468 | 2720.7 | 46.3 | 5.2 | "/lb | 2.75 | 9.875 | 1.25 | 17 | 0 | Raw | 12.9 | 7.26 | ef.turb.1 | 0.038 | ef.turb.2 | 0
| Prev | 104238000 | 966348 | 2294300 | 3923530 | 192458000 | 1787440 | 5491600 | 9469690 |  |  |  | prev | 1069672500 |  |  |  | prev | 1381.6 | 2564.6 | 27.5 | 35.9 | 1452.5 | 2720.7 | 46.1 | 5.1 | Lbs. | 29.535 | 21.725 | 0.3125 | 17 |  | Trtd | 13.5 | 7.82 | AC.1 | 0.434 | AC.2 | 0
| Total | 1201000 | 15999 | 36000 | 28000 | 0 | 0 | 0 | 0 |  |  |  | Total | 1011300 |  |  |  | Total | 14.9 | 0 | 0 | 0.2 | 15.5 | 0 | 0.2 | 0.1 | mg/L | 2.9487 | 2.169 | 0.031199 | 1.6972 |  |  |  |  | Raw.Trb. | 1.68 | Cmb.Trb. | 0.033
29 | Pres. | 106545000 | 999347 | 2367290 | 3980520 | 192458000 | 1787440 | 5491600 | 9469690 | 1106000 | 82980 | 1188980 | now | 1071819500 |  | 0 | 1.02 | now | 1410.3 | 2564.6 | 27.5 | 36.3 | 1482.4 | 2720.7 | 46.5 | 5.2 | "/lb | 2.5 | 9 | 1.375 | 17 | 0 | Raw | 13 | 7.31 | ef.turb.1 | 0.038 | ef.turb.2 | 0
| Prev | 105439000 | 982347 | 2330300 | 3951530 | 192458000 | 1787440 | 5491600 | 9469690 |  |  |  | prev | 1070683800 |  |  |  | prev | 1396.5 | 2564.6 | 27.5 | 36.1 | 1468 | 2720.7 | 46.3 | 5.2 | Lbs. | 26.85 | 19.8 | 0.34375 | 17 |  | Trtd | 13.7 | 7.88 | AC.1 | 0.452 | AC.2 | 0
| Total | 1106000 | 17000 | 36990 | 28990 | 0 | 0 | 0 | 0 |  |  |  | Total | 1135700 |  |  |  | Total | 13.8 | 0 | 0 | 0.2 | 14.4 | 0 | 0.2 | 0 | mg/L | 2.9109 | 2.1466 | 0.037267 | 1.843 |  |  |  |  | Raw.Trb. | 1.4 | Cmb.Trb. | 0.033
30 | Pres. | 107917000 | 1007350 | 2403290 | 4009520 | 192485000 | 1787440 | 5491600 | 9469690 | 1399000 | 73003 | 1472003 | now | 1073115900 |  | 0 | 1.01 | now | 1427.3 | 2564.6 | 27.5 | 36.4 | 1499.8 | 2720.7 | 46.6 | 5.3 | "/lb | 3 | 11.0625 | 1.125 | 21 | 0 | Raw | 14.3 | 7.47 | ef.turb.1 | 0.042 | ef.turb.2 | 0
| Prev | 106545000 | 999347 | 2367290 | 3980520 | 192458000 | 1787440 | 5491600 | 9469690 |  |  |  | prev | 1071819500 |  |  |  | prev | 1410.3 | 2564.6 | 27.5 | 36.3 | 1482.4 | 2720.7 | 46.5 | 5.2 | Lbs. | 32.22 | 24.3375 | 0.28125 | 21 |  | Trtd | 14.5 | 7.89 | AC.1 | 0.609 | AC.2 | 0
| Total | 1372000 | 8003 | 36000 | 29000 | 27000 | 0 | 0 | 0 |  |  |  | Total | 1296400 |  |  |  | Total | 17 | 0 | 0 | 0.1 | 17.4 | 0 | 0.1 | 0.1 | mg/L | 2.7615 | 2.0859 | 0.024105 | 1.7998 |  |  |  |  | Raw.Trb. | 1.51 | Cmb.Trb. | 0.037
31 | Pres. | 109201000 | 1015350 | 2403290 | 4018520 | 192485000 | 1787440 | 5491600 | 9469690 | 1284000 | 17000 | 1301000 | now | 1074367800 |  | 0 | 1.09 | now | 1443.2 | 2564.6 | 27.5 | 36.5 | 1516 | 2720.7 | 46.6 | 5.3 | "/lb | 2.625 | 20 | 1 | 20 | 0 | Raw | 15.1 | 7.35 | ef.turb.1 | 0.045 | ef.turb.2 | 0
| Prev | 107917000 | 1007350 | 2403290 | 4009520 | 192485000 | 1787440 | 5491600 | 9469690 |  |  |  | prev | 1073115900 |  |  |  | prev | 1427.3 | 2564.6 | 27.5 | 36.4 | 1499.8 | 2720.7 | 46.6 | 5.3 | Lbs. | 28.1925 | 44 | 0.25 | 20 |  | Trtd | 14.9 | 7.83 | AC.1 | 0.4 | AC.2 | 0
| Total | 1284000 | 8000 | 0 | 9000 | 0 | 0 | 0 | 0 |  |  |  | Total | 1251900 |  |  |  | Total | 15.9 | 0 | 0 | 0.1 | 16.2 | 0 | 0 | 0 | mg/L | 2.6327 | 4.1089 | 0.023346 | 1.8677 |  |  |  |  | Raw.Trb. | 1.47 | Cmb.Trb. | 0.036
[10 empty] | Totals | [6 empty] | AVG | [10 empty] | totals | [5 empty] | AVG TRTD |  |  |  | Avg.Cmb.Trb.
[10 empty] | 31462500 | 1911151 | 33373651 |  | 31295100 |  | 1.27 | 0.99419 | [5 empty] | 181.7 | 229.6 |  |  |  | 755.371 | 642.4 | 13.0312 | 427 |  |  | 13.6387 | 7.7655 |  |  | 0.033935
[22 empty] | total- | 411.3

## Jun, 2021
June, 2021
Filters | [15 empty] | Rain | Cl2 | Pump Hours | [8 empty] | Chemicals | [5 empty] | Misc. |  |  | Turbidity
Day |  | CW.Tot.1 | Cla.Wst.1 | BW.Wst.1 | FTWst.1 | CW.Tot.2 | Cla.Wst.2 | BW.Wst.2 | FTWst.2 | Treated Total | Wastewater | Total Influent | Totalizer |  |  | Inches | Resid | Pump | Ef.Pmp.1 | Ef.Pmp.2 | Blo.1 | Blo.2 | URT.1 | URT.2 | BWP | SWP | Chem | ACH | SA | Poly | Cl2.1 | Cl2.2 | water | Temp | pH | F1 |  | F2
1 | Pres. | 110911000 | 1032350 | 2440290 | 4051520 | 192697000 | 1787440 | 5491600 | 9487700 | 1922000 | 105010 | 2027010 | now | 1075941800 |  | 0 | 1.09 | now | 1464.1 | 2567.8 | 27.5 | 36.8 | 1537.6 | 2724.2 | 46.8 | 5.4 | "/lb | 4.375 | 15.5 | 2 | 28 | 0 | Raw | 15.8 | 7.45 | ef.turb.1 | 0.04 | ef.turb.2 | 0
| Prev | 109201000 | 1015350 | 2403290 | 4018520 | 192485000 | 1787440 | 5491600 | 9469690 |  |  |  | prev | 1074367800 |  |  |  | prev | 1443.2 | 2564.6 | 27.5 | 36.5 | 1516 | 2720.7 | 46.6 | 5.3 | Lbs. | 46.9875 | 34.1 | 0.5 | 28 |  | Trtd | 15.9 | 7.78 | AC.1 | 0.34 | AC.2 | 0
| Total | 1710000 | 17000 | 37000 | 33000 | 212000 | 0 | 0 | 18010 |  |  |  | Total | 1574000 |  |  |  | Total | 20.9 | 3.2 | 0 | 0.3 | 21.6 | 3.5 | 0.2 | 0.1 | mg/L | 2.9313 | 2.1273 | 0.031193 | 1.7468 |  |  |  |  | Raw.Trb. | 1.52 | Cmb.Trb. | 0.03
2 | Pres. | 111773000 | 1062350 | 2476290 | 4175510 | 193351000 | 1796440 | 5491600 | 9509710 | 1516000 | 221000 | 1737000 | now | 1077490200 |  | 0 | 1.07 | now | 1476 | 2577.1 | 27.5 | 37.3 | 1551.5 | 2734 | 47 | 5.4 | "/lb | 3.75 | 13.375 | 2.125 | 12 | 8 | Raw | 18 | 7.28 | ef.turb.1 | 0.045 | ef.turb.2 | 0
| Prev | 110911000 | 1032350 | 2440290 | 4051520 | 192697000 | 1787440 | 5491600 | 9487700 |  |  |  | prev | 1075941800 |  |  |  | prev | 1464.1 | 2567.8 | 27.5 | 36.8 | 1537.6 | 2724.2 | 46.8 | 5.4 | Lbs. | 40.275 | 29.425 | 0.53125 | 20 |  | Trtd | 17.8 | 7.71 | AC.1 | 0.381 | AC.2 | 0
| Total | 862000 | 30000 | 36000 | 123990 | 654000 | 9000 | 0 | 22010 |  |  |  | Total | 1548400 |  |  |  | Total | 11.9 | 9.3 | 0 | 0.5 | 13.9 | 9.8 | 0.2 | 0 | mg/L | 3.1854 | 2.3273 | 0.042018 | 1.5818 |  |  |  |  | Raw.Trb. | 1.71 | Cmb.Trb. | 0.036
10.6
3 | Pres. | 112537000 | 1069350 | 2513280 | 4227510 | 193962000 | 1796440 | 5524590 | 9546720 | 1375000 | 165990 | 1540990 | now | 1078853500 |  | 0 | 0.92 | now | 1487 | 2587.6 | 27.5 | 37.5 | 1563.5 | 2745.1 | 47.3 | 5.5 | "/lb | 3.25 | 13.875 | 2.25 | 13 | 8 | Raw | 18.1 | 7.36 | ef.turb.1 | 0.042 | ef.turb.2 | 0.053
| Prev | 111773000 | 1062350 | 2476290 | 4175510 | 193351000 | 1796440 | 5491600 | 9509710 |  |  |  | prev | 1077490200 |  |  |  | prev | 1476 | 2577.1 | 27.5 | 37.3 | 1551.5 | 2734 | 47 | 5.4 | Lbs. | 34.905 | 30.525 | 0.5625 | 21 |  | Trtd | 18.9 | 7.53 | AC.1 | 0.319 | AC.2 | 0.266
| Total | 764000 | 7000 | 36990 | 52000 | 611000 | 0 | 32990 | 37010 |  |  |  | Total | 1363300 |  |  |  | Total | 11 | 10.5 | 0 | 0.2 | 12 | 11.1 | 0.3 | 0.1 | mg/L | 3.0438 | 2.6619 | 0.049052 | 1.8313 |  |  |  |  | Raw.Trb. | 2.13 | Cmb.Trb. | 0.038
4 | Pres. | 113166000 | 1069350 | 2513280 | 4239500 | 194668000 | 1805440 | 5524590 | 9559730 | 1335000 | 34000 | 1369000 | now | 1080241200 |  | 0 | 1.19 | now | 1498.1 | 2598.4 | 27.7 | 37.5 | 1574.7 | 2756.3 | 47.3 | 5.5 | "/lb | 3.25 | 14.25 | 2.5 | 9 | 9 | Raw | 17.4 | 7.4 | ef.turb.1 | 0.043 | ef.turb.2 | 0.066
| Prev | 112537000 | 1069350 | 2513280 | 4227510 | 193962000 | 1796440 | 5524590 | 9546720 |  |  |  | prev | 1078853500 |  |  |  | prev | 1487 | 2587.6 | 27.5 | 37.5 | 1563.5 | 2745.1 | 47.3 | 5.5 | Lbs. | 34.905 | 31.35 | 0.625 | 18 |  | Trtd | 17.9 | 7.89 | AC.1 | 0.328 | AC.2 | 0.185
| Total | 629000 | 0 | 0 | 11990 | 706000 | 9000 | 0 | 13010 |  |  |  | Total | 1387700 |  |  |  | Total | 11.1 | 10.8 | 0.2 | 0 | 11.2 | 11.2 | 0 | 0 | mg/L | 3.135 | 2.8157 | 0.056135 | 1.6167 |  |  |  |  | Raw.Trb. | 1.85 | Cmb.Trb. | 0.049
5 | Pres. | 113985000 | 1076350 | 2549280 | 4284500 | 195431000 | 1812440 | 5556590 | 9589740 | 1582000 | 157010 | 1739010 | now | 1081398900 | 0 | 0.02 | 1.14 | now | 1511 | 2611.5 | 28 | 37.6 | 1588.6 | 2770.1 | 47.7 | 5.5 | "/lb | 3.375 | 17 | 2.5 | 10 | 10 | Raw | 16.3 | 7.55 | ef.turb.1 | 0.04 | ef.turb.2 | 0.06
| Prev | 113166000 | 1069350 | 2513280 | 4239500 | 194668000 | 1805440 | 5524590 | 9559730 |  |  |  | prev | 1080241200 |  |  |  | prev | 1498.1 | 2598.4 | 27.7 | 37.5 | 1574.7 | 2756.3 | 47.3 | 5.5 | Lbs. | 36.2475 | 37.4 | 0.625 | 20 |  | Trtd | 18.7 | 7.75 | AC.1 | 0.23 | AC.2 | 0.28
| Total | 819000 | 7000 | 36000 | 45000 | 763000 | 7000 | 32000 | 30010 |  |  |  | Total | 1157700 |  |  |  | Total | 12.9 | 13.1 | 0.3 | 0.1 | 13.9 | 13.8 | 0.4 | 0 | mg/L | 2.7473 | 2.8346 | 0.04737 | 1.5159 |  |  |  |  | Raw.Trb. | 1.86 | Cmb.Trb. | 0.05
6 | Pres. | 114349000 | 1076350 | 2549280 | 4297500 | 195768000 | 1812440 | 5556590 | 9602750 | 701000 | 26010 | 727010 | now | 1082381000 |  | 0.17 | 1.13 | now | 1516.8 | 2617.3 | 28 | 37.6 | 1594.5 | 2776 | 47.7 | 5.5 | "/lb | 1.5 | 8 | 0.875 | 4 | 4 | Raw | 14.6 | 7.51 | ef.turb.1 | 0.043 | ef.turb.2 | 0.049
| Prev | 113985000 | 1076350 | 2549280 | 4284500 | 195431000 | 1812440 | 5556590 | 9589740 |  |  |  | prev | 1081398900 |  |  |  | prev | 1511 | 2611.5 | 28 | 37.6 | 1588.6 | 2770.1 | 47.7 | 5.5 | Lbs. | 16.11 | 17.6 | 0.21875 | 8 |  | Trtd | 16.2 | 7.78 | AC.1 | 0.3 | AC.2 | 0.35
| Total | 364000 | 0 | 0 | 13000 | 337000 | 0 | 0 | 13010 |  |  |  | Total | 982100 |  |  |  | Total | 5.8 | 5.8 | 0 | 0 | 5.9 | 5.9 | 0 | 0 | mg/L | 2.7556 | 3.0104 | 0.037417 | 1.3684 |  |  |  |  | Raw.Trb. | 1.51 | Cmb.Trb. | 0.037
7 | Pres. | 115450000 | 1086350 | 2586280 | 4336500 | 195792000 | 1812440 | 5556590 | 9602750 | 1125000 | 86000 | 1211000 | now | 1083407900 |  | 0.01 | 1.05 | now | 1529.9 | 2617.7 | 28 | 37.7 | 1608.3 | 2776.4 | 47.9 | 5.6 | "/lb | 2.375 | 9.25 | 1 | 13 | 0 | Raw | 13.5 | 7.44 | ef.turb.1 | 0.04 | ef.turb.2 | 0.05
| Prev | 114349000 | 1076350 | 2549280 | 4297500 | 195768000 | 1812440 | 5556590 | 9602750 |  |  |  | prev | 1082381000 |  |  |  | prev | 1516.8 | 2617.3 | 28 | 37.6 | 1594.5 | 2776 | 47.7 | 5.5 | Lbs. | 25.5075 | 20.35 | 0.25 | 13 |  | Trtd | 14.6 | 7.78 | AC.1 | 0.28 | AC.2 | 0.31
| Total | 1101000 | 10000 | 37000 | 39000 | 24000 | 0 | 0 | 0 |  |  |  | Total | 1026900 |  |  |  | Total | 13.1 | 0.4 | 0 | 0.1 | 13.8 | 0.4 | 0.2 | 0.1 | mg/L | 2.7186 | 2.1689 | 0.026645 | 1.3856 |  |  |  |  | Raw.Trb. | 1.53 | Cmb.Trb. | 0.04
8 | Pres. | 116647000 | 1096350 | 2586280 | 4354500 | 195792000 | 1812440 | 5556590 | 9602750 | 1197000 | 28000 | 1225000 | now | 1084507600 |  | 0.01 | 1.05 | now | 1544 | 2617.7 | 28 | 37.8 | 1622.7 | 2776.4 | 47.9 | 5.6 | "/lb | 2.625 | 9.125 | 1.0625 | 15 | 0 | Raw | 14 | 7.56 | ef.turb.1 | 0.04 | ef.turb.2 | 0
| Prev | 115450000 | 1086350 | 2586280 | 4336500 | 195792000 | 1812440 | 5556590 | 9602750 |  |  |  | prev | 1083407900 |  |  |  | prev | 1529.9 | 2617.7 | 28 | 37.7 | 1608.3 | 2776.4 | 47.9 | 5.6 | Lbs. | 28.1925 | 20.075 | 0.26562 | 15 |  | Trtd | 15.3 | 7.84 | AC.1 | 0.31 | AC.2 | 0
| Total | 1197000 | 10000 | 0 | 18000 | 0 | 0 | 0 | 0 |  |  |  | Total | 1099700 |  |  |  | Total | 14.1 | 0 | 0 | 0.1 | 14.4 | 0 | 0 | 0 | mg/L | 2.8241 | 2.0109 | 0.026608 | 1.5026 |  |  |  |  | Raw.Trb. | 1.35 | Cmb.Trb. | 0.04
9 | Pres. | 117945000 | 1096350 | 2619280 | 4414490 | 195792000 | 1812440 | 5556590 | 9602750 | 1298000 | 92990 | 1390990 | now | 1085697500 |  | 0.12 | 1.07 | now | 1559.4 | 2617.7 | 28 | 37.8 | 1638.8 | 2776.4 | 48 | 5.7 | "/lb | 3.25 | 10 | 1.25 | 16 |  | Raw | 13.5 | 7.47 | ef.turb.1 | 0.04 | ef.turb.2 | 0
| Prev | 116647000 | 1096350 | 2586280 | 4354500 | 195792000 | 1812440 | 5556590 | 9602750 |  |  |  | prev | 1084507600 |  |  |  | prev | 1544 | 2617.7 | 28 | 37.8 | 1622.7 | 2776.4 | 47.9 | 5.6 | Lbs. | 34.905 | 22 | 0.3125 | 16 |  | Trtd | 15.1 | 7.77 | AC.1 | 0.601 | AC.2 | 0
| Total | 1298000 | 0 | 33000 | 59990 | 0 | 0 | 0 | 0 |  |  |  | Total | 1189900 |  |  |  | Total | 15.4 | 0 | 0 | 0 | 16.1 | 0 | 0.1 | 0.1 | mg/L | 3.2244 | 2.0323 | 0.028868 | 1.478 |  |  |  |  | Raw.Trb. | 1.5 | Cmb.Trb. | 0.034
10 | Pres. | 119233000 | 1106350 | 2651270 | 4444490 | 195792000 | 1812440 | 5556590 | 9602750 | 1288000 | 71990 | 1359990 | now | 1086805200 |  | 0 | 1.08 | now | 1574.6 | 2617.7 | 28 | 37.9 | 1654.4 | 2776.4 | 48.2 | 5.7 | "/lb | 2.75 | 9.9375 | 1.5 | 16 | 0 | Raw | 14.6 | 7.47 | ef.turb.1 | 0.041 | ef.turb.2 | 0
| Prev | 117945000 | 1096350 | 2619280 | 4414490 | 195792000 | 1812440 | 5556590 | 9602750 |  |  |  | prev | 1085697500 |  |  |  | prev | 1559.4 | 2617.7 | 28 | 37.8 | 1638.8 | 2776.4 | 48 | 5.7 | Lbs. | 29.535 | 21.8625 | 0.375 | 16 |  | Trtd | 15.6 | 7.69 | AC.1 | 0.3 | AC.2 | 0
| Total | 1288000 | 10000 | 31990 | 30000 | 0 | 0 | 0 | 0 |  |  |  | Total | 1107700 |  |  |  | Total | 15.2 | 0 | 0 | 0.1 | 15.6 | 0 | 0.2 | 0 | mg/L | 2.7495 | 2.0353 | 0.03491 | 1.4895 |  |  |  |  | Raw.Trb. | 1.36 | Cmb.Trb. | 0.037
11 | Pres. | 120117000 | 1116350 | 2684270 | 4483490 | 195792000 | 1812440 | 5556590 | 9602750 | 884000 | 82000 | 966000 | now | 1087836700 |  | 0.12 | 1.04 | now | 1585 | 2617.7 | 28 | 38 | 1665.4 | 2776.4 | 48.3 | 5.8 | "/lb | 2.125 | 6.875 | 1.375 | 11 | 0 | Raw | 14.7 | 7.55 | ef.turb.1 | 0.045 | ef.turb.2 | 0
| Prev | 119233000 | 1106350 | 2651270 | 4444490 | 195792000 | 1812440 | 5556590 | 9602750 |  |  |  | prev | 1086805200 |  |  |  | prev | 1574.6 | 2617.7 | 28 | 37.9 | 1654.4 | 2776.4 | 48.2 | 5.7 | Lbs. | 22.8225 | 15.125 | 0.34375 | 11 |  | Trtd | 15.2 | 7.8 | AC.1 | 0.334 | AC.2 | 0
| Total | 884000 | 10000 | 33000 | 39000 | 0 | 0 | 0 | 0 |  |  |  | Total | 1031500 |  |  |  | Total | 10.4 | 0 | 0 | 0.1 | 11 | 0 | 0.1 | 0.1 | mg/L | 3.0956 | 2.0515 | 0.046626 | 1.492 |  |  |  |  | Raw.Trb. | 1.11 | Cmb.Trb. | 0.038
12 | Pres. | 121147000 | 1116350 | 2684270 | 4492490 | 195792000 | 1812440 | 5556590 | 9602750 | 1030000 | 9000 | 1039000 | now | 1088733500 |  | 0.55 | 1 | now | 1597.2 | 2617.7 | 28 | 38 | 1677.7 | 2776.4 | 48.3 | 5.8 | "/lb | 2.5 | 7.9375 | 1.5 | 13 | 0 | Raw | 15.9 | 7.58 | ef.turb.1 | 0.04 | ef.turb.2 | 0
| Prev | 120117000 | 1116350 | 2684270 | 4483490 | 195792000 | 1812440 | 5556590 | 9602750 |  |  |  | prev | 1087836700 |  |  |  | prev | 1585 | 2617.7 | 28 | 38 | 1665.4 | 2776.4 | 48.3 | 5.8 | Lbs. | 26.85 | 17.4625 | 0.375 | 13 |  | Trtd | 15.8 | 7.83 | AC.1 | 0.367 | AC.2 | 0
| Total | 1030000 | 0 | 0 | 9000 | 0 | 0 | 0 | 0 |  |  |  | Total | 896800 |  |  |  | Total | 12.2 | 0 | 0 | 0 | 12.3 | 0 | 0 | 0 | mg/L | 3.1257 | 2.0328 | 0.043654 | 1.5134 |  |  |  |  | Raw.Trb. | 1.23 | Cmb.Trb. | 0.037
13 | Pres. | 122061000 | 1126350 | 2717270 | 4544480 | 195792000 | 1812440 | 5556590 | 9602750 | 914000 | 94990 | 1008990 | now | 1089685900 |  | 0.31 | 0.96 | now | 1608 | 2617.7 | 28 | 38.2 | 1689.3 | 2776.4 | 48.5 | 5.8 | "/lb | 1.875 | 7 | 1 | 13 | 0 | Raw | 16.9 | 7.48 | ef.turb.1 | 0.043 | ef.turb.2 | 0
| Prev | 121147000 | 1116350 | 2684270 | 4492490 | 195792000 | 1812440 | 5556590 | 9602750 |  |  |  | prev | 1088733500 |  |  |  | prev | 1597.2 | 2617.7 | 28 | 38 | 1677.7 | 2776.4 | 48.3 | 5.8 | Lbs. | 20.1375 | 15.4 | 0.25 | 13 |  | Trtd | 16.2 | 7.94 | AC.1 | 0.317 | AC.2 | 0
| Total | 914000 | 10000 | 33000 | 51990 | 0 | 0 | 0 | 0 |  |  |  | Total | 952400 |  |  |  | Total | 10.8 | 0 | 0 | 0.2 | 11.6 | 0 | 0.2 | 0 | mg/L | 2.6418 | 2.0203 | 0.032797 | 1.7054 |  |  |  |  | Raw.Trb. | 1.62 | Cmb.Trb. | 0.035
14 | Pres. | 123170000 | 1136350 | 2717270 | 4553480 | 195792000 | 1812440 | 5556590 | 9602750 | 1109000 | 19000 | 1128000 | now | 1090637500 |  | 0.12 | 1.1 | now | 1621 | 2617.7 | 28 | 38.3 | 1702.6 | 2776.4 | 48.5 | 5.8 | "/lb | 3.5 | 8 | 1.5 | 17 | 0 | Raw | 15.7 | 7.55 | ef.turb.1 | 0.044 | ef.turb.2 | 0
| Prev | 122061000 | 1126350 | 2717270 | 4544480 | 195792000 | 1812440 | 5556590 | 9602750 |  |  |  | prev | 1089685900 |  |  |  | prev | 1608 | 2617.7 | 28 | 38.2 | 1689.3 | 2776.4 | 48.5 | 5.8 | Lbs. | 37.59 | 17.6 | 0.375 | 17 |  | Trtd | 15.8 | 7.75 | AC.1 | 0.49 | AC.2 | 0
| Total | 1109000 | 10000 | 0 | 9000 | 0 | 0 | 0 | 0 |  |  |  | Total | 951600 |  |  |  | Total | 13 | 0 | 0 | 0.1 | 13.3 | 0 | 0 | 0 | mg/L | 4.0642 | 1.9029 | 0.040545 | 1.838 |  |  |  |  | Raw.Trb. | 2.01 | Cmb.Trb. | 0.037
15 | Pres. | 123887000 | 1136350 | 2749270 | 4592480 | 195792000 | 1812440 | 5556590 | 9602750 | 717000 | 71000 | 788000 | now | 1091583600 |  | 0.12 | 1.12 | now | 1629.7 | 2617.7 | 28 | 38.3 | 1711.7 | 2776.4 | 48.6 | 5.9 | "/lb | 2 | 5.625 | 1.125 | 10 | 0 | Raw | 15.4 | 7.5 | ef.turb.1 | 0.038 | ef.turb.2 | 0
| Prev | 123170000 | 1136350 | 2717270 | 4553480 | 195792000 | 1812440 | 5556590 | 9602750 |  |  |  | prev | 1090637500 |  |  |  | prev | 1621 | 2617.7 | 28 | 38.3 | 1702.6 | 2776.4 | 48.5 | 5.8 | Lbs. | 21.48 | 12.375 | 0.28125 | 10 |  | Trtd | 15.9 | 7.74 | AC.1 | 0.432 | AC.2 | 0
| Total | 717000 | 0 | 32000 | 39000 | 0 | 0 | 0 | 0 |  |  |  | Total | 946100 |  |  |  | Total | 8.7 | 0 | 0 | 0 | 9.1 | 0 | 0.1 | 0.1 | mg/L | 3.5921 | 2.0695 | 0.047034 | 1.6723 |  |  |  |  | Raw.Trb. | 2.3 | Cmb.Trb. | 0.035
16 | Pres. | 124792000 | 1143350 | 2749270 | 4609480 | 196173000 | 1818440 | 5588590 | 9646760 | 1286000 | 106010 | 1392010 | now | 1092725900 |  | 0 | 1.09 | now | 1642.2 | 2624.3 | 28 | 38.6 | 1724.6 | 2783.8 | 48.8 | 5.9 | "/lb | 3.125 | 12.25 | 1.5 | 9 | 4 | Raw | 14.8 | 7.47 | ef.turb.1 | 0.038 | ef.turb.2 | 0.062
| Prev | 123887000 | 1136350 | 2749270 | 4592480 | 195792000 | 1812440 | 5556590 | 9602750 |  |  |  | prev | 1091583600 |  |  |  | prev | 1629.7 | 2617.7 | 28 | 38.3 | 1711.7 | 2776.4 | 48.6 | 5.9 | Lbs. | 33.5625 | 26.95 | 0.375 | 13 |  | Trtd | 15.6 | 7.74 | AC.1 | 0.296 | AC.2 | 0.3387
| Total | 905000 | 7000 | 0 | 17000 | 381000 | 6000 | 32000 | 44010 |  |  |  | Total | 1142300 |  |  |  | Total | 12.5 | 6.6 | 0 | 0.3 | 12.9 | 7.4 | 0.2 | 0 | mg/L | 3.1293 | 2.5128 | 0.034964 | 1.2121 |  |  |  |  | Raw.Trb. | 2.11 | Cmb.Trb. | 0.049
17 | Pres. | 125660000 | 1143350 | 2781260 | 4639480 | 196917000 | 1818440 | 5620590 | 9677780 | 1612000 | 125010 | 1737010 | now | 1094012900 |  | 0 | 0.98 | now | 1655.3 | 2637.3 | 28.1 | 38.6 | 1738.3 | 2797.3 | 49.2 | 6 | "/lb | 4.125 | 16.25 | 2 | 14 | 11 | Raw | 15.9 | 7.47 | ef.turb.1 | 0.038 | ef.turb.2 | 0.057
| Prev | 124792000 | 1143350 | 2749270 | 4609480 | 196173000 | 1818440 | 5588590 | 9646760 |  |  |  | prev | 1092725900 |  |  |  | prev | 1642.2 | 2624.3 | 28 | 38.6 | 1724.6 | 2783.8 | 48.8 | 5.9 | Lbs. | 44.3025 | 35.75 | 0.5 | 25 |  | Trtd | 16.4 | 7.81 | AC.1 | 0.333 | AC.2 | 0.401
| Total | 868000 | 0 | 31990 | 30000 | 744000 | 0 | 32000 | 31020 |  |  |  | Total | 1287000 |  |  |  | Total | 13.1 | 13 | 0.1 | 0 | 13.7 | 13.5 | 0.4 | 0.1 | mg/L | 3.2953 | 2.6592 | 0.037191 | 1.8596 |  |  |  |  | Raw.Trb. | 1.62 | Cmb.Trb. | 0.04
18 | Pres. | 126269000 | 1150350 | 2781260 | 4659470 | 197454000 | 1825440 | 5620590 | 9695780 | 1146000 | 51990 | 1197990 | now | 1095400300 |  | 0 | 1.07 | now | 1664.8 | 2647.5 | 28.1 | 38.9 | 1748.3 | 2808 | 49.2 | 6 | "/lb | 2.75 | 11.5 | 1.625 | 7 | 6 | Raw | 16.3 | 7.5 | ef.turb.1 | 0.039 | ef.turb.2 | 0.051
| Prev | 125660000 | 1143350 | 2781260 | 4639480 | 196917000 | 1818440 | 5620590 | 9677780 |  |  |  | prev | 1094012900 |  |  |  | prev | 1655.3 | 2637.3 | 28.1 | 38.6 | 1738.3 | 2797.3 | 49.2 | 6 | Lbs. | 29.535 | 25.3 | 0.40625 | 13 |  | Trtd | 16.4 | 7.87 | AC.1 | 0.254 | AC.2 | 0.263
| Total | 609000 | 7000 | 0 | 19990 | 537000 | 7000 | 0 | 18000 |  |  |  | Total | 1387400 |  |  |  | Total | 9.5 | 10.2 | 0 | 0.3 | 10 | 10.7 | 0 | 0 | mg/L | 3.0902 | 2.6471 | 0.042505 | 1.3602 |  |  |  |  | Raw.Trb. | 1.54 | Cmb.Trb. | 0.037
19 | Pres. | 127077000 | 1150350 | 2814260 | 4686470 | 198148000 | 1825440 | 5652580 | 9721800 | 1502000 | 118010 | 1620010 | now | 1096636800 |  | 0 | 1.02 | now | 1677.2 | 2659.7 | 28.2 | 38.9 | 1761.1 | 2820.5 | 49.2 | 6 | "/lb | 3.75 | 12 | 1.75 | 13 | 7 | Raw | 16.9 | 7.64 | ef.turb.1 | 0.04 | ef.turb.2 | 0.05
| Prev | 126269000 | 1150350 | 2781260 | 4659470 | 197454000 | 1825440 | 5620590 | 9695780 |  |  |  | prev | 1095400300 |  |  |  | prev | 1664.8 | 2647.5 | 28.1 | 38.9 | 1748.3 | 2808 | 49.2 | 6 | Lbs. | 40.275 | 26.4 | 0.4375 | 20 |  | Trtd | 17 | 7.84 | AC.1 | 0.29 | AC.2 | 0.36
| Total | 808000 | 0 | 33000 | 27000 | 694000 | 0 | 31990 | 26020 |  |  |  | Total | 1236500 |  |  |  | Total | 12.4 | 12.2 | 0.1 | 0 | 12.8 | 12.5 | 0 | 0 | mg/L | 3.2151 | 2.1075 | 0.034925 | 1.5966 |  |  |  |  | Raw.Trb. | 1.63 | Cmb.Trb. | 0.04
20 | Pres. | 127764000 | 1157350 | 2814260 | 4702470 | 198710000 | 1831440 | 5652580 | 9733880 | 1249000 | 41080 | 1290080 | now | 1098060300 |  | 0 | 1.02 | now | 1689.9 | 2669.4 | 28.4 | 38.9 | 1771.2 | 2830.6 | 49.5 | 6 | "/lb | 3 | 12.5 | 1.375 | 11 | 5 | Raw | 17.5 | 7.53 | ef.turb.1 | 0.046 | ef.turb.2 | 0.048
| Prev | 127077000 | 1150350 | 2814260 | 4686470 | 198148000 | 1825440 | 5652580 | 9721800 |  |  |  | prev | 1096636800 |  |  |  | prev | 1677.2 | 2659.7 | 28.2 | 38.9 | 1761.1 | 2820.5 | 49.2 | 6 | Lbs. | 32.22 | 27.5 | 0.34375 | 16 |  | Trtd | 18.1 | 7.84 | AC.1 | 0.27 | AC.2 | 0.27
| Total | 687000 | 7000 | 0 | 16000 | 562000 | 6000 | 0 | 12080 |  |  |  | Total | 1423500 |  |  |  | Total | 12.7 | 9.7 | 0.2 | 0 | 10.1 | 10.1 | 0.3 | 0 | mg/L | 3.0931 | 2.64 | 0.033 | 1.536 |  |  |  |  | Raw.Trb. | 1.62 | Cmb.Trb. | 0.04
21 | Pres. | 128160000 | 1157350 | 2846260 | 4727470 | 199653000 | 1831440 | 5684580 | 9753810 | 1339000 | 108930 | 1447930 | now | 1099438300 |  | 0 | 1.01 | now | 1701.9 | 2684.5 | 28.5 | 39 | 1786.6 | 2845.9 | 49.8 | 6.1 | "/lb | 5 | 19.25 | 1.125 | 19 | 7 | Raw | 18.9 | 7.51 | ef.turb.1 | 0.049 | ef.turb.2 | 0.055
| Prev | 127764000 | 1157350 | 2814260 | 4702470 | 198710000 | 1831440 | 5652580 | 9733880 |  |  |  | prev | 1098060300 |  |  |  | prev | 1689.9 | 2669.4 | 28.4 | 38.9 | 1771.2 | 2830.6 | 49.5 | 6 | Lbs. | 53.7 | 42.35 | 0.28125 | 26 |  | Trtd | 19 | 7.82 | AC.1 | 0.352 | AC.2 | 0.447
| Total | 396000 | 0 | 32000 | 25000 | 943000 | 0 | 32000 | 19930 |  |  |  | Total | 1378000 |  |  |  | Total | 12 | 15.1 | 0.1 | 0.1 | 15.4 | 15.3 | 0.3 | 0.1 | mg/L | 4.8087 | 3.7923 | 0.025185 | 2.3282 |  |  |  |  | Raw.Trb. | 1.62 | Cmb.Trb. | 0.03
22 | Pres. | 129492000 | 1164350 | 2879260 | 4774470 | 200359000 | 1839440 | 5684580 | 9782820 | 2038000 | 124010 | 2162010 | now | 1100991400 |  | 0 | 1.11 | now | 1712.7 | 2695.9 | 28.5 | 39.2 | 1798.2 | 2857.9 | 50 | 6.1 | "/lb | 2.125 | 14.5 | 1 | 10 | 8 | Raw | 19.2 | 7.62 | ef.turb.1 | 0.04 | ef.turb.2 | 0.05
| Prev | 128160000 | 1157350 | 2846260 | 4727470 | 199653000 | 1831440 | 5684580 | 9753810 |  |  |  | prev | 1099438300 |  |  |  | prev | 1701.9 | 2684.5 | 28.5 | 39 | 1786.6 | 2845.9 | 49.8 | 6.1 | Lbs. | 22.8225 | 31.9 | 0.25 | 18 |  | Trtd | 19.9 | 7.91 | AC.1 | 0.21 | AC.2 | 0.21
| Total | 1332000 | 7000 | 33000 | 47000 | 706000 | 8000 | 0 | 29010 |  |  |  | Total | 1553100 |  |  |  | Total | 10.8 | 11.4 | 0 | 0.2 | 11.6 | 12 | 0.2 | 0 | mg/L | 1.3427 | 1.8768 | 0.014709 | 1.059 |  |  |  |  | Raw.Trb. | 1.54 | Cmb.Trb. | 0.04
23 | Pres. | 130050000 | 1164350 | 2915460 | 4915460 | 201012000 | 1839440 | 5717580 | 9813830 | 1211000 | 241200 | 1452200 | now | 1102393100 |  | 0 | 0.93 | now | 1720.5 | 2705.3 | 28.5 | 39.3 | 1808.1 | 2867.8 | 50.5 | 6.3 | "/lb | 3.25 | 7.875 | 0.75 | 7 | 6 | Raw | 19.3 | 7.69 | ef.turb.1 | 0.05 | ef.turb.2 | 0.06
| Prev | 129492000 | 1164350 | 2879260 | 4774470 | 200359000 | 1839440 | 5684580 | 9782820 |  |  |  | prev | 1100991400 |  |  |  | prev | 1712.7 | 2695.9 | 28.5 | 39.2 | 1798.2 | 2857.9 | 50 | 6.1 | Lbs. | 34.905 | 17.325 | 0.1875 | 13 |  | Trtd | 19.7 | 7.8 | AC.1 | 0.26 | AC.2 | 0.33
| Total | 558000 | 0 | 36200 | 140990 | 653000 | 0 | 33000 | 31010 |  |  |  | Total | 1401700 |  |  |  | Total | 7.8 | 9.4 | 0 | 0.1 | 9.9 | 9.9 | 0.5 | 0.2 | mg/L | 3.456 | 1.7154 | 0.018565 | 1.2872 |  |  |  |  | Raw.Trb. | 1.52 | Cmb.Trb. | 0.04
24 | Pres. | 130855000 | 1180360 | 2944250 | 5037450 | 201945000 | 1847440 | 5717580 | 9827840 | 1738000 | 188800 | 1926800 | now | 1103867500 |  | 0 | 0.96 | now | 1731.7 | 2718.5 | 28.9 | 39.3 | 1821.2 | 2881.3 | 50.5 | 6.3 | "/lb | 3 | 12.5 | 1.125 | 15 | 11 | Raw | 18.6 | 7.66 | ef.turb.1 | 0.055 | ef.turb.2 | 0.052
| Prev | 130050000 | 1164350 | 2915460 | 4915460 | 201012000 | 1839440 | 5717580 | 9813830 |  |  |  | prev | 1102393100 |  |  |  | prev | 1720.5 | 2705.3 | 28.5 | 39.3 | 1808.1 | 2867.8 | 50.5 | 6.3 | Lbs. | 32.22 | 27.5 | 0.28125 | 26 |  | Trtd | 20.2 | 7.78 | AC.1 | 0.22 | AC.2 | 0.29
| Total | 805000 | 16010 | 28790 | 121990 | 933000 | 8000 | 0 | 14010 |  |  |  | Total | 1474400 |  |  |  | Total | 11.2 | 13.2 | 0.4 | 0 | 13.1 | 13.5 | 0 | 0 | mg/L | 2.2228 | 1.8972 | 0.019403 | 1.7937 |  |  |  |  | Raw.Trb. | 1.59 | Cmb.Trb. | 0.036
25 | Pres. | 131839000 | 1180360 | 2976250 | 5077440 | 202906000 | 1847440 | 5749580 | 9865850 | 1945000 | 142000 | 2087000 | now | 1105620500 |  | 0 | 1.09 | now | 1745.5 | 2732.3 | 28.9 | 39.4 | 1835.6 | 2895.6 | 50.8 | 6.4 | "/lb | 4.5 | 13.875 | 1.75 | 13 | 13 | Raw | 19.6 | 7.55 | ef.turb.1 | 0.039 | ef.turb.2 | 0.05
| Prev | 130855000 | 1180360 | 2944250 | 5037450 | 201945000 | 1847440 | 5717580 | 9827840 |  |  |  | prev | 1103867500 |  |  |  | prev | 1731.7 | 2718.5 | 28.9 | 39.3 | 1821.2 | 2881.3 | 50.5 | 6.3 | Lbs. | 48.33 | 30.525 | 0.4375 | 26 |  | Trtd | 20.4 | 7.93 | AC.1 | 0.224 | AC.2 | 0.253
| Total | 984000 | 0 | 32000 | 39990 | 961000 | 0 | 32000 | 38010 |  |  |  | Total | 1753000 |  |  |  | Total | 13.8 | 13.8 | 0 | 0.1 | 14.4 | 14.3 | 0.3 | 0.1 | mg/L | 2.9794 | 1.8818 | 0.026971 | 1.6028 |  |  |  |  | Raw.Trb. | 1.39 | Cmb.Trb. | 0.036
26 | Pres. | 132244000 | 1303360 | 2976250 | 5092440 | 204229000 | 1855440 | 5781570 | 9889960 | 1728000 | 202100 | 1930100 | now | 1107183200 |  | 0 | 0.98 | now | 1751.3 | 2751 | 29.7 | 40.8 | 1843.9 | 2914.7 | 51 | 6.4 | "/lb | 2.9375 | 11.75 | 1 | 13 | 12 | Raw | 20.7 | 7.68 | ef.turb.1 | 0.044 | ef.turb.2 | 0.055
| Prev | 131839000 | 1180360 | 2976250 | 5077440 | 202906000 | 1847440 | 5749580 | 9865850 |  |  |  | prev | 1105620500 |  |  |  | prev | 1745.5 | 2732.3 | 28.9 | 39.4 | 1835.6 | 2895.6 | 50.8 | 6.4 | Lbs. | 31.5488 | 25.85 | 0.25 | 25 |  | Trtd | 21.6 | 7.94 | AC.1 | 0.191 | AC.2 | 0.179
| Total | 405000 | 123000 | 0 | 15000 | 1323000 | 8000 | 31990 | 24110 |  |  |  | Total | 1562700 |  |  |  | Total | 5.8 | 18.7 | 0.8 | 1.4 | 8.3 | 19.1 | 0.2 | 0 | mg/L | 2.1891 | 1.7937 | 0.017347 | 1.7347 |  |  |  |  | Raw.Trb. | 1.33 | Cmb.Trb. | 0.038
27 | Pres. | 133067000 | 1311360 | 2976250 | 5115440 | 205049000 | 1863440 | 5781570 | 9903876 | 1643000 | 52916 | 1695916 | now | 1108882800 |  | 0 | 1.01 | now | 1762.7 | 2762.6 | 29.9 | 40.8 | 1855.8 | 2926.6 | 51 | 6.4 | "/lb | 3 | 11.5 | 0.875 | 13 | 12 | Raw | 21.4 | 7.64 | ef.turb.1 | 0.042 | ef.turb.2 | 0.056
| Prev | 132244000 | 1303360 | 2976250 | 5092440 | 204229000 | 1855440 | 5781570 | 9889960 |  |  |  | prev | 1107183200 |  |  |  | prev | 1751.3 | 2751 | 29.7 | 40.8 | 1843.9 | 2914.7 | 51 | 6.4 | Lbs. | 32.22 | 25.3 | 0.21875 | 25 |  | Trtd | 22.2 | 7.86 | AC.1 | 0.606 | AC.2 | 0.258
| Total | 823000 | 8000 | 0 | 23000 | 820000 | 8000 | 0 | 13916 |  |  |  | Total | 1699600 |  |  |  | Total | 11.4 | 11.6 | 0.2 | 0 | 11.9 | 11.9 | 0 | 0 | mg/L | 2.3514 | 1.8464 | 0.015964 | 1.8245 |  |  |  |  | Raw.Trb. | 1.41 | Cmb.Trb. | 0.039
28 | Pres. | 134125000 | 1319360 | 3009250 | 5141440 | 206079000 | 1863440 | 5813510 | 9929880 | 2088000 | 124944 | 2212944 | now | 1110808200 |  | 0 | 0.98 | now | 1777.3 | 2777.4 | 30.1 | 40.9 | 1871 | 2941.7 | 51.3 | 6.5 | "/lb | 3.625 | 13 | 1.125 | 16 | 15 | Raw | 22.8 | 7.71 | ef.turb.1 | 0.04 | ef.turb.2 | 0.05
| Prev | 133067000 | 1311360 | 2976250 | 5115440 | 205049000 | 1863440 | 5781570 | 9903876 |  |  |  | prev | 1108882800 |  |  |  | prev | 1762.7 | 2762.6 | 29.9 | 40.8 | 1855.8 | 2926.6 | 51 | 6.4 | Lbs. | 38.9325 | 28.6 | 0.28125 | 31 |  | Trtd | 25.4 | 7.8 | AC.1 | 0.2 | AC.2 | 0.28
| Total | 1058000 | 8000 | 33000 | 26000 | 1030000 | 0 | 31940 | 26004 |  |  |  | Total | 1925400 |  |  |  | Total | 14.6 | 14.8 | 0.2 | 0.1 | 15.2 | 15.1 | 0.3 | 0.1 | mg/L | 2.2357 | 1.6424 | 0.016151 | 1.7802 |  |  |  |  | Raw.Trb. | 1.41 | Cmb.Trb. | 0.04
29 | Pres. | 134948000 | 1327360 | 3042240 | 5167440 | 206907000 | 1871440 | 5813570 | 9943880 | 1651000 | 89050 | 1740050 | now | 1112420800 |  | 0 | 0.98 | now | 1788.7 | 2789.2 | 30.1 | 41.1 | 1882.9 | 2953.8 | 51.5 | 6.5 | "/lb | 3.125 | 11.25 | 1 | 12 | 12 | Raw | 22.7 | 7.66 | ef.turb.1 | 0.04 | ef.turb.2 | 0.06
| Prev | 134125000 | 1319360 | 3009250 | 5141440 | 206079000 | 1863440 | 5813510 | 9929880 |  |  |  | prev | 1110808200 |  |  |  | prev | 1777.3 | 2777.4 | 30.1 | 40.9 | 1871 | 2941.7 | 51.3 | 6.5 | Lbs. | 33.5625 | 24.75 | 0.25 | 24 |  | Trtd | 24.1 | 7.78 | AC.1 | 0.21 | AC.2 | 0.17
| Total | 823000 | 8000 | 32990 | 26000 | 828000 | 8000 | 60 | 14000 |  |  |  | Total | 1612600 |  |  |  | Total | 11.4 | 11.8 | 0 | 0.2 | 11.9 | 12.1 | 0.2 | 0 | mg/L | 2.4375 | 1.7975 | 0.018156 | 1.743 |  |  |  |  | Raw.Trb. | 1.35 | Cmb.Trb. | 0.04
30 | Pres. | 135862000 | 1336360 | 3042240 | 5182440 | 207755000 | 1879440 | 5846570 | 9969900 | 1762000 | 91020 | 1853020 | now | 1114010800 |  | 0 | 0.89 | now | 1801.4 | 2801.4 | 30.4 | 41.1 | 1895.9 | 2966.5 | 51.7 | 6.5 | "/lb | 3.25 | 11.9375 | 3 | 13 | 12 | Raw | 21.8 | 7.61 | ef.turb.1 | 0.05 | ef.turb.2 | 0.05
| Prev | 134948000 | 1327360 | 3042240 | 5167440 | 206907000 | 1871440 | 5813570 | 9943880 |  |  |  | prev | 1112420800 |  |  |  | prev | 1788.7 | 2789.2 | 30.1 | 41.1 | 1882.9 | 2953.8 | 51.5 | 6.5 | Lbs. | 34.905 | 26.2625 | 0.75 | 25 |  | Trtd | 23.7 | 7.9 | AC.1 | 0.24 | AC.2 | 0.31
| Total | 914000 | 9000 | 0 | 15000 | 848000 | 8000 | 33000 | 26020 |  |  |  | Total | 1590000 |  |  |  | Total | 12.7 | 12.2 | 0.3 | 0 | 13 | 12.7 | 0.2 | 0 | mg/L | 2.3753 | 1.7872 | 0.051037 | 1.7012 |  |  |  |  | Raw.Trb. | 1.42 | Cmb.Trb. | 0.04
[10 empty] | Totals | [6 empty] | AVG | [10 empty] | totals | [5 empty] | AVG TRTD |  |  |  | Avg.Cmb.Trb.
[10 empty] | 41931000 | 3071060 | 45002060 |  | 39643000 |  | 1.55 | 1.0377 | [5 empty] | 379.9 | 245.8 |  |  |  | 999.4912 | 764.9125 | 11.1406 | 565 |  |  | 18.1533 | 7.8067 |  |  | 0.0386
[22 empty] | total- | 625.7

## July, 2021
July, 2021
Filters | [15 empty] | Rain | Cl2 | Pump Hours | [8 empty] | Chemicals | [5 empty] | Misc. |  |  | Turbidity
Day |  | CW.Tot.1 | Cla.Wst.1 | BW.Wst.1 | FTWst.1 | CW.Tot.2 | Cla.Wst.2 | BW.Wst.2 | FTWst.2 | Treated Total | Wastewater | Total Influent | Totalizer |  |  | Inches | Resid | Pump | Ef.Pmp.1 | Ef.Pmp.2 | Blo.1 | Blo.2 | URT.1 | URT.2 | BWP | SWP | Chem | ACH | SA | Poly | Cl2.1 | Cl2.2 | water | Temp | pH | F1 |  | F2
1 | Pres. | 136574000 | 1344360 | 3074240 | 5208430 | 208490000 | 1879440 | 5846570 | 9983900 | 1447000 | 79990 | 1526990 | now | 1115431200 |  | 0 | 1.01 | now | 1811.3 | 2811.9 | 30.5 | 41.1 | 1906.3 | 2977.2 | 51.8 | 6.6 | "/lb | 2.875 | 10 | 0.875 | 10 | 11 | Raw | 20.3 | 7.51 | ef.turb.1 | 0.039 | ef.turb.2 | 0.052
| Prev | 135862000 | 1336360 | 3042240 | 5182440 | 207755000 | 1879440 | 5846570 | 9969900 |  |  |  | prev | 1114010800 |  |  |  | prev | 1801.4 | 2801.4 | 30.4 | 41.1 | 1895.9 | 2966.5 | 51.7 | 6.5 | Lbs. | 30.8775 | 22 | 0.21875 | 21 |  | Trtd | 21.7 | 7.61 | AC.1 | 0.235 | AC.2 | 0.34
| Total | 712000 | 8000 | 32000 | 25990 | 735000 | 0 | 0 | 14000 |  |  |  | Total | 1420400 |  |  |  | Total | 9.9 | 10.5 | 0.1 | 0 | 10.4 | 10.7 | 0.1 | 0.1 | mg/L | 2.5586 | 1.823 | 0.018126 | 1.7401 |  |  |  |  | Raw.Trb. | 1.16 | Cmb.Trb. | 0.037
2 | Pres. | 137526000 | 1344360 | 3074240 | 5223430 | 209371000 | 1887440 | 5878570 | 10007900 | 1833000 | 79000 | 1912000 | now | 1117065400 |  | 0 | 0.91 | now | 1824.5 | 2824.5 | 30.7 | 41.1 | 1919.7 | 2990.3 | 52 | 6.6 | "/lb | 3.375 | 12.5 | 1.5 | 13 | 14 | Raw | 19.5 | 7.52 | ef.turb.1 | 0.052 | ef.turb.2 | 0.052
| Prev | 136574000 | 1344360 | 3074240 | 5208430 | 208490000 | 1879440 | 5846570 | 9983900 |  |  |  | prev | 1115431200 |  |  |  | prev | 1811.3 | 2811.9 | 30.5 | 41.1 | 1906.3 | 2977.2 | 51.8 | 6.6 | Lbs. | 36.2475 | 27.5 | 0.375 | 27 |  | Trtd | 22.8 | 7.96 | AC.1 | 0.38 | AC.2 | 0.21
| Total | 952000 | 0 | 0 | 15000 | 881000 | 8000 | 32000 | 24000 |  |  |  | Total | 1634200 |  |  |  | Total | 13.2 | 12.6 | 0.2 | 0 | 13.4 | 13.1 | 0.2 | 0 | mg/L | 2.3711 | 1.7989 | 0.02453 | 1.7662 |  |  |  |  | Raw.Trb. | 1.32 | Cmb.Trb. | 0.043
10.6
3 | Pres. | 138481000 | 1352360 | 3107240 | 5249430 | 210292000 | 1895440 | 5910560 | 10032900 | 1876000 | 131990 | 2007990 | now | 1118717300 |  | 0 | 0.98 | now | 1837.7 | 2837.7 | 31 | 41.1 | 1933.5 | 3003.8 | 52.4 | 6.6 | "/lb | 3.5 | 11.5 | 1.5 | 13 | 15 | Raw | 20 | 7.75 | ef.turb.1 | 0.04 | ef.turb.2 | 0.05
| Prev | 137526000 | 1344360 | 3074240 | 5223430 | 209371000 | 1887440 | 5878570 | 10007900 |  |  |  | prev | 1117065400 |  |  |  | prev | 1824.5 | 2824.5 | 30.7 | 41.1 | 1919.7 | 2990.3 | 52 | 6.6 | Lbs. | 37.59 | 25.3 | 0.375 | 28 |  | Trtd | 22.8 | 7.93 | AC.1 | 0.2 | AC.2 | 0.24
| Total | 955000 | 8000 | 33000 | 26000 | 921000 | 8000 | 31990 | 25000 |  |  |  | Total | 1651900 |  |  |  | Total | 13.2 | 13.2 | 0.3 | 0 | 13.8 | 13.5 | 0.4 | 0 | mg/L | 2.4026 | 1.617 | 0.023968 | 1.7896 |  |  |  |  | Raw.Trb. | 1.21 | Cmb.Trb. | 0.04
4 | Pres. | 139140000 | 1360360 | 3107240 | 5263430 | 210947000 | 1895440 | 5910560 | 10046900 | 1314000 | 36000 | 1350000 | now | 1120029300 |  | 0 | 1 | now | 1846.8 | 2847 | 31.1 | 41.1 | 1943 | 3013.4 | 52.4 | 6.6 | "/lb | 3 | 7.875 | 1.0625 | 9 | 11 | Raw | 21.4 | 7.92 | ef.turb.1 | 0.04 | ef.turb.2 | 0.06
| Prev | 138481000 | 1352360 | 3107240 | 5249430 | 210292000 | 1895440 | 5910560 | 10032900 |  |  |  | prev | 1118717300 |  |  |  | prev | 1837.7 | 2837.7 | 31 | 41.1 | 1933.5 | 3003.8 | 52.4 | 6.6 | Lbs. | 32.22 | 17.325 | 0.26562 | 20 |  | Trtd | 23 | 7.96 | AC.1 | 0.21 | AC.2 | 0.23
| Total | 659000 | 8000 | 0 | 14000 | 655000 | 0 | 0 | 14000 |  |  |  | Total | 1312000 |  |  |  | Total | 9.1 | 9.3 | 0.1 | 0 | 9.5 | 9.6 | 0 | 0 | mg/L | 2.9401 | 1.5809 | 0.024239 | 1.825 |  |  |  |  | Raw.Trb. | 1.24 | Cmb.Trb. | 0.04
5 | Pres. | 139962000 | 1360360 | 3139240 | 5289430 | 211746000 | 1903440 | 5914560 | 10060900 | 1621000 | 84000 | 1705000 | now | 1121442800 | 0 | 0 | 0.98 | now | 1858.2 | 2858.4 | 31.3 | 41.2 | 1954.7 | 3025.1 | 52.6 | 6.7 | "/lb | 4 | 11 | 1.75 | 11 | 14 | Raw | 20.1 | 7.82 | ef.turb.1 | 0.04 | ef.turb.2 | 0.05
| Prev | 139140000 | 1360360 | 3107240 | 5263430 | 210947000 | 1895440 | 5910560 | 10046900 |  |  |  | prev | 1120029300 |  |  |  | prev | 1846.8 | 2847 | 31.1 | 41.1 | 1943 | 3013.4 | 52.4 | 6.6 | Lbs. | 42.96 | 24.2 | 0.4375 | 25 |  | Trtd | 22.8 | 7.89 | AC.1 | 0.35 | AC.2 | 0.17
| Total | 822000 | 0 | 32000 | 26000 | 799000 | 8000 | 4000 | 14000 |  |  |  | Total | 1413500 |  |  |  | Total | 11.4 | 11.4 | 0.2 | 0.1 | 11.7 | 11.7 | 0.2 | 0.1 | mg/L | 3.1777 | 1.7901 | 0.032362 | 1.8492 |  |  |  |  | Raw.Trb. | 1.33 | Cmb.Trb. | 0.04
6 | Pres. | 140831000 | 1368360 | 3139240 | 5304430 | 212584000 | 1903440 | 5943560 | 10084900 | 1707000 | 76000 | 1783000 | now | 1123054000 |  | 0 | 0.95 | now | 1870.2 | 2870.4 | 31.3 | 41.3 | 1967.1 | 3037.4 | 52.7 | 6.7 | "/lb | 4.5 | 10.0625 | 2.25 | 13 | 12 | Raw | 19.3 | 7.61 | ef.turb.1 | 0.05 | ef.turb.2 | 0.05
| Prev | 139962000 | 1360360 | 3139240 | 5289430 | 211746000 | 1903440 | 5914560 | 10060900 |  |  |  | prev | 1121442800 |  |  |  | prev | 1858.2 | 2858.4 | 31.3 | 41.2 | 1954.7 | 3025.1 | 52.6 | 6.7 | Lbs. | 48.33 | 22.1375 | 0.5625 | 25 |  | Trtd | 22.6 | 7.88 | AC.1 | 0.2 | AC.2 | 0.13
| Total | 869000 | 8000 | 0 | 15000 | 838000 | 0 | 29000 | 24000 |  |  |  | Total | 1611200 |  |  |  | Total | 12 | 12 | 0 | 0.1 | 12.4 | 12.3 | 0.1 | 0 | mg/L | 3.3948 | 1.555 | 0.039511 | 1.7561 |  |  |  |  | Raw.Trb. | 1.35 | Cmb.Trb. | 0.05
7 | Pres. | 141692000 | 1376360 | 3172240 | 5330430 | 213414000 | 1911440 | 5974560 | 10109000 | 1691000 | 130100 | 1821100 | now | 1124530800 |  | 0 | 1.03 | now | 1882.2 | 2882.3 | 31.4 | 41.6 | 1979.6 | 3049.7 | 53 | 6.8 | "/lb | 5.0625 | 11.625 | 2.25 | 12 | 12 | Raw | 19.7 | 7.36 | ef.turb.1 | 0.04 | ef.turb.2 | 0.052
| Prev | 140831000 | 1368360 | 3139240 | 5304430 | 212584000 | 1903440 | 5943560 | 10084900 |  |  |  | prev | 1123054000 |  |  |  | prev | 1870.2 | 2870.4 | 31.3 | 41.3 | 1967.1 | 3037.4 | 52.7 | 6.7 | Lbs. | 54.3713 | 25.575 | 0.5625 | 24 |  | Trtd | 20.7 | 7.9 | AC.1 | 0.255 | AC.2 | 0.234
| Total | 861000 | 8000 | 33000 | 26000 | 830000 | 8000 | 31000 | 24100 |  |  |  | Total | 1476800 |  |  |  | Total | 12 | 11.9 | 0.1 | 0.3 | 12.5 | 12.3 | 0.3 | 0.1 | mg/L | 3.8553 | 1.8135 | 0.039885 | 1.7018 |  |  |  |  | Raw.Trb. | 1.41 | Cmb.Trb. | 0.039
8 | Pres. | 142496000 | 1376360 | 3204230 | 5363420 | 214201000 | 1919440 | 5974560 | 10133000 | 1591000 | 96980 | 1687980 | now | 1126029100 |  | 0 | 0.99 | now | 1893.3 | 2893.6 | 31.5 | 41.6 | 1991.2 | 3061.4 | 53.2 | 6.8 | "/lb | 4.9688 | 11.0625 | 2.25 | 12 | 11 | Raw | 19.2 | 7.5 | ef.turb.1 | 0.042 | ef.turb.2 | 0.065
| Prev | 141692000 | 1376360 | 3172240 | 5330430 | 213414000 | 1911440 | 5974560 | 10109000 |  |  |  | prev | 1124530800 |  |  |  | prev | 1882.2 | 2882.3 | 31.4 | 41.6 | 1979.6 | 3049.7 | 53 | 6.8 | Lbs. | 53.3644 | 24.3375 | 0.5625 | 23 |  | Trtd | 20.4 | 7.93 | AC.1 | 0.374 | AC.2 | 0.192
| Total | 804000 | 0 | 31990 | 32990 | 787000 | 8000 | 0 | 24000 |  |  |  | Total | 1498300 |  |  |  | Total | 11.1 | 11.3 | 0.1 | 0 | 11.6 | 11.7 | 0.2 | 0 | mg/L | 4.0218 | 1.8342 | 0.042392 | 1.7334 |  |  |  |  | Raw.Trb. | 1.37 | Cmb.Trb. | 0.052
9 | Pres. | 143417000 | 1384370 | 3204230 | 5385420 | 215063000 | 1927440 | 6006560 | 10164000 | 1783000 | 101010 | 1884010 | now | 1127650000 |  | 0 | 1.04 | now | 1906 | 2905.9 | 31.8 | 41.7 | 2004.4 | 3074.3 | 53.4 | 6.8 | "/lb | 5.5 | 11.875 | 2.875 | 12 | 12 | Raw | 17.9 | 7.52 | ef.turb.1 | 0.049 | ef.turb.2 | 0.052
| Prev | 142496000 | 1376360 | 3204230 | 5363420 | 214201000 | 1919440 | 5974560 | 10133000 |  |  |  | prev | 1126029100 |  |  |  | prev | 1893.3 | 2893.6 | 31.5 | 41.6 | 1991.2 | 3061.4 | 53.2 | 6.8 | Lbs. | 59.07 | 26.125 | 0.71875 | 24 |  | Trtd | 19.5 | 7.81 | AC.1 | 0.218 | AC.2 | 0.262
| Total | 921000 | 8010 | 0 | 22000 | 862000 | 8000 | 32000 | 31000 |  |  |  | Total | 1620900 |  |  |  | Total | 12.7 | 12.3 | 0.3 | 0.1 | 13.2 | 12.9 | 0.2 | 0 | mg/L | 3.9724 | 1.7569 | 0.048335 | 1.614 |  |  |  |  | Raw.Trb. | 1.17 | Cmb.Trb. | 0.041
10 | Pres. | 144269000 | 1393370 | 3237230 | 5411420 | 215915000 | 1935440 | 6006560 | 10178000 | 1704000 | 90000 | 1794000 | now | 1129076900 |  | 0 | 0.99 | now | 1917.8 | 2918 | 31.8 | 41.9 | 2016.5 | 3086.8 | 53.5 | 6.9 | "/lb | 5.25 | 11.5 | 2.25 | 12 | 11 | Raw | 19.2 | 7.58 | ef.turb.1 | 0.041 | ef.turb.2 | 0.061
| Prev | 143417000 | 1384370 | 3204230 | 5385420 | 215063000 | 1927440 | 6006560 | 10164000 |  |  |  | prev | 1127650000 |  |  |  | prev | 1906 | 2905.9 | 31.8 | 41.7 | 2004.4 | 3074.3 | 53.4 | 6.8 | Lbs. | 56.385 | 25.3 | 0.5625 | 23 |  | Trtd | 19 | 7.8 | AC.1 | 0.242 | AC.2 | 0.208
| Total | 852000 | 9000 | 33000 | 26000 | 852000 | 8000 | 0 | 14000 |  |  |  | Total | 1426900 |  |  |  | Total | 11.8 | 12.1 | 0 | 0.2 | 12.1 | 12.5 | 0.1 | 0.1 | mg/L | 3.9676 | 1.7803 | 0.039581 | 1.6184 |  |  |  |  | Raw.Trb. | 1.27 | Cmb.Trb. | 0.046
11 | Pres. | 144889000 | 1393370 | 3237230 | 5433420 | 216505000 | 1943440 | 6006560 | 10199000 | 1210000 | 51000 | 1261000 | now | 1130476100 |  | 0 | 1.02 | now | 1926.4 | 2926.4 | 31.9 | 41.9 | 2025.5 | 3095.7 | 53.5 | 6.9 | "/lb | 4 | 8.25 | 1.625 | 8 | 8 | Raw | 19.5 | 7.59 | ef.turb.1 | 0.044 | ef.turb.2 | 0.054
| Prev | 144269000 | 1393370 | 3237230 | 5411420 | 215915000 | 1935440 | 6006560 | 10178000 |  |  |  | prev | 1129076900 |  |  |  | prev | 1917.8 | 2918 | 31.8 | 41.9 | 2016.5 | 3086.8 | 53.5 | 6.9 | Lbs. | 42.96 | 18.15 | 0.40625 | 16 |  | Trtd | 20.6 | 7.85 | AC.1 | 0.329 | AC.2 | 0.231
| Total | 620000 | 0 | 0 | 22000 | 590000 | 8000 | 0 | 21000 |  |  |  | Total | 1399200 |  |  |  | Total | 8.6 | 8.4 | 0.1 | 0 | 9 | 8.9 | 0 | 0 | mg/L | 4.2571 | 1.7986 | 0.040257 | 1.5855 |  |  |  |  | Raw.Trb. | 1.3 | Cmb.Trb. | 0.041
12 | Pres. | 145803000 | 1401370 | 3269230 | 5459420 | 217398000 | 1943440 | 6039560 | 10224000 | 1807000 | 124000 | 1931000 | now | 1132005600 |  | 0 | 1.02 | now | 1939.1 | 2939.2 | 32 | 42.1 | 2038.8 | 3108.8 | 53.9 | 6.9 | "/lb | 5.5625 | 12.25 | 2.5 | 13 | 13 | Raw | 20 | 7.63 | ef.turb.1 | 0.044 | ef.turb.2 | 0.05
| Prev | 144889000 | 1393370 | 3237230 | 5433420 | 216505000 | 1943440 | 6006560 | 10199000 |  |  |  | prev | 1130476100 |  |  |  | prev | 1926.4 | 2926.4 | 31.9 | 41.9 | 2025.5 | 3095.7 | 53.5 | 6.9 | Lbs. | 59.7413 | 26.95 | 0.625 | 26 |  | Trtd | 21.3 | 7.9 | AC.1 | 0.22 | AC.2 | 0.39
| Total | 914000 | 8000 | 32000 | 26000 | 893000 | 0 | 33000 | 25000 |  |  |  | Total | 1529500 |  |  |  | Total | 12.7 | 12.8 | 0.1 | 0.2 | 13.3 | 13.1 | 0.4 | 0 | mg/L | 3.9642 | 1.7883 | 0.041472 | 1.7252 |  |  |  |  | Raw.Trb. | 1.31 | Cmb.Trb. | 0.038
13 | Pres. | 146581000 | 1409370 | 3269230 | 5474420 | 218166000 | 1951440 | 6039560 | 10238000 | 1546000 | 45000 | 1591000 | now | 1133565300 |  | 0 | 1.02 | now | 1949.9 | 2950.1 | 32 | 42.3 | 2049.9 | 3120 | 53.9 | 6.9 | "/lb | 4.875 | 10 | 2 | 11 | 10 | Raw | 19.6 | 7.43 | ef.turb.1 | 0.041 | ef.turb.2 | 0.055
| Prev | 145803000 | 1401370 | 3269230 | 5459420 | 217398000 | 1943440 | 6039560 | 10224000 |  |  |  | prev | 1132005600 |  |  |  | prev | 1939.1 | 2939.2 | 32 | 42.1 | 2038.8 | 3108.8 | 53.9 | 6.9 | Lbs. | 52.3575 | 22 | 0.5 | 21 |  | Trtd | 21.1 | 7.9 | AC.1 | 0.279 | AC.2 | 0.217
| Total | 778000 | 8000 | 0 | 15000 | 768000 | 8000 | 0 | 14000 |  |  |  | Total | 1559700 |  |  |  | Total | 10.8 | 10.9 | 0 | 0.2 | 11.1 | 11.2 | 0 | 0 | mg/L | 4.0607 | 1.7063 | 0.038779 | 1.6287 |  |  |  |  | Raw.Trb. | 1.27 | Cmb.Trb. | 0.04
14 | Pres. | 147431000 | 1409370 | 3301230 | 5498410 | 218972000 | 1959450 | 6070550 | 10261000 | 1656000 | 117990 | 1773990 | now | 1135109900 |  | 0 | 0.99 | now | 1961.7 | 2961.6 | 32.1 | 42.4 | 2062.1 | 3131.9 | 54.2 | 7 | "/lb | 5.4375 | 11.375 | 2.25 | 12 | 11 | Raw | 19.6 | 7.44 | ef.turb.1 | 0.04 | ef.turb.2 | 0.056
| Prev | 146581000 | 1409370 | 3269230 | 5474420 | 218166000 | 1951440 | 6039560 | 10238000 |  |  |  | prev | 1133565300 |  |  |  | prev | 1949.9 | 2950.1 | 32 | 42.3 | 2049.9 | 3120 | 53.9 | 6.9 | Lbs. | 58.3987 | 25.025 | 0.5625 | 23 |  | Trtd | 21.2 | 7.79 | AC.1 | 0.446 | AC.2 | 0.232
| Total | 850000 | 0 | 32000 | 23990 | 806000 | 8010 | 30990 | 23000 |  |  |  | Total | 1544600 |  |  |  | Total | 11.8 | 11.5 | 0.1 | 0.1 | 12.2 | 11.9 | 0.3 | 0.1 | mg/L | 4.2284 | 1.812 | 0.040728 | 1.6653 |  |  |  |  | Raw.Trb. | 1.36 | Cmb.Trb. | 0.038
15 | Pres. | 148238000 | 1417370 | 3301230 | 5520410 | 219726000 | 1967450 | 6102550 | 10291000 | 1561000 | 100000 | 1661000 | now | 1136439246 |  | 0 | 0.89 | now | 1972.9 | 2972.6 | 32.3 | 42.6 | 2073.8 | 3143.3 | 54.4 | 7 | "/lb | 5.5 | 10.5 | 2.125 | 13 | 13 | Raw | 19.5 | 7.54 | ef.turb.1 | 0.043 | ef.turb.2 | 0.055
| Prev | 147431000 | 1409370 | 3301230 | 5498410 | 218972000 | 1959450 | 6070550 | 10261000 |  |  |  | prev | 1135109900 |  |  |  | prev | 1961.7 | 2961.6 | 32.1 | 42.4 | 2062.1 | 3131.9 | 54.2 | 7 | Lbs. | 59.07 | 23.1 | 0.53125 | 26 |  | Trtd | 21.1 | 7.72 | AC.1 | 0.237 | AC.2 | 0.396
| Total | 807000 | 8000 | 0 | 22000 | 754000 | 8000 | 32000 | 30000 |  |  |  | Total | 1329346 |  |  |  | Total | 11.2 | 11 | 0.2 | 0.2 | 11.7 | 11.4 | 0.2 | 0 | mg/L | 4.5373 | 1.7744 | 0.040807 | 1.9971 |  |  |  |  | Raw.Trb. | 1.17 | Cmb.Trb. | 0.041
16 | Pres. | 148906000 | 1417370 | 3334220 | 5553410 | 220402000 | 1967450 | 6102550 | 10313000 | 1344000 | 87990 | 1431990 | now | 1137851600 |  | 0 | 0.86 | now | 1982.1 | 2982.1 | 32.3 | 42.6 | 2083.5 | 3153.2 | 54.5 | 7.1 | "/lb | 4.5 | 9 | 1.5 | 12 | 12 | Raw | 18.6 | 7.59 | ef.turb.1 | 0.039 | ef.turb.2 | 0.056
| Prev | 148238000 | 1417370 | 3301230 | 5520410 | 219726000 | 1967450 | 6102550 | 10291000 |  |  |  | prev | 1136439246 |  |  |  | prev | 1972.9 | 2972.6 | 32.3 | 42.6 | 2073.8 | 3143.3 | 54.4 | 7 | Lbs. | 48.33 | 19.8 | 0.375 | 24 |  | Trtd | 20.4 | 7.88 | AC.1 | 0.261 | AC.2 | 0.337
| Total | 668000 | 0 | 32990 | 33000 | 676000 | 0 | 0 | 22000 |  |  |  | Total | 1412354 |  |  |  | Total | 9.2 | 9.5 | 0 | 0 | 9.7 | 9.9 | 0.1 | 0.1 | mg/L | 4.3117 | 1.7664 | 0.033455 | 2.1411 |  |  |  |  | Raw.Trb. | 1.27 | Cmb.Trb. | 0.04
17 | Pres. | 149690000 | 1425370 | 3334220 | 5567410 | 221150000 | 1975450 | 6135550 | 10336000 | 1532000 | 86000 | 1618000 | now | 1139101800 |  | 0 | 0.85 | now | 1993 | 2992.6 | 32.4 | 42.9 | 2094.7 | 3164.1 | 54.7 | 7.1 | "/lb | 5 | 9.875 | 2.125 | 16 | 15 | Raw | 18.8 | 7.55 | ef.turb.1 | 0.05 | ef.turb.2 | 0.06
| Prev | 148906000 | 1417370 | 3334220 | 5553410 | 220402000 | 1967450 | 6102550 | 10313000 |  |  |  | prev | 1137851600 |  |  |  | prev | 1982.1 | 2982.1 | 32.3 | 42.6 | 2083.5 | 3153.2 | 54.5 | 7.1 | Lbs. | 53.7 | 21.725 | 0.53125 | 31 |  | Trtd | 21.7 | 7.9 | AC.1 | 0.22 | AC.2 | 0.23
| Total | 784000 | 8000 | 0 | 14000 | 748000 | 8000 | 33000 | 23000 |  |  |  | Total | 1250200 |  |  |  | Total | 10.9 | 10.5 | 0.1 | 0.3 | 11.2 | 10.9 | 0.2 | 0 | mg/L | 4.2029 | 1.7003 | 0.041579 | 2.4263 |  |  |  |  | Raw.Trb. | 1.29 | Cmb.Trb. | 0.04
18 | Pres. | 150229000 | 1425370 | 3334220 | 5582410 | 221689000 | 1975450 | 6135550 | 10351000 | 1078000 | 30000 | 1108000 | now | 1140271200 |  | 0 | 1.05 | now | 2000.5 | 3000.1 | 32.4 | 42.9 | 2102.5 | 3171.8 | 54.7 | 7.1 | "/lb | 3.625 | 7.5 | 1.375 | 10 | 10 | Raw | 19 | 7.48 | ef.turb.1 | 0.04 | ef.turb.2 | 0.06
| Prev | 149690000 | 1425370 | 3334220 | 5567410 | 221150000 | 1975450 | 6135550 | 10336000 |  |  |  | prev | 1139101800 |  |  |  | prev | 1993 | 2992.6 | 32.4 | 42.9 | 2094.7 | 3164.1 | 54.7 | 7.1 | Lbs. | 38.9325 | 16.5 | 0.34375 | 20 |  | Trtd | 21.8 | 7.85 | AC.1 | 0.27 | AC.2 | 0.29
| Total | 539000 | 0 | 0 | 15000 | 539000 | 0 | 0 | 15000 |  |  |  | Total | 1169400 |  |  |  | Total | 7.5 | 7.5 | 0 | 0 | 7.8 | 7.7 | 0 | 0 | mg/L | 4.3304 | 1.8353 | 0.038235 | 2.2246 |  |  |  |  | Raw.Trb. | 1.4 | Cmb.Trb. | 0.05
19 | Pres. | 151039000 | 1433370 | 3366220 | 5614410 | 222523000 | 1983450 | 6135550 | 10372100 | 1644000 | 101100 | 1745100 | now | 1141573200 |  | 0 | 1.07 | now | 2011.8 | 3011.7 | 32.6 | 42.9 | 2114.3 | 3184 | 54.9 | 7.1 | "/lb | 5.4375 | 11.25 | 2.25 | 12 | 12 | Raw | 19.1 | 7.53 | ef.turb.1 | 0.04 | ef.turb.2 | 0.06
| Prev | 150229000 | 1425370 | 3334220 | 5582410 | 221689000 | 1975450 | 6135550 | 10351000 |  |  |  | prev | 1140271200 |  |  |  | prev | 2000.5 | 3000.1 | 32.4 | 42.9 | 2102.5 | 3171.8 | 54.7 | 7.1 | Lbs. | 58.3987 | 24.75 | 0.5625 | 24 |  | Trtd | 22 | 7.82 | AC.1 | 0.2 | AC.2 | 0.22
| Total | 810000 | 8000 | 32000 | 32000 | 834000 | 8000 | 0 | 21100 |  |  |  | Total | 1302000 |  |  |  | Total | 11.3 | 11.6 | 0.2 | 0 | 11.8 | 12.2 | 0.2 | 0 | mg/L | 4.2593 | 1.8051 | 0.041026 | 1.7504 |  |  |  |  | Raw.Trb. | 1.44 | Cmb.Trb. | 0.04
20 | Pres. | 151748000 | 1441370 | 3366220 | 5665400 | 223304000 | 1991450 | 6167550 | 10433100 | 1490000 | 159990 | 1649990 | now | 1142877400 |  | 0 | 0.95 | now | 2021.5 | 3022.7 | 32.7 | 43.2 | 2125.1 | 3195.9 | 55 | 7.1 | "/lb | 5.6875 | 9.75 | 2.0625 | 12 | 11 | Raw | 19.4 | 7.44 | ef.turb.1 | 0.044 | ef.turb.2 | 0.058
| Prev | 151039000 | 1433370 | 3366220 | 5614410 | 222523000 | 1983450 | 6135550 | 10372100 |  |  |  | prev | 1141573200 |  |  |  | prev | 2011.8 | 3011.7 | 32.6 | 42.9 | 2114.3 | 3184 | 54.9 | 7.1 | Lbs. | 61.0838 | 21.45 | 0.51562 | 23 |  | Trtd | 20.4 | 7.76 | AC.1 | 0.246 | AC.2 | 0.287
| Total | 709000 | 8000 | 0 | 50990 | 781000 | 8000 | 32000 | 61000 |  |  |  | Total | 1304200 |  |  |  | Total | 9.7 | 11 | 0.1 | 0.3 | 10.8 | 11.9 | 0.1 | 0 | mg/L | 4.9156 | 1.7261 | 0.041494 | 1.8509 |  |  |  |  | Raw.Trb. | 1.38 | Cmb.Trb. | 0.041
21 | Pres. | 152421000 | 1441370 | 3398220 | 5697400 | 224000000 | 1991450 | 6167550 | 10454100 | 1369000 | 85000 | 1454000 | now | 1144188500 |  | 0 | 0.98 | now | 2031 | 3032.3 | 32.7 | 43.2 | 2134.9 | 3205.9 | 55.2 | 7.1 | "/lb | 4.625 | 9.375 | 1.875 | 11 | 12 | Raw | 19 | 7.49 | ef.turb.1 | 0.042 | ef.turb.2 | 0.058
| Prev | 151748000 | 1441370 | 3366220 | 5665400 | 223304000 | 1991450 | 6167550 | 10433100 |  |  |  | prev | 1142877400 |  |  |  | prev | 2021.5 | 3022.7 | 32.7 | 43.2 | 2125.1 | 3195.9 | 55 | 7.1 | Lbs. | 49.6725 | 20.625 | 0.46875 | 23 |  | Trtd | 20 | 7.81 | AC.1 | 0.353 | AC.2 | 0.37
| Total | 673000 | 0 | 32000 | 32000 | 696000 | 0 | 0 | 21000 |  |  |  | Total | 1311100 |  |  |  | Total | 9.5 | 9.6 | 0 | 0 | 9.8 | 10 | 0.2 | 0 | mg/L | 4.3506 | 1.8064 | 0.041056 | 2.0145 |  |  |  |  | Raw.Trb. | 1.46 | Cmb.Trb. | 0.041
22 | Pres. | 153136000 | 1449370 | 3398220 | 5726400 | 224684000 | 1999540 | 6200540 | 10493100 | 1399000 | 117080 | 1516080 | now | 1145508600 |  | 0 | 1.01 | now | 2041 | 3042.3 | 33 | 43.3 | 2145.5 | 3216.4 | 55.4 | 7.2 | "/lb | 4.375 | 10.25 | 1.875 | 11 | 10 | Raw | 18.9 | 7.38 | ef.turb.1 | 0.044 | ef.turb.2 | 0.055
| Prev | 152421000 | 1441370 | 3398220 | 5697400 | 224000000 | 1991450 | 6167550 | 10454100 |  |  |  | prev | 1144188500 |  |  |  | prev | 2031 | 3032.3 | 32.7 | 43.2 | 2134.9 | 3205.9 | 55.2 | 7.1 | Lbs. | 46.9875 | 22.55 | 0.46875 | 21 |  | Trtd | 19.4 | 7.74 | AC.1 | 0.259 | AC.2 | 0.264
| Total | 715000 | 8000 | 0 | 29000 | 684000 | 8090 | 32990 | 39000 |  |  |  | Total | 1320100 |  |  |  | Total | 10 | 10 | 0.3 | 0.1 | 10.6 | 10.5 | 0.2 | 0.1 | mg/L | 4.0272 | 1.9327 | 0.040175 | 1.7998 |  |  |  |  | Raw.Trb. | 1.44 | Cmb.Trb. | 0.052
23 | Pres. | 153861000 | 1449370 | 3430220 | 5758390 | 225433000 | 1999540 | 6200540 | 10515100 | 1474000 | 85990 | 1559990 | now | 1146815300 |  | 0 | 1.07 | now | 2050.9 | 3052.7 | 33 | 43.3 | 2156.1 | 3227.2 | 55.5 | 7.2 | "/lb | 3.875 | 10 | 2.375 | 11 | 11 | Raw | 18 | 7.46 | ef.turb.1 | 0.041 | ef.turb.2 | 0.057
| Prev | 153136000 | 1449370 | 3398220 | 5726400 | 224684000 | 1999540 | 6200540 | 10493100 |  |  |  | prev | 1145508600 |  |  |  | prev | 2041 | 3042.3 | 33 | 43.3 | 2145.5 | 3216.4 | 55.4 | 7.2 | Lbs. | 41.6175 | 22 | 0.59375 | 22 |  | Trtd | 19.7 | 7.85 | AC.1 | 0.327 | AC.2 | 0.342
| Total | 725000 | 0 | 32000 | 31990 | 749000 | 0 | 0 | 22000 |  |  |  | Total | 1306700 |  |  |  | Total | 9.9 | 10.4 | 0 | 0 | 10.6 | 10.8 | 0.1 | 0 | mg/L | 3.3854 | 1.7896 | 0.048299 | 1.7896 |  |  |  |  | Raw.Trb. | 1.25 | Cmb.Trb. | 0.041
24 | Pres. | 154370000 | 1457370 | 3430220 | 5787390 | 225906000 | 2007450 | 6232540 | 10553100 | 982000 | 114910 | 1096910 | now | 1147918300 |  | 0 | 1.03 | now | 2058.1 | 3059.3 | 33.3 | 43.3 | 2163.7 | 3234.4 | 55.7 | 7.2 | "/lb | 2.375 | 7 | 1.5 | 8 | 3 | Raw | 18.6 | 7.53 | ef.turb.1 | 0.045 | ef.turb.2 | 0.054
| Prev | 153861000 | 1449370 | 3430220 | 5758390 | 225433000 | 1999540 | 6200540 | 10515100 |  |  |  | prev | 1146815300 |  |  |  | prev | 2050.9 | 3052.7 | 33 | 43.3 | 2156.1 | 3227.2 | 55.5 | 7.2 | Lbs. | 25.5075 | 15.4 | 0.375 | 11 |  | Trtd | 20.1 | 7.73 | AC.1 | 0.239 | AC.2 | 0.26
| Total | 509000 | 8000 | 0 | 29000 | 473000 | 7910 | 32000 | 38000 |  |  |  | Total | 1103000 |  |  |  | Total | 7.2 | 6.6 | 0.3 | 0 | 7.6 | 7.2 | 0.2 | 0 | mg/L | 3.1145 | 1.8804 | 0.045788 | 1.3431 |  |  |  |  | Raw.Trb. | 1.27 | Cmb.Trb. | 0.039
25 | Pres. | 155150000 | 1457370 | 3430220 | 5809390 | 226687000 | 2007450 | 6232540 | 10575100 | 1561000 | 44000 | 1605000 | now | 1149400400 |  | 0 | 0.8 | now | 2069 | 3070.2 | 33.3 | 43.3 | 2174.9 | 3245.6 | 55.7 | 7.2 | "/lb | 3.25 | 10.25 | 2 | 14 | 14 | Raw | 19.7 | 7.31 | ef.turb.1 | 0.042 | ef.turb.2 | 0.052
| Prev | 154370000 | 1457370 | 3430220 | 5787390 | 225906000 | 2007450 | 6232540 | 10553100 |  |  |  | prev | 1147918300 |  |  |  | prev | 2058.1 | 3059.3 | 33.3 | 43.3 | 2163.7 | 3234.4 | 55.7 | 7.2 | Lbs. | 34.905 | 22.55 | 0.5 | 28 |  | Trtd | 20.3 | 7.75 | AC.1 | 0.316 | AC.2 | 0.333
| Total | 780000 | 0 | 0 | 22000 | 781000 | 0 | 0 | 22000 |  |  |  | Total | 1482100 |  |  |  | Total | 10.9 | 10.9 | 0 | 0 | 11.2 | 11.2 | 0 | 0 | mg/L | 2.6811 | 1.7321 | 0.038406 | 2.1507 |  |  |  |  | Raw.Trb. | 1.35 | Cmb.Trb. | 0.045
26 | Pres. | 155886000 | 1465370 | 3463210 | 5841390 | 227587000 | 2015450 | 6265540 | 10599100 | 1636000 | 137990 | 1773990 | now | 1150733706 |  | 0 | 1.13 | now | 2079.2 | 3082.9 | 33.3 | 43.6 | 2185.7 | 3258.7 | 56.1 | 7.3 | "/lb | 2.94 | 10.25 | 2.75 | 13 | 11 | Raw | 20 | 7.37 | ef.turb.1 | 0.04 | ef.turb.2 | 0.06
| Prev | 155150000 | 1457370 | 3430220 | 5809390 | 226687000 | 2007450 | 6232540 | 10575100 |  |  |  | prev | 1149400400 |  |  |  | prev | 2069 | 3070.2 | 33.3 | 43.3 | 2174.9 | 3245.6 | 55.7 | 7.2 | Lbs. | 31.5756 | 22.55 | 0.6875 | 24 |  | Trtd | 21.1 | 7.78 | AC.1 | 0.21 | AC.2 | 0.21
| Total | 736000 | 8000 | 32990 | 32000 | 900000 | 8000 | 33000 | 24000 |  |  |  | Total | 1333306 |  |  |  | Total | 10.2 | 12.7 | 0 | 0.3 | 10.8 | 13.1 | 0.4 | 0.1 | mg/L | 2.3142 | 1.6527 | 0.050388 | 1.759 |  |  |  |  | Raw.Trb. | 1.31 | Cmb.Trb. | 0.04
27 | Pres. | 156438000 | 1473370 | 3495210 | 5866390 | 228177000 | 2015450 | 6265540 | 10613200 | 1142000 | 79100 | 1221100 | now | 1151970100 |  | 0 | 1.15 | now | 2086.9 | 3091.2 | 33.5 | 43.6 | 2194 | 3267.1 | 56.2 | 7.4 | "/lb | 3 | 8.9375 | 2.125 | 9 | 10 | Raw | 20.1 | 7.44 | ef.turb.1 | 0.044 | ef.turb.2 | 0.059
| Prev | 155886000 | 1465370 | 3463210 | 5841390 | 227587000 | 2015450 | 6265540 | 10599100 |  |  |  | prev | 1150733706 |  |  |  | prev | 2079.2 | 3082.9 | 33.3 | 43.6 | 2185.7 | 3258.7 | 56.1 | 7.3 | Lbs. | 32.22 | 19.6625 | 0.53125 | 19 |  | Trtd | 21.4 | 7.86 | AC.1 | 0.303 | AC.2 | 0.267
| Total | 552000 | 8000 | 32000 | 25000 | 590000 | 0 | 0 | 14100 |  |  |  | Total | 1236394 |  |  |  | Total | 7.7 | 8.3 | 0.2 | 0 | 8.3 | 8.4 | 0.1 | 0.1 | mg/L | 3.3829 | 2.0645 | 0.055778 | 1.9949 |  |  |  |  | Raw.Trb. | 1.31 | Cmb.Trb. | 0.041
28 | Pres. | 157173000 | 1473370 | 3495210 | 5881390 | 228867000 | 2023450 | 6297540 | 10632200 | 1425000 | 74000 | 1499000 | now | 1153303900 |  | 0 | 1.03 | now | 2097.1 | 3100.8 | 33.6 | 43.7 | 2204.4 | 3277.2 | 56.4 | 7.4 | "/lb | 2.25 | 9.25 | 2.375 | 10 | 11 | Raw | 19.8 | 7.47 | ef.turb.1 | 0.054 | ef.turb.2 | 0.059
| Prev | 156438000 | 1473370 | 3495210 | 5866390 | 228177000 | 2015450 | 6265540 | 10613200 |  |  |  | prev | 1151970100 |  |  |  | prev | 2086.9 | 3091.2 | 33.5 | 43.6 | 2194 | 3267.1 | 56.2 | 7.4 | Lbs. | 24.165 | 20.35 | 0.59375 | 21 |  | Trtd | 21.4 | 7.69 | AC.1 | 0.468 | AC.2 | 0.24
| Total | 735000 | 0 | 0 | 15000 | 690000 | 8000 | 32000 | 19000 |  |  |  | Total | 1333800 |  |  |  | Total | 10.2 | 9.6 | 0.1 | 0.1 | 10.4 | 10.1 | 0.2 | 0 | mg/L | 2.0333 | 1.7123 | 0.04996 | 1.767 |  |  |  |  | Raw.Trb. | 1.34 | Cmb.Trb. | 0.044
29 | Pres. | 157994000 | 1481370 | 3495210 | 5908380 | 229696000 | 2030450 | 6297540 | 10653200 | 1650000 | 62990 | 1712990 | now | 1154657600 |  | 0 | 0.99 | now | 2108.5 | 3112.3 | 33.6 | 43.9 | 2216.4 | 3289.2 | 56.4 | 7.4 | "/lb | 3.0625 | 11.25 | 2.875 | 13 | 13 | Raw | 20.2 | 7.37 | ef.turb.1 | 0.044 | ef.turb.2 | 0.065
| Prev | 157173000 | 1473370 | 3495210 | 5881390 | 228867000 | 2023450 | 6297540 | 10632200 |  |  |  | prev | 1153303900 |  |  |  | prev | 2097.1 | 3100.8 | 33.6 | 43.7 | 2204.4 | 3277.2 | 56.4 | 7.4 | Lbs. | 32.8912 | 24.75 | 0.71875 | 26 |  | Trtd | 21.4 | 7.86 | AC.1 | 0.264 | AC.2 | 0.278
| Total | 821000 | 8000 | 0 | 26990 | 829000 | 7000 | 0 | 21000 |  |  |  | Total | 1353700 |  |  |  | Total | 11.4 | 11.5 | 0 | 0.2 | 12 | 12 | 0 | 0 | mg/L | 2.3902 | 1.7986 | 0.052231 | 1.8894 |  |  |  |  | Raw.Trb. | 1.39 | Cmb.Trb. | 0.047
30 | Pres. | 158735000 | 1481370 | 3528210 | 5936380 | 230428000 | 2030450 | 6329530 | 10681200 | 1473000 | 120990 | 1593990 | now | 1156084500 |  | 0 | 1 | now | 2118.8 | 3122.6 | 33.7 | 44 | 2227.2 | 3299.9 | 56.7 | 7.4 | "/lb | 4.75 | 10 | 2.875 | 11 | 12 | Raw | 21 | 7.47 | ef.turb.1 | 0.043 | ef.turb.2 | 0.061
| Prev | 157994000 | 1481370 | 3495210 | 5908380 | 229696000 | 2030450 | 6297540 | 10653200 |  |  |  | prev | 1154657600 |  |  |  | prev | 2108.5 | 3112.3 | 33.6 | 43.9 | 2216.4 | 3289.2 | 56.4 | 7.4 | Lbs. | 51.015 | 22 | 0.71875 | 23 |  | Trtd | 22.5 | 7.88 | AC.1 | 0.359 | AC.2 | 0.503
| Total | 741000 | 0 | 33000 | 28000 | 732000 | 0 | 31990 | 28000 |  |  |  | Total | 1426900 |  |  |  | Total | 10.3 | 10.3 | 0.1 | 0.1 | 10.8 | 10.7 | 0.3 | 0 | mg/L | 4.1527 | 1.7908 | 0.058507 | 1.8722 |  |  |  |  | Raw.Trb. | 1.35 | Cmb.Trb. | 0.047
31 | Pres. | 159239000 | 1489370 | 3528210 | 5964380 | 230956000 | 2030450 | 6329530 | 10696200 | 1032000 | 51000 | 1083000 | now | 1157278700 |  | 0 | 0.97 | now | 2125.8 | 3129.9 | 33.8 | 44 | 2234.7 | 3307.4 | 56.7 | 7.4 | "/lb | 3.125 | 7 | 1.75 | 8 | 8 | Raw | 21.5 | 7.52 | ef.turb.1 | 0.06 | ef.turb.2 | 0.06
| Prev | 158735000 | 1481370 | 3528210 | 5936380 | 230428000 | 2030450 | 6329530 | 10681200 |  |  |  | prev | 1156084500 |  |  |  | prev | 2118.8 | 3122.6 | 33.7 | 44 | 2227.2 | 3299.9 | 56.7 | 7.4 | Lbs. | 33.5625 | 15.4 | 0.4375 | 16 |  | Trtd | 23.2 | 7.79 | AC.1 | 0.23 | AC.2 | 0.28
| Total | 504000 | 8000 | 0 | 28000 | 528000 | 0 | 0 | 15000 |  |  |  | Total | 1194200 |  |  |  | Total | 7 | 7.3 | 0.1 | 0 | 7.5 | 7.5 | 0 | 0 | mg/L | 3.8995 | 1.7893 | 0.050831 | 1.859 |  |  |  |  | Raw.Trb. | 1.14 | Cmb.Trb. | 0.05
[10 empty] | Totals | [6 empty] | AVG | [10 empty] | totals | [5 empty] | AVG TRTD |  |  |  | Avg.Cmb.Trb.
[10 empty] | 46578000 | 2781190 | 49359190 |  | 43267900 |  | 0 | 0.99226 | [5 empty] | 338.8 | 340.9 |  |  |  | 1388.5075 | 687.0875 | 15.6875 | 708 |  |  | 21.2065 | 7.8316 |  |  | 0.04271
[22 empty] | total- | 679.7

## Aug, 2021
August, 2021
Filters | [15 empty] | Rain | Cl2 | Pump Hours | [8 empty] | Chemicals | [5 empty] | Misc. |  |  | Turbidity |  |  |  | Meters
Day |  | CW.Tot.1 | Cla.Wst.1 | BW.Wst.1 | FTWst.1 | CW.Tot.2 | Cla.Wst.2 | BW.Wst.2 | FTWst.2 | Treated Total | Wastewater | Total Influent | Totalizer |  |  | Inches | Resid | Pump | Ef.Pmp.1 | Ef.Pmp.2 | Blo.1 | Blo.2 | URT.1 | URT.2 | BWP | SWP | Chem | ACH | SA | Poly | Cl2.1 | Cl2.2 | water | Temp | pH | F1 |  | F2 |  |  | RM1 | RM2 | BWM
1 | Pres. | 160025000 | 1489370 | 3561210 | 5984380 | 231752000 | 2038440 | 6329530 | 10706200 | 1582000 | 70990 | 1652990 | now | 1158417500 |  | 0 | 0.9 | now | 2136.8 | 3141 | 33.9 | 44 | 2245.9 | 3318.7 | 56.9 | 7.5 | "/lb | 4.5 | 10.25 | 2.375 | 11 | 11 | Raw | 20.3 | 7.47 | ef.turb.1 | 0.05 | ef.turb.2 | 0.08 | Pres. | 457777000 | 259436200 | 170750000
| Prev | 159239000 | 1489370 | 3528210 | 5964380 | 230956000 | 2030450 | 6329530 | 10696200 |  |  |  | prev | 1157278700 |  |  |  | prev | 2125.8 | 3129.9 | 33.8 | 44 | 2234.7 | 3307.4 | 56.7 | 7.4 | Lbs. | 48.33 | 22.55 | 0.59375 | 22 |  | Trtd | 23.4 | 7.81 | AC.1 | 0.3 | AC.2 | 0.19 | Prev. | 457189000 | 258856700 | 170750000
| Total | 786000 | 0 | 33000 | 20000 | 796000 | 7990 | 0 | 10000 |  |  |  | Total | 1138800 |  |  |  | Total | 11 | 11.1 | 0.1 | 0 | 11.2 | 11.3 | 0.2 | 0.1 | mg/L | 3.6631 | 1.7091 | 0.045002 | 1.6674 |  |  |  |  | Raw.Trb. | 1.13 | Cmb.Trb. | 0.05 | Total | 588000 | 579500 | 0
2 | Pres. | 160602000 | 1497370 | 3561210 | 5999380 | 232305000 | 2038440 | 6361530 | 10731200 | 1130000 | 80000 | 1210000 | now | 1159690500 |  | 0 | 1.04 | now | 2144.8 | 3148.8 | 34.1 | 44 | 2254.3 | 3326.8 | 57.1 | 7.5 | "/lb | 4.125 | 8.9375 | 2.125 | 9 | 10 | Raw | 20.8 | 7.52 | ef.turb.1 | 0.049 | ef.turb.2 | 0.06 | Pres. | 458649000 | 260300400 | 170786000
| Prev | 160025000 | 1489370 | 3561210 | 5984380 | 231752000 | 2038440 | 6329530 | 10706200 |  |  |  | prev | 1158417500 |  |  |  | prev | 2136.8 | 3141 | 33.9 | 44 | 2245.9 | 3318.7 | 56.9 | 7.5 | Lbs. | 44.3025 | 19.6625 | 0.53125 | 19 |  | Trtd | 23.2 | 7.77 | AC.1 | 0.2208 | AC.2 | 0.2 | Prev. | 457777000 | 259436200 | 170750000
| Total | 577000 | 8000 | 0 | 15000 | 553000 | 0 | 32000 | 25000 |  |  |  | Total | 1273000 |  |  |  | Total | 8 | 7.8 | 0.2 | 0 | 8.4 | 8.1 | 0.2 | 0 | mg/L | 4.7009 | 2.0864 | 0.056371 | 2.0161 |  |  |  |  | Raw.Trb. | 1.21 | Cmb.Trb. | 0.04 | Total | 872000 | 864200 | 36000
10.6
3 | Pres. | 161411000 | 1505370 | 3593200 | 6037370 | 233154000 | 2046440 | 6361530 | 10752200 | 1658000 | 106980 | 1764980 | now | 1160995900 |  | 0 | 0.89 | now | 2156.2 | 3160.6 | 34.1 | 44.3 | 2266.4 | 3339.1 | 57.2 | 7.5 | "/lb | 5.5 | 10.9375 | 2.875 | 13 | 13 | Raw | 20.9 | 7.45 | ef.turb.1 | 0.046 | ef.turb.2 | 0.065 | Pres. | 459293000 | 260911900 | 170821000
| Prev | 160602000 | 1497370 | 3561210 | 5999380 | 232305000 | 2038440 | 6361530 | 10731200 |  |  |  | prev | 1159690500 |  |  |  | prev | 2144.8 | 3148.8 | 34.1 | 44 | 2254.3 | 3326.8 | 57.1 | 7.5 | Lbs. | 59.07 | 24.0625 | 0.71875 | 26 |  | Trtd | 22.6 | 7.87 | AC.1 | 0.268 | AC.2 | 0.234 | Prev. | 458649000 | 260300400 | 170786000
| Total | 809000 | 8000 | 31990 | 37990 | 849000 | 8000 | 0 | 21000 |  |  |  | Total | 1305400 |  |  |  | Total | 11.4 | 11.8 | 0 | 0.3 | 12.1 | 12.3 | 0.1 | 0 | mg/L | 4.2719 | 1.7402 | 0.051979 | 1.8803 |  |  |  |  | Raw.Trb. | 1.2 | Cmb.Trb. | 0.047 | Total | 644000 | 611500 | 35000
4 | Pres. | 161982000 | 1505370 | 3593200 | 6066370 | 233687000 | 2046440 | 6393530 | 10791200 | 1104000 | 100000 | 1204000 | now | 1162269900 |  | 0 | 1.01 | now | 2164.2 | 3168.1 | 34.2 | 44.3 | 2274.7 | 3347.1 | 57.4 | 7.5 | "/lb | 3.5 | 7.25 | 2 | 9 | 8 | Raw | 20.5 | 7.48 | ef.turb.1 | 0.063 | ef.turb.2 | 0.062 | Pres. | 460219000 | 261836500 | 170857000
| Prev | 161411000 | 1505370 | 3593200 | 6037370 | 233154000 | 2046440 | 6361530 | 10752200 |  |  |  | prev | 1160995900 |  |  |  | prev | 2156.2 | 3160.6 | 34.1 | 44.3 | 2266.4 | 3339.1 | 57.2 | 7.5 | Lbs. | 37.59 | 15.95 | 0.5 | 17 |  | Trtd | 21.8 | 7.85 | AC.1 | 0.5 | AC.2 | 0.34 | Prev. | 459293000 | 260911900 | 170821000
| Total | 571000 | 0 | 0 | 29000 | 533000 | 0 | 32000 | 39000 |  |  |  | Total | 1274000 |  |  |  | Total | 8 | 7.5 | 0.1 | 0 | 8.3 | 8 | 0.2 | 0 | mg/L | 4.0826 | 1.7323 | 0.054304 | 1.8463 |  |  |  |  | Raw.Trb. | 1.2 | Cmb.Trb. | 0.048 | Total | 926000 | 924600 | 36000
5 | Pres. | 162767000 | 1513370 | 3593200 | 6081370 | 234477000 | 2054440 | 6393530 | 10806200 | 1575000 | 46000 | 1621000 | now | 1163509500 | 0 | 0 | 0.95 | now | 2175.1 | 3179.2 | 34.4 | 44.3 | 2286.1 | 3358.4 | 57.4 | 7.5 | "/lb | 4.5 | 10.9375 | 2.625 | 12 | 13 | Raw | 20.7 | 7.44 | ef.turb.1 | 0.047 | ef.turb.2 | 0.078 | Pres. | 460871000 | 262450300 | 170892000
| Prev | 161982000 | 1505370 | 3593200 | 6066370 | 233687000 | 2046440 | 6393530 | 10791200 |  |  |  | prev | 1162269900 |  |  |  | prev | 2164.2 | 3168.1 | 34.2 | 44.3 | 2274.7 | 3347.1 | 57.4 | 7.5 | Lbs. | 48.33 | 24.0625 | 0.65625 | 25 |  | Trtd | 22.8 | 7.75 | AC.1 | 0.245 | AC.2 | 0.175 | Prev. | 460219000 | 261836500 | 170857000
| Total | 785000 | 8000 | 0 | 15000 | 790000 | 8000 | 0 | 15000 |  |  |  | Total | 1239600 |  |  |  | Total | 10.9 | 11.1 | 0.2 | 0 | 11.4 | 11.3 | 0 | 0 | mg/L | 3.6793 | 1.8319 | 0.04996 | 1.9032 |  |  |  |  | Raw.Trb. | 1.16 | Cmb.Trb. | 0.054 | Total | 652000 | 613800 | 35000
6 | Pres. | 163448000 | 1513370 | 3626200 | 6105370 | 235175000 | 2054440 | 6393530 | 10820200 | 1379000 | 71000 | 1450000 | now | 1164735700 |  | 0 | 1.03 | now | 2184.5 | 3188.9 | 34.4 | 44.3 | 2295.8 | 3368.3 | 57.6 | 7.6 | "/lb | 4 | 9.5 | 2.875 | 11 | 10 | Raw | 20.4 | 7.49 | ef.turb.1 | 0.047 | ef.turb.2 | 0.061 | Pres. | 461747000 | 263311700 | 170892000
| Prev | 162767000 | 1513370 | 3593200 | 6081370 | 234477000 | 2054440 | 6393530 | 10806200 |  |  |  | prev | 1163509500 |  |  |  | prev | 2175.1 | 3179.2 | 34.4 | 44.3 | 2286.1 | 3358.4 | 57.4 | 7.5 | Lbs. | 42.96 | 20.9 | 0.71875 | 21 |  | Trtd | 22 | 7.7 | AC.1 | 0.427 | AC.2 | 0.264 | Prev. | 460871000 | 262450300 | 170892000
| Total | 681000 | 0 | 33000 | 24000 | 698000 | 0 | 0 | 14000 |  |  |  | Total | 1226200 |  |  |  | Total | 9.4 | 9.7 | 0 | 0 | 9.7 | 9.9 | 0.2 | 0.1 | mg/L | 3.7354 | 1.8173 | 0.062495 | 1.826 |  |  |  |  | Raw.Trb. | 1.21 | Cmb.Trb. | 0.043 | Total | 876000 | 861400 | 0
7 | Pres. | 164071000 | 1522370 | 3626200 | 6120370 | 235772000 | 2062440 | 6425530 | 10844200 | 1220000 | 88000 | 1308000 | now | 1165944300 |  | 0 | 1 | now | 2193.3 | 3197.3 | 34.6 | 44.5 | 2304.9 | 3377.1 | 57.7 | 7.6 | "/lb | 3.5 | 9.25 | 2 | 10 | 9 | Raw | 20.7 | 7.51 | ef.turb.1 | 0.046 | ef.turb.2 | 0.06 | Pres. | 463206000 | 264735000 | 170962000
| Prev | 163448000 | 1513370 | 3626200 | 6105370 | 235175000 | 2054440 | 6393530 | 10820200 |  |  |  | prev | 1164735700 |  |  |  | prev | 2184.5 | 3188.9 | 34.4 | 44.3 | 2295.8 | 3368.3 | 57.6 | 7.6 | Lbs. | 37.59 | 20.35 | 0.5 | 19 |  | Trtd | 21.9 | 7.75 | AC.1 | 0.215 | AC.2 | 0.167 | Prev. | 461747000 | 263311700 | 170892000
| Total | 623000 | 9000 | 0 | 15000 | 597000 | 8000 | 32000 | 24000 |  |  |  | Total | 1208600 |  |  |  | Total | 8.8 | 8.4 | 0.2 | 0.2 | 9.1 | 8.8 | 0.1 | 0 | mg/L | 3.6944 | 2 | 0.049141 | 1.8674 |  |  |  |  | Raw.Trb. | 1.19 | Cmb.Trb. | 0.046 | Total | 1459000 | 1423300 | 70000
8 | Pres. | 164655000 | 1522370 | 3658200 | 6145370 | 236379000 | 2062440 | 6425530 | 10859300 | 1191000 | 72100 | 1263100 | now | 1167085500 |  | 0 | 1.02 | now | 2201.6 | 3205.9 | 34.6 | 44.5 | 2313.6 | 3386.1 | 57.9 | 7.7 | "/lb | 3.5 | 8.25 | 2 | 9 | 10 | Raw | 19.6 | 7.55 | ef.turb.1 | 0.044 | ef.turb.2 | 0.062 | Pres. | 463870000 | 265401520 | 170998000
| Prev | 164071000 | 1522370 | 3626200 | 6120370 | 235772000 | 2062440 | 6425530 | 10844200 |  |  |  | prev | 1165944300 |  |  |  | prev | 2193.3 | 3197.3 | 34.6 | 44.5 | 2304.9 | 3377.1 | 57.7 | 7.6 | Lbs. | 37.59 | 18.15 | 0.5 | 19 |  | Trtd | 21.7 | 7.87 | AC.1 | 0.358 | AC.2 | 0.257 | Prev. | 463206000 | 264735000 | 170962000
| Total | 584000 | 0 | 32000 | 25000 | 607000 | 0 | 0 | 15100 |  |  |  | Total | 1141200 |  |  |  | Total | 8.3 | 8.6 | 0 | 0 | 8.7 | 9 | 0.2 | 0.1 | mg/L | 3.7844 | 1.8273 | 0.050338 | 1.9128 |  |  |  |  | Raw.Trb. | 1.15 | Cmb.Trb. | 0.043 | Total | 664000 | 666520 | 36000
9 | Pres. | 165255000 | 1530370 | 3658200 | 6159370 | 236960000 | 2070440 | 6457530 | 10874300 | 1181000 | 77000 | 1258000 | now | 1168365700 |  | 0 | 0.96 | now | 2209.8 | 3213.8 | 34.7 | 44.8 | 2322.2 | 3394.3 | 58.1 | 7.7 | "/lb | 3 | 6.25 | 1.9375 | 9 | 9 | Raw | 18.7 | 7.63 | ef.turb.1 | 0.05 | ef.turb.2 | 0.06 | Pres. | 464544000 | 266034700 | 171033000
| Prev | 164655000 | 1522370 | 3658200 | 6145370 | 236379000 | 2062440 | 6425530 | 10859300 |  |  |  | prev | 1167085500 |  |  |  | prev | 2201.6 | 3205.9 | 34.6 | 44.5 | 2313.6 | 3386.1 | 57.9 | 7.7 | Lbs. | 32.22 | 13.75 | 0.48438 | 18 |  | Trtd | 21.7 | 7.88 | AC.1 | 0.24 | AC.2 | 0.19 | Prev. | 463870000 | 265401520 | 170998000
| Total | 600000 | 8000 | 0 | 14000 | 581000 | 8000 | 32000 | 15000 |  |  |  | Total | 1280200 |  |  |  | Total | 8.2 | 7.9 | 0.1 | 0.3 | 8.6 | 8.2 | 0.2 | 0 | mg/L | 3.2712 | 1.396 | 0.049177 | 1.8275 |  |  |  |  | Raw.Trb. | 1.2 | Cmb.Trb. | 0.04 | Total | 674000 | 633180 | 35000
10 | Pres. | 165952000 | 1530370 | 3658200 | 6181360 | 237708000 | 2070440 | 6457530 | 10897300 | 1445000 | 44990 | 1489990 | now | 1169740900 |  | 0 | 0.87 | now | 2219.5 | 3224.2 | 34.7 | 44.8 | 2332.2 | 3405 | 58.1 | 7.7 | "/lb | 3.75 | 10 | 2.375 | 11 | 12 | Raw | 19 | 7.41 | ef.turb.1 | 0.044 | ef.turb.2 | 0.069 | Pres. | 465316000 | 266851100 | 171033000
| Prev | 165255000 | 1530370 | 3658200 | 6159370 | 236960000 | 2070440 | 6457530 | 10874300 |  |  |  | prev | 1168365700 |  |  |  | prev | 2209.8 | 3213.8 | 34.7 | 44.8 | 2322.2 | 3394.3 | 58.1 | 7.7 | Lbs. | 40.275 | 22 | 0.59375 | 23 |  | Trtd | 20.9 | 7.79 | AC.1 | 0.343 | AC.2 | 0.329 | Prev. | 464544000 | 266034700 | 171033000
| Total | 697000 | 0 | 0 | 21990 | 748000 | 0 | 0 | 23000 |  |  |  | Total | 1375200 |  |  |  | Total | 9.7 | 10.4 | 0 | 0 | 10 | 10.7 | 0 | 0 | mg/L | 3.342 | 1.8255 | 0.049269 | 1.9085 |  |  |  |  | Raw.Trb. | 1.09 | Cmb.Trb. | 0.04 | Total | 772000 | 816400 | 0
11 | Pres. | 166723000 | 1537370 | 3691200 | 6206360 | 238507000 | 2078440 | 6457530 | 10912300 | 1570000 | 88000 | 1658000 | now | 1171182900 |  | 0 | 0.91 | now | 2230.2 | 3235.3 | 34.9 | 44.8 | 2343.4 | 3416.4 | 58.2 | 7.7 | "/lb | 4.0625 | 10.75 | 2.625 | 13 | 13 | Raw | 19.9 | 7.45 | ef.turb.1 | 0.043 | ef.turb.2 | 0.063 | Pres. | 466185000 | 267717700 | 171068000
| Prev | 165952000 | 1530370 | 3658200 | 6181360 | 237708000 | 2070440 | 6457530 | 10897300 |  |  |  | prev | 1169740900 |  |  |  | prev | 2219.5 | 3224.2 | 34.7 | 44.8 | 2332.2 | 3405 | 58.1 | 7.7 | Lbs. | 43.6313 | 23.65 | 0.65625 | 26 |  | Trtd | 21 | 7.81 | AC.1 | 0.193 | AC.2 | 0.166 | Prev. | 465316000 | 266851100 | 171033000
| Total | 771000 | 7000 | 33000 | 25000 | 799000 | 8000 | 0 | 15000 |  |  |  | Total | 1442000 |  |  |  | Total | 10.7 | 11.1 | 0.2 | 0 | 11.2 | 11.4 | 0.1 | 0 | mg/L | 3.3322 | 1.8062 | 0.050119 | 1.9857 |  |  |  |  | Raw.Trb. | 1.21 | Cmb.Trb. | 0.042 | Total | 869000 | 866600 | 35000
12 | Pres. | 167621000 | 1537370 | 3691200 | 6220360 | 239365000 | 2078440 | 6489520 | 10936300 | 1756000 | 69990 | 1825990 | now | 1172594900 |  | 0 | 0.95 | now | 2242.7 | 3247.4 | 35 | 44.9 | 2356.2 | 3428.2 | 58.4 | 7.7 | "/lb | 4.875 | 11.875 | 2.9375 | 14 | 14 | Raw | 21.7 | 7.44 | ef.turb.1 | 0.047 | ef.turb.2 | 0.062 | Pres. | 467161000 | 268656300 | 171103000
| Prev | 166723000 | 1537370 | 3691200 | 6206360 | 238507000 | 2078440 | 6457530 | 10912300 |  |  |  | prev | 1171182900 |  |  |  | prev | 2230.2 | 3235.3 | 34.9 | 44.8 | 2343.4 | 3416.4 | 58.2 | 7.7 | Lbs. | 52.3575 | 26.125 | 0.73438 | 28 |  | Trtd | 23.1 | 7.82 | AC.1 | 0.217 | AC.2 | 0.231 | Prev. | 466185000 | 267717700 | 171068000
| Total | 898000 | 0 | 0 | 14000 | 858000 | 0 | 31990 | 24000 |  |  |  | Total | 1412000 |  |  |  | Total | 12.5 | 12.1 | 0.1 | 0.1 | 12.8 | 11.8 | 0.2 | 0 | mg/L | 3.5751 | 1.7839 | 0.050145 | 1.9119 |  |  |  |  | Raw.Trb. | 1.23 | Cmb.Trb. | 0.042 | Total | 976000 | 938600 | 35000
13 | Pres. | 168378000 | 1546370 | 3723200 | 6257360 | 240144000 | 2086440 | 6489520 | 10961300 | 1536000 | 111000 | 1647000 | now | 1174025900 |  | 0 | 0.91 | now | 2253.3 | 3258.2 | 35 | 45.1 | 2367.4 | 3440.1 | 58.6 | 7.8 | "/lb | 5 | 10.5 | 3.5 | 12 | 13 | Raw | 22.1 | 7.52 | ef.turb.1 | 0.046 | ef.turb.2 | 0.064 | Pres. | 468032000 | 269521888 | 171138000
| Prev | 167621000 | 1537370 | 3691200 | 6220360 | 239365000 | 2078440 | 6489520 | 10936300 |  |  |  | prev | 1172594900 |  |  |  | prev | 2242.7 | 3247.4 | 35 | 44.9 | 2356.2 | 3428.2 | 58.4 | 7.7 | Lbs. | 53.7 | 23.1 | 0.875 | 25 |  | Trtd | 23.9 | 7.8 | AC.1 | 0.184 | AC.2 | 0.175 | Prev. | 467161000 | 268656300 | 171103000
| Total | 757000 | 9000 | 32000 | 37000 | 779000 | 8000 | 0 | 25000 |  |  |  | Total | 1431000 |  |  |  | Total | 10.6 | 10.8 | 0 | 0.2 | 11.2 | 11.9 | 0.2 | 0.1 | mg/L | 4.192 | 1.8032 | 0.068305 | 1.9516 |  |  |  |  | Raw.Trb. | 1.19 | Cmb.Trb. | 0.048 | Total | 871000 | 865588 | 35000
14 | Pres. | 168965000 | 1546370 | 3723200 | 6276360 | 240704000 | 2086440 | 6522520 | 10988300 | 1147000 | 79000 | 1226000 | now | 1175224400 |  | 0 | 0.94 | now | 2261.5 | 3266.1 | 35 | 45.2 | 2375.9 | 3448.3 | 58.7 | 7.8 | "/lb | 3.375 | 7.75 | 2 | 10 | 10 | Raw | 21.8 | 7.72 | ef.turb.1 | 0.05 | ef.turb.2 | 0.06 | Pres. | 468687000 | 270143968 | 171174000
| Prev | 168378000 | 1546370 | 3723200 | 6257360 | 240144000 | 2086440 | 6489520 | 10961300 |  |  |  | prev | 1174025900 |  |  |  | prev | 2253.3 | 3258.2 | 35 | 45.1 | 2367.4 | 3440.1 | 58.6 | 7.8 | Lbs. | 36.2475 | 17.05 | 0.5 | 20 |  | Trtd | 24.6 | 7.86 | AC.1 | 0.23 | AC.2 | 0.2 | Prev. | 468032000 | 269521888 | 171138000
| Total | 587000 | 0 | 0 | 19000 | 560000 | 0 | 33000 | 27000 |  |  |  | Total | 1198500 |  |  |  | Total | 8.2 | 7.9 | 0 | 0.1 | 8.5 | 8.2 | 0.1 | 0 | mg/L | 3.7892 | 1.7824 | 0.052269 | 2.0907 |  |  |  |  | Raw.Trb. | 1.06 | Cmb.Trb. | 0.04 | Total | 655000 | 622080 | 36000
15 | Pres. | 169539000 | 1554370 | 3756190 | 6301360 | 241301000 | 2094440 | 6522520 | 11002300 | 1171000 | 87990 | 1258990 | now | 1176339400 |  | 0 | 1.01 | now | 2269.5 | 3274.4 | 35.3 | 45.2 | 2384.4 | 3457 | 58.9 | 7.8 | "/lb | 3.5 | 7.875 | 2 | 10 | 9 | Raw | 22.4 | 7.95 | ef.turb.1 | 0.05 | ef.turb.2 | 0.06 | Pres. | 469344000 | 270800300 | 171209000
| Prev | 168965000 | 1546370 | 3723200 | 6276360 | 240704000 | 2086440 | 6522520 | 10988300 |  |  |  | prev | 1175224400 |  |  |  | prev | 2261.5 | 3266.1 | 35 | 45.2 | 2375.9 | 3448.3 | 58.7 | 7.8 | Lbs. | 37.59 | 17.325 | 0.5 | 19 |  | Trtd | 24.8 | 7.91 | AC.1 | 0.16 | AC.2 | 0.17 | Prev. | 468687000 | 270143968 | 171174000
| Total | 574000 | 8000 | 32990 | 25000 | 597000 | 8000 | 0 | 14000 |  |  |  | Total | 1115000 |  |  |  | Total | 8 | 8.3 | 0.3 | 0 | 8.5 | 8.7 | 0.2 | 0 | mg/L | 3.849 | 1.774 | 0.051197 | 1.9455 |  |  |  |  | Raw.Trb. | 1.01 | Cmb.Trb. | 0.04 | Total | 657000 | 656332 | 35000
16 | Pres. | 170232000 | 1554370 | 3756190 | 6316350 | 241960000 | 2094440 | 6554520 | 11026300 | 1352000 | 70990 | 1422990 | now | 1177578700 |  | 0 | 0.96 | now | 2279.1 | 3283.8 | 35.3 | 45.2 | 2394.2 | 3466.5 | 59.1 | 7.8 | "/lb | 3.75 | 9.25 | 2.25 | 11 | 12 | Raw | 21.5 | 7.66 | ef.turb.1 | 0.05 | ef.turb.2 | 0.06 | Pres. | 470111000 | 271525300 | 171244000
| Prev | 169539000 | 1554370 | 3756190 | 6301360 | 241301000 | 2094440 | 6522520 | 11002300 |  |  |  | prev | 1176339400 |  |  |  | prev | 2269.5 | 3274.4 | 35.3 | 45.2 | 2384.4 | 3457 | 58.9 | 7.8 | Lbs. | 40.275 | 20.35 | 0.5625 | 23 |  | Trtd | 24.6 | 7.93 | AC.1 | 0.23 | AC.2 | 0.23 | Prev. | 469344000 | 270800300 | 171209000
| Total | 693000 | 0 | 0 | 14990 | 659000 | 0 | 32000 | 24000 |  |  |  | Total | 1239300 |  |  |  | Total | 9.6 | 9.4 | 0 | 0 | 9.8 | 9.5 | 0.2 | 0 | mg/L | 3.5718 | 1.8048 | 0.049886 | 2.0398 |  |  |  |  | Raw.Trb. | 1.1 | Cmb.Trb. | 0.04 | Total | 767000 | 725000 | 35000
17 | Pres. | 170914000 | 1562370 | 3756190 | 6330350 | 242642000 | 2102440 | 6554520 | 11040300 | 1364000 | 44000 | 1408000 | now | 1178739600 |  | 0 | 0.96 | now | 2288.6 | 3293.3 | 35.3 | 45.5 | 2404.1 | 3476.4 | 59.1 | 7.8 | "/lb | 3.75 | 9 | 2.25 | 11 | 11 | Raw | 19.9 | 7.6 | ef.turb.1 | 0.073 | ef.turb.2 | 0.076 | Pres. | 470878000 | 272272900 | 171244000
| Prev | 170232000 | 1554370 | 3756190 | 6316350 | 241960000 | 2094440 | 6554520 | 11026300 |  |  |  | prev | 1177578700 |  |  |  | prev | 2279.1 | 3283.8 | 35.3 | 45.2 | 2394.2 | 3466.5 | 59.1 | 7.8 | Lbs. | 40.275 | 19.8 | 0.5625 | 22 |  | Trtd | 22 | 7.8 | AC.1 | 0.167 | AC.2 | 0.19 | Prev. | 470111000 | 271525300 | 171244000
| Total | 682000 | 8000 | 0 | 14000 | 682000 | 8000 | 0 | 14000 |  |  |  | Total | 1160900 |  |  |  | Total | 9.5 | 9.5 | 0 | 0.3 | 9.9 | 9.9 | 0 | 0 | mg/L | 3.5404 | 1.7405 | 0.049447 | 1.9339 |  |  |  |  | Raw.Trb. | 1.11 | Cmb.Trb. | 0.052 | Total | 767000 | 747600 | 0
18 | Pres. | 171600000 | 1562370 | 3788190 | 6355350 | 243370000 | 2102440 | 6554520 | 11054300 | 1414000 | 71000 | 1485000 | now | 1179963400 |  | 0 | 1.02 | now | 2298.2 | 3303.4 | 35.3 | 45.5 | 2414.1 | 3486.8 | 59.2 | 7.9 | "/lb | 3.9375 | 9.9375 | 2.25 | 11 | 12 | Raw | 18 | 7.51 | ef.turb.1 | 0.043 | ef.turb.2 | 0.059 | Pres. | 471644000 | 273060700 | 171280000
| Prev | 170914000 | 1562370 | 3756190 | 6330350 | 242642000 | 2102440 | 6554520 | 11040300 |  |  |  | prev | 1178739600 |  |  |  | prev | 2288.6 | 3293.3 | 35.3 | 45.5 | 2404.1 | 3476.4 | 59.1 | 7.8 | Lbs. | 42.2888 | 21.8625 | 0.5625 | 23 |  | Trtd | 20.1 | 7.76 | AC.1 | 0.266 | AC.2 | 0.258 | Prev. | 470878000 | 272272900 | 171244000
| Total | 686000 | 0 | 32000 | 25000 | 728000 | 0 | 0 | 14000 |  |  |  | Total | 1223800 |  |  |  | Total | 9.6 | 10.1 | 0 | 0 | 10 | 10.4 | 0.1 | 0.1 | mg/L | 3.586 | 1.8539 | 0.047699 | 1.9503 |  |  |  |  | Raw.Trb. | 1.06 | Cmb.Trb. | 0.041 | Total | 766000 | 787800 | 36000
19 | Pres. | 172253000 | 1570370 | 3788190 | 6370350 | 243990000 | 2110440 | 6586520 | 11078300 | 1273000 | 87000 | 1360000 | now | 1181182000 |  | 0 | 1.05 | now | 2307.3 | 3312.1 | 35.5 | 45.6 | 2423.5 | 3495.9 | 59.4 | 7.9 | "/lb | 3.75 | 8.625 | 2.25 | 10 | 11 | Raw | 18.7 | 7.53 | ef.turb.1 | 0.045 | ef.turb.2 | 0.058 | Pres. | 472374000 | 273753000 | 171315000
| Prev | 171600000 | 1562370 | 3788190 | 6355350 | 243370000 | 2102440 | 6554520 | 11054300 |  |  |  | prev | 1179963400 |  |  |  | prev | 2298.2 | 3303.4 | 35.3 | 45.5 | 2414.1 | 3486.8 | 59.2 | 7.9 | Lbs. | 40.275 | 18.975 | 0.5625 | 21 |  | Trtd | 20.4 | 7.77 | AC.1 | 0.176 | AC.2 | 0.186 | Prev. | 471644000 | 273060700 | 171280000
| Total | 653000 | 8000 | 0 | 15000 | 620000 | 8000 | 32000 | 24000 |  |  |  | Total | 1218600 |  |  |  | Total | 9.1 | 8.7 | 0.2 | 0.1 | 9.4 | 9.1 | 0.2 | 0 | mg/L | 3.7935 | 1.7873 | 0.052982 | 1.978 |  |  |  |  | Raw.Trb. | 1.08 | Cmb.Trb. | 0.039 | Total | 730000 | 692300 | 35000
20 | Pres. | 172921000 | 1570370 | 3821190 | 6394350 | 244685000 | 2118440 | 6586520 | 11092300 | 1363000 | 79000 | 1442000 | now | 1182327700 |  | 0.02 | 1.06 | now | 2316.8 | 3321.7 | 35.6 | 45.6 | 2433.3 | 3505.9 | 59.6 | 8 | "/lb | 3.9375 | 9.25 | 2.25 | 11 | 11 | Raw | 19 | 7.5 | ef.turb.1 | 0.043 | ef.turb.2 | 0.06 | Pres. | 473116000 | 274511900 | 171350000
| Prev | 172253000 | 1570370 | 3788190 | 6370350 | 243990000 | 2110440 | 6586520 | 11078300 |  |  |  | prev | 1181182000 |  |  |  | prev | 2307.3 | 3312.1 | 35.5 | 45.6 | 2423.5 | 3495.9 | 59.4 | 7.9 | Lbs. | 42.2888 | 20.35 | 0.5625 | 22 |  | Trtd | 21.1 | 7.79 | AC.1 | 0.27 | AC.2 | 0.251 | Prev. | 472374000 | 273753000 | 171315000
| Total | 668000 | 0 | 33000 | 24000 | 695000 | 8000 | 0 | 14000 |  |  |  | Total | 1145700 |  |  |  | Total | 9.5 | 9.6 | 0.1 | 0 | 9.8 | 10 | 0.2 | 0.1 | mg/L | 3.7202 | 1.7902 | 0.049484 | 1.9354 |  |  |  |  | Raw.Trb. | 1.12 | Cmb.Trb. | 0.04 | Total | 742000 | 758900 | 35000
21 | Pres. | 173478000 | 1578370 | 3821190 | 6409350 | 245223000 | 2118440 | 6619510 | 11116400 | 1095000 | 80090 | 1175090 | now | 1183410000 |  | 0.01 | 1.09 | now | 2324.6 | 3329.3 | 35.8 | 45.7 | 2441.5 | 3513.8 | 59.8 | 8 | "/lb | 3 | 8.25 | 1.9375 | 9 | 9 | Raw | 19 | 7.56 | ef.turb.1 | 0.044 | ef.turb.2 | 0.058 | Pres. | 473745000 | 275104900 | 171386000
| Prev | 172921000 | 1570370 | 3821190 | 6394350 | 244685000 | 2118440 | 6586520 | 11092300 |  |  |  | prev | 1182327700 |  |  |  | prev | 2316.8 | 3321.7 | 35.6 | 45.6 | 2433.3 | 3505.9 | 59.6 | 8 | Lbs. | 32.22 | 18.15 | 0.48438 | 18 |  | Trtd | 20.6 | 7.87 | AC.1 | 0.17 | AC.2 | 0.226 | Prev. | 473116000 | 274511900 | 171350000
| Total | 557000 | 8000 | 0 | 15000 | 538000 | 0 | 32990 | 24100 |  |  |  | Total | 1082300 |  |  |  | Total | 7.8 | 7.6 | 0.2 | 0.1 | 8.2 | 7.9 | 0.2 | 0 | mg/L | 3.5281 | 1.9875 | 0.05304 | 1.971 |  |  |  |  | Raw.Trb. | 1.06 | Cmb.Trb. | 0.038 | Total | 629000 | 593000 | 36000
22 | Pres. | 173960000 | 1578370 | 3853190 | 6433350 | 245712000 | 2126440 | 6619510 | 11130400 | 971000 | 78000 | 1049000 | now | 1184471000 |  | 0 | 1.1 | now | 2331.3 | 3336.2 | 35.8 | 45.8 | 2448.6 | 3521 | 59.9 | 8 | "/lb | 3.25 | 6.5 | 1.625 | 7 | 7 | Raw | 18.9 | 7.45 | ef.turb.1 | 0.043 | ef.turb.2 | 0.078 | Pres. | 474293000 | 275646000 | 171421000
| Prev | 173478000 | 1578370 | 3821190 | 6409350 | 245223000 | 2118440 | 6619510 | 11116400 |  |  |  | prev | 1183410000 |  |  |  | prev | 2324.6 | 3329.3 | 35.8 | 45.7 | 2441.5 | 3513.8 | 59.8 | 8 | Lbs. | 34.905 | 14.3 | 0.40625 | 14 |  | Trtd | 20 | 7.89 | AC.1 | 0.32 | AC.2 | 0.214 | Prev. | 473745000 | 275104900 | 171386000
| Total | 482000 | 0 | 32000 | 24000 | 489000 | 8000 | 0 | 14000 |  |  |  | Total | 1061000 |  |  |  | Total | 6.7 | 6.9 | 0 | 0.1 | 7.1 | 7.2 | 0.1 | 0 | mg/L | 4.3102 | 1.7658 | 0.050166 | 1.7288 |  |  |  |  | Raw.Trb. | 1.14 | Cmb.Trb. | 0.048 | Total | 548000 | 541100 | 35000
23 | Pres. | 174542000 | 1586370 | 3853190 | 6448340 | 246330000 | 2126440 | 6619510 | 11145400 | 1200000 | 37990 | 1237990 | now | 1185608200 |  | 0 | 1.04 | now | 2339.6 | 3344.7 | 35.8 | 45.9 | 2457.3 | 3529.7 | 59.9 | 8 | "/lb | 3 | 8.25 | 2.125 | 10 | 10 | Raw | 16.7 | 7.64 | ef.turb.1 | 0.05 | ef.turb.2 | 0.06 | Pres. | 474954000 | 276317900 | 171421000
| Prev | 173960000 | 1578370 | 3853190 | 6433350 | 245712000 | 2126440 | 6619510 | 11130400 |  |  |  | prev | 1184471000 |  |  |  | prev | 2331.3 | 3336.2 | 35.8 | 45.8 | 2448.6 | 3521 | 59.9 | 8 | Lbs. | 32.22 | 18.15 | 0.53125 | 20 |  | Trtd | 19.2 | 8.06 | AC.1 | 0.2 | AC.2 | 0.28 | Prev. | 474293000 | 275646000 | 171421000
| Total | 582000 | 8000 | 0 | 14990 | 618000 | 0 | 0 | 15000 |  |  |  | Total | 1137200 |  |  |  | Total | 8.3 | 8.5 | 0 | 0.1 | 8.7 | 8.7 | 0 | 0 | mg/L | 3.2194 | 1.8135 | 0.053083 | 1.9984 |  |  |  |  | Raw.Trb. | 0.92 | Cmb.Trb. | 0.04 | Total | 661000 | 671900 | 0
24 | Pres. | 175056000 | 1586370 | 3853190 | 6462340 | 246931000 | 2134440 | 6650510 | 11161400 | 1115000 | 69000 | 1184000 | now | 1186803500 |  | 0 | 1.06 | now | 2346.7 | 3353.1 | 35.9 | 46.1 | 2464.7 | 3538.4 | 60.1 | 8 | "/lb | 2.75 | 7.625 | 1.9375 | 8 | 9 | Raw | 16.1 | 7.62 | ef.turb.1 | 0.044 | ef.turb.2 | 0.057 | Pres. | 475520000 | 276981400 | 171456000
| Prev | 174542000 | 1586370 | 3853190 | 6448340 | 246330000 | 2126440 | 6619510 | 11145400 |  |  |  | prev | 1185608200 |  |  |  | prev | 2339.6 | 3344.7 | 35.8 | 45.9 | 2457.3 | 3529.7 | 59.9 | 8 | Lbs. | 29.535 | 16.775 | 0.48438 | 17 |  | Trtd | 18.4 | 7.91 | AC.1 | 0.371 | AC.2 | 0.208 | Prev. | 474954000 | 276317900 | 171421000
| Total | 514000 | 0 | 0 | 14000 | 601000 | 8000 | 31000 | 16000 |  |  |  | Total | 1195300 |  |  |  | Total | 7.1 | 8.4 | 0.1 | 0.2 | 7.4 | 8.7 | 0.2 | 0 | mg/L | 3.1761 | 1.8039 | 0.052088 | 1.8281 |  |  |  |  | Raw.Trb. | 0.9 | Cmb.Trb. | 0.036 | Total | 566000 | 663500 | 35000
25 | Pres. | 175710000 | 1594380 | 3886180 | 6494340 | 247610000 | 2142440 | 6650510 | 11183400 | 1333000 | 103000 | 1436000 | now | 1187969300 |  | 0 | 0.91 | now | 2355.8 | 3362.6 | 36.1 | 46.1 | 2474.4 | 3548.3 | 60.3 | 8.1 | "/lb | 3 | 8.625 | 2 | 10 | 10 | Raw | 17.2 | 7.71 | ef.turb.1 | 0.043 | ef.turb.2 | 0.06 | Pres. | 476260000 | 277721300 | 171491000
| Prev | 175056000 | 1586370 | 3853190 | 6462340 | 246931000 | 2134440 | 6650510 | 11161400 |  |  |  | prev | 1186803500 |  |  |  | prev | 2346.7 | 3353.1 | 35.9 | 46.1 | 2464.7 | 3538.4 | 60.1 | 8 | Lbs. | 32.22 | 18.975 | 0.5 | 20 |  | Trtd | 18.7 | 7.82 | AC.1 | 0.227 | AC.2 | 0.21 | Prev. | 475520000 | 276981400 | 171456000
| Total | 654000 | 8010 | 32990 | 32000 | 679000 | 8000 | 0 | 22000 |  |  |  | Total | 1165800 |  |  |  | Total | 9.1 | 9.5 | 0.2 | 0 | 9.7 | 9.9 | 0.2 | 0.1 | mg/L | 2.8982 | 1.7068 | 0.044975 | 1.799 |  |  |  |  | Raw.Trb. | 0.9 | Cmb.Trb. | 0.038 | Total | 740000 | 739900 | 35000
26 | Pres. | 176261000 | 1594380 | 3886180 | 6516340 | 248257000 | 2142440 | 6682510 | 11207400 | 1198000 | 78000 | 1276000 | now | 1189047800 |  | 0 | 0.91 | now | 2363.6 | 3371.7 | 36.2 | 46.2 | 2482.4 | 3557.7 | 60.4 | 8.1 | "/lb | 3.1875 | 5.75 | 2 | 10 | 8 | Raw | 18.7 | 7.58 | ef.turb.1 | 0.04 | ef.turb.2 | 0.06 | Pres. | 476878000 | 278492000 | 171526000
| Prev | 175710000 | 1594380 | 3886180 | 6494340 | 247610000 | 2142440 | 6650510 | 11183400 |  |  |  | prev | 1187969300 |  |  |  | prev | 2355.8 | 3362.6 | 36.1 | 46.1 | 2474.4 | 3548.3 | 60.3 | 8.1 | Lbs. | 34.2338 | 12.65 | 0.5 | 18 |  | Trtd | 19.8 | 8.03 | AC.1 | 0.3 | AC.2 | 0.25 | Prev. | 476260000 | 277721300 | 171491000
| Total | 551000 | 0 | 0 | 22000 | 647000 | 0 | 32000 | 24000 |  |  |  | Total | 1078500 |  |  |  | Total | 7.8 | 9.1 | 0.1 | 0.1 | 8 | 9.4 | 0.1 | 0 | mg/L | 3.4263 | 1.2661 | 0.050043 | 1.8016 |  |  |  |  | Raw.Trb. | 1 | Cmb.Trb. | 0.04 | Total | 618000 | 770700 | 35000
27 | Pres. | 176736000 | 1602350 | 3886180 | 6531340 | 248736000 | 2151440 | 6682510 | 11221400 | 954000 | 45970 | 999970 | now | 1190147000 |  | 0 | 0.92 | now | 2370.2 | 3378.3 | 36.2 | 46.4 | 2489.4 | 3564.7 | 60.4 | 8.1 | "/lb | 2.125 | 4.5 | 1.625 | 8 | 7 | Raw | 18.5 | 7.62 | ef.turb.1 | 0.05 | ef.turb.2 | 0.07 | Pres. | 477435000 | 278975000 | 171526000
| Prev | 176261000 | 1594380 | 3886180 | 6516340 | 248257000 | 2142440 | 6682510 | 11207400 |  |  |  | prev | 1189047800 |  |  |  | prev | 2363.6 | 3371.7 | 36.2 | 46.2 | 2482.4 | 3557.7 | 60.4 | 8.1 | Lbs. | 22.8225 | 9.9 | 0.40625 | 15 |  | Trtd | 19.3 | 7.87 | AC.1 | 0.24 | AC.2 | 0.22 | Prev. | 476878000 | 278492000 | 171526000
| Total | 475000 | 7970 | 0 | 15000 | 479000 | 9000 | 0 | 14000 |  |  |  | Total | 1099200 |  |  |  | Total | 6.6 | 6.6 | 0 | 0.2 | 7 | 7 | 0 | 0 | mg/L | 2.8685 | 1.2443 | 0.05106 | 1.8853 |  |  |  |  | Raw.Trb. | 1 | Cmb.Trb. | 0.04 | Total | 557000 | 483000 | 0
28 | Pres. | 177895000 | 1602350 | 3918180 | 6561340 | 248757000 | 2151440 | 6682510 | 11223400 | 1180000 | 64000 | 1244000 | now | 1191220000 |  | 0 | 0.84 | now | 2384.6 | 3378.7 | 36.2 | 46.4 | 2504.1 | 3565 | 60.6 | 8.1 | "/lb | 3.125 | 4.75 | 1.75 | 12 | 5 | Raw | 18 | 7.6 | ef.turb.1 | 0.05 | ef.turb.2 | 0.06 | Pres. | 478714000 | 278998000 | 171561000
| Prev | 176736000 | 1602350 | 3886180 | 6531340 | 248736000 | 2151440 | 6682510 | 11221400 |  |  |  | prev | 1190147000 |  |  |  | prev | 2370.2 | 3378.3 | 36.2 | 46.4 | 2489.4 | 3564.7 | 60.4 | 8.1 | Lbs. | 33.5625 | 10.45 | 0.4375 | 17 |  | Trtd | 19.5 | 7.87 | AC.1 | 0.32 | AC.2 | 0.27 | Prev. | 477435000 | 278975000 | 171526000
| Total | 1159000 | 0 | 32000 | 30000 | 21000 | 0 | 0 | 2000 |  |  |  | Total | 1073000 |  |  |  | Total | 14.4 | 0.4 | 0 | 0 | 14.7 | 0.3 | 0.2 | 0 | mg/L | 3.4104 | 1.0619 | 0.044456 | 1.7274 |  |  |  |  | Raw.Trb. | 0.91 | Cmb.Trb. | 0.04 | Total | 1279000 | 23000 | 35000
29 | Pres. | 178567000 | 1610380 | 3918180 | 6576340 | 249358000 | 2151440 | 6682510 | 11238400 | 1273000 | 38030 | 1311030 | now | 1192244500 |  | 0 | 0.84 | now | 2393.9 | 3387.1 | 36.2 | 46.5 | 2513.8 | 3573.7 | 60.6 | 8.1 | "/lb | 3.25 | 5.75 | 2.125 | 10 | 12 | Raw | 18.7 | 7.7 | ef.turb.1 | 0.05 | ef.turb.2 | 0.06 | Pres. | 480128000 | 280283700 | 171632000
| Prev | 177895000 | 1602350 | 3918180 | 6561340 | 248757000 | 2151440 | 6682510 | 11223400 |  |  |  | prev | 1191220000 |  |  |  | prev | 2384.6 | 3378.7 | 36.2 | 46.4 | 2504.1 | 3565 | 60.6 | 8.1 | Lbs. | 34.905 | 12.65 | 0.53125 | 22 |  | Trtd | 20.1 | 7.93 | AC.1 | 0.21 | AC.2 | 0.31 | Prev. | 478714000 | 278998000 | 171561000
| Total | 672000 | 8030 | 0 | 15000 | 601000 | 0 | 0 | 15000 |  |  |  | Total | 1024500 |  |  |  | Total | 9.3 | 8.4 | 0 | 0.1 | 9.7 | 8.7 | 0 | 0 | mg/L | 3.2877 | 1.1915 | 0.050039 | 2.0722 |  |  |  |  | Raw.Trb. | 0.97 | Cmb.Trb. | 0.042 | Total | 1414000 | 1285700 | 71000
30 | Pres. | 179139000 | 1618386 | 3951180 | 6601330 | 249914000 | 2159440 | 6714510 | 11267400 | 1128000 | 134996 | 1262996 | now | 1193341500 |  | 0 | 0.98 | now | 2401.9 | 3395 | 36.2 | 46.8 | 2522.3 | 3582 | 60.9 | 8.2 | "/lb | 2.9375 | 5.25 | 2 | 9 | 9 | Raw | 17 | 7.56 | ef.turb.1 | 0.04 | ef.turb.2 | 0.06 | Pres. | 480722000 | 280844300 | 171667000
| Prev | 178567000 | 1610380 | 3918180 | 6576340 | 249358000 | 2151440 | 6682510 | 11238400 |  |  |  | prev | 1192244500 |  |  |  | prev | 2393.9 | 3387.1 | 36.2 | 46.5 | 2513.8 | 3573.7 | 60.6 | 8.1 | Lbs. | 31.5488 | 11.55 | 0.5 | 18 |  | Trtd | 19.9 | 7.71 | AC.1 | 0.25 | AC.2 | 0.21 | Prev. | 480128000 | 280283700 | 171632000
| Total | 572000 | 8006 | 33000 | 24990 | 556000 | 8000 | 32000 | 29000 |  |  |  | Total | 1097000 |  |  |  | Total | 8 | 7.9 | 0 | 0.3 | 8.5 | 8.3 | 0.3 | 0.1 | mg/L | 3.3536 | 1.2277 | 0.053149 | 1.9134 |  |  |  |  | Raw.Trb. | 0.99 | Cmb.Trb. | 0.034 | Total | 594000 | 560600 | 35000
31 | Pres. | 179683000 | 1618386 | 3951180 | 6615330 | 250421000 | 2159440 | 6747500 | 11292400 | 1051000 | 71990 | 1122990 | now | 1194418800 |  | 0 | 1.06 | now | 2409.4 | 3402.1 | 36.3 | 46.9 | 2530.1 | 3589.4 | 61.1 | 8.2 | "/lb | 2.5 | 5 | 1.875 | 9 | 8 | Raw | 17.4 | 7.33 | ef.turb.1 | 0.054 | ef.turb.2 | 0.068 | Pres.
| Prev | 179139000 | 1618386 | 3951180 | 6601330 | 249914000 | 2159440 | 6714510 | 11267400 |  |  |  | prev | 1193341500 |  |  |  | prev | 2401.9 | 3395 | 36.2 | 46.8 | 2522.3 | 3582 | 60.9 | 8.2 | Lbs. | 26.85 | 11 | 0.46875 | 17 |  | Trtd | 19 | 7.66 | AC.1 | 0.336 | AC.2 | 0.269 | Prev. | 480722000 | 280844300 | 171667000
| Total | 544000 | 0 | 0 | 14000 | 507000 | 0 | 32990 | 25000 |  |  |  | Total | 1077300 |  |  |  | Total | 7.5 | 7.1 | 0.1 | 0.1 | 7.8 | 7.4 | 0.2 | 0 | mg/L | 3.0632 | 1.2549 | 0.053478 | 1.9395 |  |  |  |  | Raw.Trb. | 0.98 | Cmb.Trb. | 0.046 | Total | -480722000 | -280844300 | -171667000
[10 empty] | Totals | [6 empty] | AVG | [10 empty] | totals | [5 empty] | AVG TRTD |  |  |  | Avg.Cmb.Trb.
[10 empty] | 39909000 | 2346096 | 42255096 |  | 37140100 |  | 0.03 | 0.97387 | [5 empty] | 295.4 | 282 |  |  |  | 1202.2088 | 564.575 | 17.125 | 634 |  |  | 21.3581 | 7.8358 |  |  | 0.042484
[22 empty] | total- | 577.4

## Sep, 2021
September, 2021
Filters | [15 empty] | Rain | Cl2 | Pump Hours | [8 empty] | Chemicals | [5 empty] | Misc. |  |  | Turbidity |  |  |  | Meters
Day |  | CW.Tot.1 | Cla.Wst.1 | BW.Wst.1 | FTWst.1 | CW.Tot.2 | Cla.Wst.2 | BW.Wst.2 | FTWst.2 | Treated Total | Wastewater | Total Influent | Totalizer |  |  | Inches | Resid | Pump | Ef.Pmp.1 | Ef.Pmp.2 | Blo.1 | Blo.2 | URT.1 | URT.2 | BWP | SWP | Chem | ACH | SA | Poly | Cl2.1 | Cl2.2 | water | Temp | pH | F1 |  | F2 |  |  | RM1 | RM2 | BWM
1 | Pres. | 180314000 | 1626380 | 3951180 | 6630330 | 251043000 | 2167440 | 6747500 | 11307400 | 1253000 | 45994 | 1298994 | now | 1195547600 |  | 0 | 1.06 | now | 2418.2 | 3410.9 | 36.3 | 47.1 | 2539.2 | 3598.6 | 61.1 | 8.2 | "/lb | 3 | 5.9375 | 2.125 | 9 | 9 | Raw | 17.5 | 7.4 | ef.turb.1 | 0.045 | ef.turb.2 | 0.081 | Pres. | 481417000 | 281540000 | 171667000
| Prev | 179683000 | 1618386 | 3951180 | 6615330 | 250421000 | 2159440 | 6747500 | 11292400 |  |  |  | prev | 1194418800 |  |  |  | prev | 2409.4 | 3402.1 | 36.3 | 46.9 | 2530.1 | 3589.4 | 61.1 | 8.2 | Lbs. | 32.22 | 13.0625 | 0.53125 | 18 |  | Trtd | 18.9 | 7.61 | AC.1 | 0.252 | AC.2 | 0.205 | Prev. | 480722000 | 280844300 | 171667000
| Total | 631000 | 7994 | 0 | 15000 | 622000 | 8000 | 0 | 15000 |  |  |  | Total | 1128800 |  |  |  | Total | 8.8 | 8.8 | 0 | 0.2 | 9.1 | 9.2 | 0 | 0 | mg/L | 3.0832 | 1.25 | 0.050837 | 1.7225 |  |  |  |  | Raw.Trb. | 0.91 | Cmb.Trb. | 0.058 | Total | 695000 | 695700 | 0
2 | Pres. | 180936000 | 1634180 | 3983180 | 6654330 | 251712000 | 2167440 | 6747500 | 11322400 | 1291000 | 78800 | 1369800 | now | 1196713000 |  | 0 | 1.05 | now | 2427 | 3420.1 | 36.3 | 47.2 | 2548.5 | 3608.1 | 61.3 | 8.2 | "/lb | 3.0625 | 5.875 | 2.9375 | 9 | 9 | Raw | 16.4 | 7.35 | ef.turb.1 | 0.043 | ef.turb.2 | 0.059 | Pres. | 482148000 | 282260800 | 171703000
| Prev | 180314000 | 1626380 | 3951180 | 6630330 | 251043000 | 2167440 | 6747500 | 11307400 |  |  |  | prev | 1195547600 |  |  |  | prev | 2418.2 | 3410.9 | 36.3 | 47.1 | 2539.2 | 3598.6 | 61.1 | 8.2 | Lbs. | 32.8912 | 12.925 | 0.73438 | 18 |  | Trtd | 17.3 | 7.87 | AC.1 | 0.217 | AC.2 | 0.245 | Prev. | 481417000 | 281540000 | 171667000
| Total | 622000 | 7800 | 32000 | 24000 | 669000 | 0 | 0 | 15000 |  |  |  | Total | 1165400 |  |  |  | Total | 8.8 | 9.2 | 0 | 0.1 | 9.3 | 9.5 | 0.2 | 0 | mg/L | 3.0548 | 1.2004 | 0.068206 | 1.6718 |  |  |  |  | Raw.Trb. | 0.88 | Cmb.Trb. | 0.036 | Total | 731000 | 720800 | 36000
10.6
3 | Pres. | 181501000 | 1634380 | 3983180 | 6669330 | 252226000 | 2175430 | 6779500 | 11345500 | 1079000 | 78290 | 1157290 | now | 1197840500 |  | 0 | 1.01 | now | 2434.9 | 3427.5 | 36.3 | 47.4 | 2556.6 | 3615.9 | 61.4 | 8.3 | "/lb | 2.75 | 5 | 1.9375 | 7 | 7 | Raw | 16 | 7.33 | ef.turb.1 | 0.05 | ef.turb.2 | 0.058 | Pres. | 482775000 | 282829500 | 171737000
| Prev | 180936000 | 1634180 | 3983180 | 6654330 | 251712000 | 2167440 | 6747500 | 11322400 |  |  |  | prev | 1196713000 |  |  |  | prev | 2427 | 3420.1 | 36.3 | 47.2 | 2548.5 | 3608.1 | 61.3 | 8.2 | Lbs. | 29.535 | 11 | 0.48438 | 14 |  | Trtd | 17.9 | 7.81 | AC.1 | 0.359 | AC.2 | 0.183 | Prev. | 482148000 | 282260800 | 171703000
| Total | 565000 | 200 | 0 | 15000 | 514000 | 7990 | 32000 | 23100 |  |  |  | Total | 1127500 |  |  |  | Total | 7.9 | 7.4 | 0 | 0.2 | 8.1 | 7.8 | 0.1 | 0.1 | mg/L | 3.2821 | 1.2224 | 0.053826 | 1.5558 |  |  |  |  | Raw.Trb. | 0.9 | Cmb.Trb. | 0.036 | Total | 627000 | 568700 | 34000
4 | Pres. | 182176000 | 1643380 | 3983180 | 6683330 | 252901000 | 2183430 | 6779500 | 11361500 | 1350000 | 47000 | 1397000 | now | 1198968600 |  | 0 | 0.95 | now | 2444.3 | 3436.9 | 36.6 | 47.4 | 2566.4 | 3625.7 | 61.4 | 8.3 | "/lb | 3.0625 | 6.125 | 2.25 | 10 | 9 | Raw | 16.5 | 7.4 | ef.turb.1 | 0.044 | ef.turb.2 | 0.064 | Pres. | 483529000 | 283584700 | 171737000
| Prev | 181501000 | 1634380 | 3983180 | 6669330 | 252226000 | 2175430 | 6779500 | 11345500 |  |  |  | prev | 1197840500 |  |  |  | prev | 2434.9 | 3427.5 | 36.3 | 47.4 | 2556.6 | 3615.9 | 61.4 | 8.3 | Lbs. | 32.8912 | 13.475 | 0.5625 | 19 |  | Trtd | 17.6 | 7.88 | AC.1 | 0.217 | AC.2 | 0.216 | Prev. | 482775000 | 282829500 | 171737000
| Total | 675000 | 9000 | 0 | 14000 | 675000 | 8000 | 0 | 16000 |  |  |  | Total | 1128100 |  |  |  | Total | 9.4 | 9.4 | 0.3 | 0 | 9.8 | 9.8 | 0 | 0 | mg/L | 2.9213 | 1.1968 | 0.04996 | 1.6875 |  |  |  |  | Raw.Trb. | 0.93 | Cmb.Trb. | 0.04 | Total | 754000 | 755200 | 0
5 | Pres. | 182741000 | 1643380 | 4015170 | 6708330 | 253490000 | 2183430 | 6779500 | 11377500 | 1154000 | 72990 | 1226990 | now | 1200056500 | 0 | 0 | 1.03 | now | 2452.2 | 3445.1 | 36.6 | 47.4 | 2574.7 | 3634.1 | 61.6 | 8.3 | "/lb | 2.9375 | 5.25 | 1.9375 | 8 | 8 | Raw | 15.9 | 7.32 | ef.turb.1 | 0.044 | ef.turb.2 | 0.063 | Pres. | 484173000 | 284223900 | 171773000
| Prev | 182176000 | 1643380 | 3983180 | 6683330 | 252901000 | 2183430 | 6779500 | 11361500 |  |  |  | prev | 1198968600 |  |  |  | prev | 2444.3 | 3436.9 | 36.6 | 47.4 | 2566.4 | 3625.7 | 61.4 | 8.3 | Lbs. | 31.5488 | 11.55 | 0.48438 | 16 |  | Trtd | 17.9 | 7.89 | AC.1 | 0.33 | AC.2 | 0.329 | Prev. | 483529000 | 283584700 | 171737000
| Total | 565000 | 0 | 31990 | 25000 | 589000 | 0 | 0 | 16000 |  |  |  | Total | 1087900 |  |  |  | Total | 7.9 | 8.2 | 0 | 0 | 8.3 | 8.4 | 0.2 | 0 | mg/L | 3.278 | 1.2001 | 0.050328 | 1.6624 |  |  |  |  | Raw.Trb. | 1.04 | Cmb.Trb. | 0.037 | Total | 644000 | 639200 | 36000
6 | Pres. | 183263000 | 1651380 | 4015170 | 6723320 | 253986000 | 2191430 | 6811500 | 11400500 | 1018000 | 85990 | 1103990 | now | 1201158000 |  | 0 | 1.04 | now | 2459.7 | 3452.1 | 36.6 | 47.7 | 2582.5 | 3641.5 | 61.8 | 8.3 | "/lb | 2.625 | 4.625 | 1.75 | 7 | 7 | Raw | 18.5 | 7.55 | ef.turb.1 | 0.047 | ef.turb.2 | 0.06 | Pres. | 484757000 | 284784000 | 171807000
| Prev | 182741000 | 1643380 | 4015170 | 6708330 | 253490000 | 2183430 | 6779500 | 11377500 |  |  |  | prev | 1200056500 |  |  |  | prev | 2452.2 | 3445.1 | 36.6 | 47.4 | 2574.7 | 3634.1 | 61.6 | 8.3 | Lbs. | 28.1925 | 10.175 | 0.4375 | 14 |  | Trtd | 19.2 | 7.75 | AC.1 | 0.209 | AC.2 | 0.213 | Prev. | 484173000 | 284223900 | 171773000
| Total | 522000 | 8000 | 0 | 14990 | 496000 | 8000 | 32000 | 23000 |  |  |  | Total | 1101500 |  |  |  | Total | 7.5 | 7 | 0 | 0.3 | 7.8 | 7.4 | 0.2 | 0 | mg/L | 3.3206 | 1.1985 | 0.05153 | 1.649 |  |  |  |  | Raw.Trb. | 0.98 | Cmb.Trb. | 0.037 | Total | 584000 | 560100 | 34000
7 | Pres. | 184009000 | 1651380 | 4048170 | 6747320 | 254559000 | 2191430 | 6811500 | 11423500 | 1319000 | 80000 | 1399000 | now | 1202330300 |  | 0 | 1.04 | now | 2470.2 | 3460.1 | 36.6 | 47.7 | 2593.3 | 3649.8 | 61.9 | 8.4 | "/lb | 3.5 | 6.25 | 2.25 | 11 | 8 | Raw | 17.9 | 7.71 | ef.turb.1 | 0.05 | ef.turb.2 | 0.06 | Pres. | 485594000 | 285417400 | 171843000
| Prev | 183263000 | 1651380 | 4015170 | 6723320 | 253986000 | 2191430 | 6811500 | 11400500 |  |  |  | prev | 1201158000 |  |  |  | prev | 2459.7 | 3452.1 | 36.6 | 47.7 | 2582.5 | 3641.5 | 61.8 | 8.3 | Lbs. | 37.59 | 13.75 | 0.5625 | 19 |  | Trtd | 19.8 | 7.84 | AC.1 | 0.29 | AC.2 | 0.31 | Prev. | 484757000 | 284784000 | 171807000
| Total | 746000 | 0 | 33000 | 24000 | 573000 | 0 | 0 | 23000 |  |  |  | Total | 1172300 |  |  |  | Total | 10.5 | 8 | 0 | 0 | 10.8 | 8.3 | 0.1 | 0.1 | mg/L | 3.4171 | 1.2499 | 0.051134 | 1.7272 |  |  |  |  | Raw.Trb. | 0.92 | Cmb.Trb. | 0.04 | Total | 837000 | 633400 | 36000
8 | Pres. | 184671000 | 1659380 | 4048170 | 6762320 | 255192000 | 2199430 | 6842500 | 11447500 | 1295000 | 86000 | 1381000 | now | 1203455400 |  | 0 | 1.01 | now | 2479.5 | 3469 | 36.7 | 48 | 2603 | 3659.1 | 62.1 | 8.4 | "/lb | 3.25 | 5.75 | 2.0625 | 9 | 9 | Raw | 18.1 | 7.57 | ef.turb.1 | 0.052 | ef.turb.2 | 0.062 | Pres. | 486332000 | 286123300 | 171878000
| Prev | 184009000 | 1651380 | 4048170 | 6747320 | 254559000 | 2191430 | 6811500 | 11423500 |  |  |  | prev | 1202330300 |  |  |  | prev | 2470.2 | 3460.1 | 36.6 | 47.7 | 2593.3 | 3649.8 | 61.9 | 8.4 | Lbs. | 34.905 | 12.65 | 0.51562 | 18 |  | Trtd | 19.2 | 7.87 | AC.1 | 0.21 | AC.2 | 0.203 | Prev. | 485594000 | 285417400 | 171843000
| Total | 662000 | 8000 | 0 | 15000 | 633000 | 8000 | 31000 | 24000 |  |  |  | Total | 1125100 |  |  |  | Total | 9.3 | 8.9 | 0.1 | 0.3 | 9.7 | 9.3 | 0.2 | 0 | mg/L | 3.2319 | 1.1713 | 0.047742 | 1.6666 |  |  |  |  | Raw.Trb. | 0.96 | Cmb.Trb. | 0.04 | Total | 738000 | 705900 | 35000
9 | Pres. | 185171000 | 1667380 | 4048170 | 6776320 | 255709000 | 2207430 | 6842500 | 11462500 | 1017000 | 45000 | 1062000 | now | 1204584000 |  | 0 | 1.05 | now | 2486.7 | 3476.7 | 36.9 | 48 | 2610.6 | 3666.7 | 62.1 | 8.4 | "/lb | 3.125 | 4.75 | 1.625 | 7 | 7 | Raw | 18.5 | 7.49 | ef.turb.1 | 0.048 | ef.turb.2 | 0.066 | Pres. | 486898000 | 286696400 | 171878000
| Prev | 184671000 | 1659380 | 4048170 | 6762320 | 255192000 | 2199430 | 6842500 | 11447500 |  |  |  | prev | 1203455400 |  |  |  | prev | 2479.5 | 3469 | 36.7 | 48 | 2603 | 3659.1 | 62.1 | 8.4 | Lbs. | 33.5625 | 10.45 | 0.40625 | 14 |  | Trtd | 19.9 | 7.88 | AC.1 | 0.249 | AC.2 | 0.24 | Prev. | 486332000 | 286123300 | 171878000
| Total | 500000 | 8000 | 0 | 14000 | 517000 | 8000 | 0 | 15000 |  |  |  | Total | 1128600 |  |  |  | Total | 7.2 | 7.7 | 0.2 | 0 | 7.6 | 7.6 | 0 | 0 | mg/L | 3.957 | 1.2321 | 0.047897 | 1.6506 |  |  |  |  | Raw.Trb. | 0.94 | Cmb.Trb. | 0.042 | Total | 566000 | 573100 | 0
10 | Pres. | 185748000 | 1667380 | 4080170 | 6776320 | 256294000 | 2215430 | 6842500 | 11477500 | 1162000 | 55000 | 1217000 | now | 1205713000 |  | 0 | 0.93 | now | 2494.8 | 3484.4 | 37 | 48 | 2619 | 3675.3 | 62.3 | 8.4 | "/lb | 2.875 | 5 | 1.875 | 8 | 8 | Raw | 18.6 | 7.68 | ef.turb.1 | 0.05 | ef.turb.2 | 0.06 | Pres. | 487548000 | 287341000 | 171913000
| Prev | 185171000 | 1667380 | 4048170 | 6776320 | 255709000 | 2207430 | 6842500 | 11462500 |  |  |  | prev | 1204584000 |  |  |  | prev | 2486.7 | 3476.7 | 36.9 | 48 | 2610.6 | 3666.7 | 62.1 | 8.4 | Lbs. | 30.8775 | 11 | 0.46875 | 16 |  | Trtd | 20.4 | 7.95 | AC.1 | 0.3 | AC.2 | 0.26 | Prev. | 486898000 | 286696400 | 171878000
| Total | 577000 | 0 | 32000 | 0 | 585000 | 8000 | 0 | 15000 |  |  |  | Total | 1129000 |  |  |  | Total | 8.1 | 7.7 | 0.1 | 0 | 8.4 | 8.6 | 0.2 | 0 | mg/L | 3.1862 | 1.1351 | 0.048369 | 1.651 |  |  |  |  | Raw.Trb. | 0.93 | Cmb.Trb. | 0.03 | Total | 650000 | 644600 | 35000
11 | Pres. | 186322000 | 1675380 | 4080170 | 6815320 | 256848000 | 2215430 | 6875490 | 11501500 | 1128000 | 103990 | 1231990 | now | 1206719800 |  | 0 | 0.94 | now | 2502.8 | 3492.3 | 37.2 | 48.1 | 2627.3 | 3683.3 | 62.5 | 8.4 | "/lb | 2.875 | 5 | 1.875 | 7 | 8 | Raw | 17.2 | 8.19 | ef.turb.1 | 0.05 | ef.turb.2 | 0.06 | Pres. | 488194000 | 287953500 | 171948000
| Prev | 185748000 | 1667380 | 4080170 | 6776320 | 256294000 | 2215430 | 6842500 | 11477500 |  |  |  | prev | 1205713000 |  |  |  | prev | 2494.8 | 3484.4 | 37 | 48 | 2619 | 3675.3 | 62.3 | 8.4 | Lbs. | 30.8775 | 11 | 0.46875 | 15 |  | Trtd | 19.2 | 7.77 | AC.1 | 0.2 | AC.2 | 0.3 | Prev. | 487548000 | 287341000 | 171913000
| Total | 574000 | 8000 | 0 | 39000 | 554000 | 0 | 32990 | 24000 |  |  |  | Total | 1006800 |  |  |  | Total | 8 | 7.9 | 0.2 | 0.1 | 8.3 | 8 | 0.2 | 0 | mg/L | 3.2822 | 1.1693 | 0.049827 | 1.5945 |  |  |  |  | Raw.Trb. | 0.93 | Cmb.Trb. | 0.04 | Total | 646000 | 612500 | 35000
12 | Pres. | 186859000 | 1683380 | 4080170 | 6830320 | 257409000 | 2223430 | 6875490 | 11515500 | 1098000 | 45000 | 1143000 | now | 1207703400 |  | 0.96 | 0.88 | now | 2510.3 | 3500.1 | 37.2 | 48.3 | 2635.2 | 3691.3 | 62.5 | 8.4 | "/lb | 2.75 | 5 | 2 | 7 | 8 | Raw | 17.6 | 7.64 | ef.turb.1 | 0.05 | ef.turb.2 | 0.06 | Pres. | 488803000 | 288571680 | 171948000
| Prev | 186322000 | 1675380 | 4080170 | 6815320 | 256848000 | 2215430 | 6875490 | 11501500 |  |  |  | prev | 1206719800 |  |  |  | prev | 2502.8 | 3492.3 | 37.2 | 48.1 | 2627.3 | 3683.3 | 62.5 | 8.4 | Lbs. | 29.535 | 11 | 0.5 | 15 |  | Trtd | 19.1 | 7.9 | AC.1 | 0.25 | AC.2 | 0.24 | Prev. | 488194000 | 287953500 | 171948000
| Total | 537000 | 8000 | 0 | 15000 | 561000 | 8000 | 0 | 14000 |  |  |  | Total | 983600 |  |  |  | Total | 7.5 | 7.8 | 0 | 0.2 | 7.9 | 8 | 0 | 0 | mg/L | 3.2253 | 1.2012 | 0.054601 | 1.638 |  |  |  |  | Raw.Trb. | 1.02 | Cmb.Trb. | 0.04 | Total | 609000 | 618180 | 0
13 | Pres. | 188161000 | 1691380 | 4113170 | 6851320 | 257409000 | 2223430 | 6875490 | 11515500 | 1302000 | 62000 | 1364000 | now | 1208798600 |  | 0 | 0.96 | now | 2525.8 | 3500.1 | 37.2 | 48.4 | 2651.2 | 3691.3 | 62.6 | 8.5 | "/lb | 3.25 | 5 | 1.875 | 17 | 0 | Raw | 16.8 | 7.71 | ef.turb.1 | 0.05 | ef.turb.2 | 0.06 | Pres. | 490238000 | 288571680 | 171984000
| Prev | 186859000 | 1683380 | 4080170 | 6830320 | 257409000 | 2223430 | 6875490 | 11515500 |  |  |  | prev | 1207703400 |  |  |  | prev | 2510.3 | 3500.1 | 37.2 | 48.3 | 2635.2 | 3691.3 | 62.5 | 8.4 | Lbs. | 34.905 | 11 | 0.46875 | 17 |  | Trtd | 18.3 | 7.85 | AC.1 | 0.37 | AC.2 | 0.31 | Prev. | 488803000 | 288571680 | 171948000
| Total | 1302000 | 8000 | 33000 | 21000 | 0 | 0 | 0 | 0 |  |  |  | Total | 1095200 |  |  |  | Total | 15.5 | 0 | 0 | 0.1 | 16 | 0 | 0.1 | 0.1 | mg/L | 3.2145 | 1.013 | 0.043168 | 1.5656 |  |  |  |  | Raw.Trb. | 0.96 | Cmb.Trb. | 0.04 | Total | 1435000 | 0 | 36000
14 | Pres. | 189104000 | 1700380 | 4145160 | 6884310 | 257409000 | 2223430 | 6875490 | 11545500 | 943000 | 103980 | 1046980 | now | 1209837600 |  | 0 | 1.02 | now | 2536.8 | 3500.1 | 37.2 | 48.5 | 2662.8 | 3691.6 | 62.8 | 8.6 | "/lb | 2.75 | 3.25 | 1.25 | 13 | 0 | Raw | 15.8 | 7.71 | ef.turb.1 | 0.05 | ef.turb.2 | x | Pres. | 491301000 | 288571680 | 172020000
| Prev | 188161000 | 1691380 | 4113170 | 6851320 | 257409000 | 2223430 | 6875490 | 11515500 |  |  |  | prev | 1208798600 |  |  |  | prev | 2525.8 | 3500.1 | 37.2 | 48.4 | 2651.2 | 3691.3 | 62.6 | 8.5 | Lbs. | 29.535 | 7.15 | 0.3125 | 13 |  | Trtd | 17.4 | 7.8 | AC.1 | 0.29 | AC.2 | x | Prev. | 490238000 | 288571680 | 171984000
| Total | 943000 | 9000 | 31990 | 32990 | 0 | 0 | 0 | 30000 |  |  |  | Total | 1039000 |  |  |  | Total | 11 | 0 | 0 | 0.1 | 11.6 | 0.3 | 0.2 | 0.1 | mg/L | 3.7554 | 0.90913 | 0.039735 | 1.653 |  |  |  |  | Raw.Trb. | 0.77 | Cmb.Trb. | 0.03 | Total | 1063000 | 0 | 36000
15 | Pres. | 190052000 | 1709380 | 4145160 | 6901310 | 257409000 | 2223430 | 6875490 | 11545500 | 948000 | 26000 | 974000 | now | 1210852500 |  | 0 | 0.88 | now | 2548.1 | 3500.4 | 37.2 | 48.7 | 2674.4 | 3691.9 | 62.8 | 8.6 | "/lb | 2.5 | 4 | 1.5 | 13 | 0 | Raw | 17.9 | 7.68 | ef.turb.1 | 0.06 | ef.turb.2 | x | Pres. | 492350000 | 288571680 | 172020000
| Prev | 189104000 | 1700380 | 4145160 | 6884310 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1209837600 |  |  |  | prev | 2536.8 | 3500.1 | 37.2 | 48.5 | 2662.8 | 3691.6 | 62.8 | 8.6 | Lbs. | 26.85 | 8.8 | 0.375 | 13 |  | Trtd | 18.5 | 7.94 | AC.1 | 0.26 | AC.2 | x | Prev. | 491301000 | 288571680 | 172020000
| Total | 948000 | 9000 | 0 | 17000 | 0 | 0 | 0 | 0 |  |  |  | Total | 1014900 |  |  |  | Total | 11.3 | 0.3 | 0 | 0.2 | 11.6 | 0.3 | 0 | 0 | mg/L | 3.396 | 1.113 | 0.04743 | 1.6443 |  |  |  |  | Raw.Trb. | 0.79 | Cmb.Trb. | 0.03 | Total | 1049000 | 0 | 0
16 | Pres. | 191243000 | 1718380 | 4178160 | 6922310 | 257409000 | 2223430 | 6875490 | 11545500 | 1191000 | 63000 | 1254000 | now | 1211861100 |  | 0 | 0.96 | now | 2562.3 | 3500.4 | 37.2 | 48.8 | 2688.9 | 3691.9 | 62.9 | 8.6 | "/lb | 3 | 4 | 1.625 | 15 | 0 | Raw | 15.1 | 7.65 | ef.turb.1 | 0.07 | ef.turb.2 | x | Pres. | 493662000 | 288571680 | 172055000
| Prev | 190052000 | 1709380 | 4145160 | 6901310 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1210852500 |  |  |  | prev | 2548.1 | 3500.4 | 37.2 | 48.7 | 2674.4 | 3691.9 | 62.8 | 8.6 | Lbs. | 32.22 | 8.8 | 0.40625 | 15 |  | Trtd | 17.7 | 8.04 | AC.1 | 0.29 | AC.2 | x | Prev. | 492350000 | 288571680 | 172020000
| Total | 1191000 | 9000 | 33000 | 21000 | 0 | 0 | 0 | 0 |  |  |  | Total | 1008600 |  |  |  | Total | 14.2 | 0 | 0 | 0.1 | 14.5 | 0 | 0.1 | 0 | mg/L | 3.2438 | 0.88594 | 0.040899 | 1.5101 |  |  |  |  | Raw.Trb. | 0.96 | Cmb.Trb. | 0.04 | Total | 1312000 | 0 | 35000
17 | Pres. | 192436000 | 1726380 | 4178160 | 6930310 | 257409000 | 2223430 | 6875490 | 11545500 | 1193000 | 16000 | 1209000 | now | 1212890600 |  | 1.1 | 0.95 | now | 2577 | 3500.4 | 37.2 | 48.9 | 2703.8 | 3691.9 | 62.9 | 8.6 | "/lb | 3 | 8 | 1.75 | 16 |  | Raw | 15.1 | 7.6 | ef.turb.1 | 0.04 | ef.turb.2 | x | Pres. | 494971000 | 288571680 | 172055000
| Prev | 191243000 | 1718380 | 4178160 | 6922310 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1211861100 |  |  |  | prev | 2562.3 | 3500.4 | 37.2 | 48.8 | 2688.9 | 3691.9 | 62.9 | 8.6 | Lbs. | 32.22 | 17.6 | 0.4375 | 16 |  | Trtd | 17.5 | 8.11 | AC.1 | 0.32 | AC.2 | x | Prev. | 493662000 | 288571680 | 172055000
| Total | 1193000 | 8000 | 0 | 8000 | 0 | 0 | 0 | 0 |  |  |  | Total | 1029500 |  |  |  | Total | 14.7 | 0 | 0 | 0.1 | 14.9 | 0 | 0 | 0 | mg/L | 3.2383 | 1.7689 | 0.043972 | 1.6081 |  |  |  |  | Raw.Trb. | 0.79 | Cmb.Trb. | 0.04 | Total | 1309000 | 0 | 0
18 | Pres. | 193212000 | 1744380 | 4210160 | 6961310 | 257409000 | 2223430 | 6875490 | 11545500 | 776000 | 81000 | 857000 | now | 1213631800 |  | 0.82 | 0.96 | now | 2586.6 | 3500.4 | 37.2 | 49.1 | 2714.1 | 3691.9 | 63.1 | 8.7 | "/lb | 4.375 | 5 | 1.25 | 11 | 0 | Raw | 16.6 | 7.76 | ef.turb.1 | 0.05 | ef.turb.2 | x | Pres. | 495862000 | 288571680 | 172091000
| Prev | 192436000 | 1726380 | 4178160 | 6930310 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1212890600 |  |  |  | prev | 2577 | 3500.4 | 37.2 | 48.9 | 2703.8 | 3691.9 | 62.9 | 8.6 | Lbs. | 46.9875 | 11 | 0.3125 | 11 |  | Trtd | 17.1 | 7.95 | AC.1 | 0.22 | AC.2 | x | Prev. | 494971000 | 288571680 | 172055000
| Total | 776000 | 18000 | 32000 | 31000 | 0 | 0 | 0 | 0 |  |  |  | Total | 741200 |  |  |  | Total | 9.6 | 0 | 0 | 0.2 | 10.3 | 0 | 0.2 | 0.1 | mg/L | 7.2603 | 1.6997 | 0.048286 | 1.6997 |  |  |  |  | Raw.Trb. | 1.15 | Cmb.Trb. | 0.03 | Total | 891000 | 0 | 36000
19 | Pres. | 193922000 | 1761380 | 4242160 | 6998300 | 257409000 | 2223430 | 6875490 | 11545500 | 710000 | 85990 | 795990 | now | 1214481700 |  | 0.477 | 0.74 | now | 2595.6 | 3500.4 | 37.2 | 49.4 | 2723.9 | 3691.9 | 63.2 | 8.7 | "/lb | 4.75 | 4.5 | 1.75 | 13 | 0 | Raw | 15.8 | 7.51 | ef.turb.1 | 0.078 | ef.turb.2 | x | Pres. | 496688000 | 288571680 | 172126000
| Prev | 193212000 | 1744380 | 4210160 | 6961310 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1213631800 |  |  |  | prev | 2586.6 | 3500.4 | 37.2 | 49.1 | 2714.1 | 3691.9 | 63.1 | 8.7 | Lbs. | 51.015 | 9.9 | 0.4375 | 13 |  | Trtd | 16.6 | 7.85 | AC.1 | 1.97 | AC.2 | x | Prev. | 495862000 | 288571680 | 172091000
| Total | 710000 | 17000 | 32000 | 36990 | 0 | 0 | 0 | 0 |  |  |  | Total | 849900 |  |  |  | Total | 9 | 0 | 0 | 0.3 | 9.8 | 0 | 0.1 | 0 | mg/L | 8.6154 | 1.6719 | 0.073885 | 2.1954 |  |  |  |  | Raw.Trb. | 8.05 | Cmb.Trb. | 0.06 | Total | 826000 | 0 | 35000
20 | Pres. | 195104000 | 1770380 | 4242160 | 7006300 | 257409000 | 2223430 | 6875490 | 11545500 | 1182000 | 17000 | 1199000 | now | 1215444000 |  | 0 | 0.9 | now | 2610.6 | 3500.4 | 37.2 | 49.5 | 2739.1 | 3691.9 | 63.2 | 8.7 | "/lb | 5.5 | 6.125 | 3.25 | 22 | 0 | Raw | 15.8 | 7.36 | ef.turb.1 | 0.06 | ef.turb.2 | x | Pres. | 497986000 | 288571680 | 172126000
| Prev | 193922000 | 1761380 | 4242160 | 6998300 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1214481700 |  |  |  | prev | 2595.6 | 3500.4 | 37.2 | 49.4 | 2723.9 | 3691.9 | 63.2 | 8.7 | Lbs. | 59.07 | 13.475 | 0.8125 | 22 |  | Trtd | 15.9 | 7.74 | AC.1 | 1.52 | AC.2 | x | Prev. | 496688000 | 288571680 | 172126000
| Total | 1182000 | 9000 | 0 | 8000 | 0 | 0 | 0 | 0 |  |  |  | Total | 962300 |  |  |  | Total | 15 | 0 | 0 | 0.1 | 15.2 | 0 | 0 | 0 | mg/L | 5.9922 | 1.3669 | 0.082421 | 2.2317 |  |  |  |  | Raw.Trb. | 6.83 | Cmb.Trb. | 0.04 | Total | 1298000 | 0 | 0
21 | Pres. | 195961000 | 1779380 | 4275160 | 7028300 | 257409000 | 2223430 | 6875490 | 11545500 | 857000 | 64000 | 921000 | now | 1216397300 |  | 0 | 1.08 | now | 2621.5 | 3500.4 | 37.2 | 49.6 | 2750.5 | 3691.9 | 63.4 | 8.8 | "/lb | 2.875 | 4.5 | 1.625 | 14 | 0 | Raw | 15.1 | 7.37 | ef.turb.1 | 0.047 | ef.turb.2 | x | Pres. | 498942000 | 288571680 | 172162000
| Prev | 195104000 | 1770380 | 4242160 | 7006300 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1215444000 |  |  |  | prev | 2610.6 | 3500.4 | 37.2 | 49.5 | 2739.1 | 3691.9 | 63.2 | 8.7 | Lbs. | 30.8775 | 9.9 | 0.40625 | 14 |  | Trtd | 16.5 | 7.7 | AC.1 | 0.461 | AC.2 | x | Prev. | 497986000 | 288571680 | 172126000
| Total | 857000 | 9000 | 33000 | 22000 | 0 | 0 | 0 | 0 |  |  |  | Total | 953300 |  |  |  | Total | 10.9 | 0 | 0 | 0.1 | 11.4 | 0 | 0.2 | 0.1 | mg/L | 4.3201 | 1.3851 | 0.056839 | 1.9588 |  |  |  |  | Raw.Trb. | 1.74 | Cmb.Trb. | 0.031 | Total | 956000 | 0 | 36000
x
22 | Pres. | 196953000 | 1788380 | 4275160 | 7036300 | 257409000 | 2223430 | 6875490 | 11545500 | 992000 | 17000 | 1009000 | now | 1217367700 |  | 0.02 | 0.98 | now | 2634.2 | 3500.4 | 37.2 | 49.7 | 2763.4 | 3691.9 | 63.4 | 8.8 | "/lb | 2.875 | 5 | 2 | 15 | 0 | Raw | 15.5 | 7.25 | ef.turb.1 | 0.045 | ef.turb.2 | x | Pres. | 500031000 | 288571680 | 172162000
| Prev | 195961000 | 1779380 | 4275160 | 7028300 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1216397300 |  |  |  | prev | 2621.5 | 3500.4 | 37.2 | 49.6 | 2750.5 | 3691.9 | 63.4 | 8.8 | Lbs. | 30.8775 | 11 | 0.5 | 15 |  | Trtd | 16.4 | 7.55 | AC.1 | 0.361 | AC.2 | x | Prev. | 498942000 | 288571680 | 172162000
| Total | 992000 | 9000 | 0 | 8000 | 0 | 0 | 0 | 0 |  |  |  | Total | 970400 |  |  |  | Total | 12.7 | 0 | 0 | 0.1 | 12.9 | 0 | 0 | 0 | mg/L | 3.7322 | 1.3296 | 0.060436 | 1.8131 |  |  |  |  | Raw.Trb. | 1.43 | Cmb.Trb. | 0.029 | Total | 1089000 | 0 | 0
23 | Pres. | 198099000 | 1788380 | 4307150 | 7056300 | 257409000 | 2223430 | 6875490 | 11545500 | 1146000 | 51990 | 1197990 | now | 1218344400 |  | 0 | 0.97 | now | 2648.8 | 3500.4 | 37.2 | 49.7 | 2778.4 | 3691.9 | 63.5 | 8.9 | "/lb | 3.25 | 5.9375 | 2.25 | 18 | 0 | Raw | 16.4 | 7.44 | ef.turb.1 | 0.042 | ef.turb.2 | x | Pres. | 501282000 | 288571680 | 172197000
| Prev | 196953000 | 1788380 | 4275160 | 7036300 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1217367700 |  |  |  | prev | 2634.2 | 3500.4 | 37.2 | 49.7 | 2763.4 | 3691.9 | 63.4 | 8.8 | Lbs. | 34.905 | 13.0625 | 0.5625 | 18 |  | Trtd | 16.9 | 7.76 | AC.1 | 0.486 | AC.2 | x | Prev. | 500031000 | 288571680 | 172162000
| Total | 1146000 | 0 | 31990 | 20000 | 0 | 0 | 0 | 0 |  |  |  | Total | 976700 |  |  |  | Total | 14.6 | 0 | 0 | 0 | 15 | 0 | 0.1 | 0.1 | mg/L | 3.6521 | 1.3667 | 0.058853 | 1.8833 |  |  |  |  | Raw.Trb. | 1.25 | Cmb.Trb. | 0.024 | Total | 1251000 | 0 | 35000
24 | Pres. | 199032000 | 1797380 | 4339150 | 7075300 | 257409000 | 2223430 | 6875490 | 11545500 | 933000 | 60000 | 993000 | now | 1219305700 |  | 0 | 1.13 | now | 2660.7 | 3500.4 | 37.2 | 49.8 | 2790.6 | 3691.9 | 63.7 | 8.9 | "/lb | 2.875 | 4.75 | 2.25 | 11 | 0 | Raw | 16 | 7.45 | ef.turb.1 | 0.042 | ef.turb.2 | x | Pres. | 502313000 | 288571680 | 172233000
| Prev | 198099000 | 1788380 | 4307150 | 7056300 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1218344400 |  |  |  | prev | 2648.8 | 3500.4 | 37.2 | 49.7 | 2778.4 | 3691.9 | 63.5 | 8.9 | Lbs. | 30.8775 | 10.45 | 0.5625 | 11 |  | Trtd | 16.8 | 7.81 | AC.1 | 0.224 | AC.2 | x | Prev. | 501282000 | 288571680 | 172197000
| Total | 933000 | 9000 | 32000 | 19000 | 0 | 0 | 0 | 0 |  |  |  | Total | 961300 |  |  |  | Total | 11.9 | 0 | 0 | 0.1 | 12.2 | 0 | 0.2 | 0 | mg/L | 3.9682 | 1.343 | 0.072289 | 1.4137 |  |  |  |  | Raw.Trb. | 1.01 | Cmb.Trb. | 0.026 | Total | 1031000 | 0 | 36000
25 | Pres. | 199976000 | 1806380 | 4339150 | 7083300 | 257409000 | 2223430 | 6875490 | 11545500 | 944000 | 17000 | 961000 | now | 1220249200 |  | 0 | 1.04 | now | 2672.8 | 3500.4 | 37.2 | 49.9 | 2802.8 | 3691.9 | 63.7 | 8.9 | "/lb | 3 | 4.75 | 1.875 | 11 | 0 | Raw | 16.3 | 7.7 | ef.turb.1 | 0.04 | ef.turb.2 | x | Pres. | 503348000 | 288571680 | 172233000
| Prev | 199032000 | 1797380 | 4339150 | 7075300 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1219305700 |  |  |  | prev | 2660.7 | 3500.4 | 37.2 | 49.8 | 2790.6 | 3691.9 | 63.7 | 8.9 | Lbs. | 32.22 | 10.45 | 0.46875 | 11 |  | Trtd | 17.1 | 8.02 | AC.1 | 0.24 | AC.2 | x | Prev. | 502313000 | 288571680 | 172233000
| Total | 944000 | 9000 | 0 | 8000 | 0 | 0 | 0 | 0 |  |  |  | Total | 943500 |  |  |  | Total | 12.1 | 0 | 0 | 0.1 | 12.2 | 0 | 0 | 0 | mg/L | 4.0925 | 1.3273 | 0.059539 | 1.3972 |  |  |  |  | Raw.Trb. | 0.9 | Cmb.Trb. | 0.03 | Total | 1035000 | 0 | 0
26 | Pres. | 201058000 | 1814390 | 4371150 | 7103300 | 257409000 | 2223430 | 6875490 | 11545500 | 1082000 | 60010 | 1142010 | now | 1221094200 |  | 0.41 | 0.97 | now | 2686.6 | 3500.4 | 37.2 | 49.9 | 2817 | 3691.9 | 63.9 | 9 | "/lb | 3.25 | 5.75 | 2 | 13 | 0 | Raw | 14.1 | 7.69 | ef.turb.1 | 0.048 | ef.turb.2 | x | Pres. | 504545000 | 288571680 | 172268000
| Prev | 199976000 | 1806380 | 4339150 | 7083300 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1220249200 |  |  |  | prev | 2672.8 | 3500.4 | 37.2 | 49.9 | 2802.8 | 3691.9 | 63.7 | 8.9 | Lbs. | 34.905 | 12.65 | 0.5 | 13 |  | Trtd | 17.1 | 8.13 | AC.1 | 0.26 | AC.2 | x | Prev. | 503348000 | 288571680 | 172233000
| Total | 1082000 | 8010 | 32000 | 20000 | 0 | 0 | 0 | 0 |  |  |  | Total | 845000 |  |  |  | Total | 13.8 | 0 | 0 | 0 | 14.2 | 0 | 0.2 | 0.1 | mg/L | 3.8681 | 1.4018 | 0.055409 | 1.4406 |  |  |  |  | Raw.Trb. | 1.05 | Cmb.Trb. | 0.03 | Total | 1197000 | 0 | 35000
27 | Pres. | 201958000 | 1841390 | 4403150 | 7122300 | 257409000 | 2223430 | 6875490 | 11545500 | 900000 | 78000 | 978000 | now | 1221929000 |  | 0.83 | 1 | now | 2698 | 3500.4 | 37.2 | 50.4 | 2829.2 | 3691.9 | 64 | 9 | "/lb | 3.5 | 4.75 | 1.875 | 11 | 0 | Raw | 17 | 7.57 | ef.turb.1 | 0.04 | ef.turb.2 | x | Pres. | 505568000 | 288571680 | 172304000
| Prev | 201058000 | 1814390 | 4371150 | 7103300 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1221094200 |  |  |  | prev | 2686.6 | 3500.4 | 37.2 | 49.9 | 2817 | 3691.9 | 63.9 | 9 | Lbs. | 37.59 | 10.45 | 0.46875 | 11 |  | Trtd | 17.1 | 8.13 | AC.1 | 0.32 | AC.2 | x | Prev. | 504545000 | 288571680 | 172268000
| Total | 900000 | 27000 | 32000 | 19000 | 0 | 0 | 0 | 0 |  |  |  | Total | 834800 |  |  |  | Total | 11.4 | 0 | 0 | 0.5 | 12.2 | 0 | 0.1 | 0 | mg/L | 5.008 | 1.3922 | 0.06245 | 1.4655 |  |  |  |  | Raw.Trb. | 1.23 | Cmb.Trb. | 0.03 | Total | 1023000 | 0 | 36000
28 | Pres. | 202855000 | 1880390 | 4468140 | 7153290 | 257409000 | 2223430 | 6875490 | 11545500 | 897000 | 134980 | 1031980 | now | 1222836200 |  | 0.43 | 0.95 | now | 2709.8 | 3500.4 | 37.2 | 50.9 | 2841.8 | 3691.9 | 64.3 | 9.2 | "/lb | 5 | 5 | 1.875 | 11 | 0 | Raw | 14.2 | 7.52 | ef.turb.1 | 0.047 | ef.turb.2 | x | Pres. | 506617000 | 288571680 | 172376000
| Prev | 201958000 | 1841390 | 4403150 | 7122300 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1221929000 |  |  |  | prev | 2698 | 3500.4 | 37.2 | 50.4 | 2829.2 | 3691.9 | 64 | 9 | Lbs. | 53.7 | 11 | 0.46875 | 11 |  | Trtd | 16.6 | 7.9 | AC.1 | 2.09 | AC.2 | x | Prev. | 505568000 | 288571680 | 172304000
| Total | 897000 | 39000 | 64990 | 30990 | 0 | 0 | 0 | 0 |  |  |  | Total | 907200 |  |  |  | Total | 11.8 | 0 | 0 | 0.5 | 12.6 | 0 | 0.3 | 0.2 | mg/L | 7.1782 | 1.4704 | 0.062659 | 1.4704 |  |  |  |  | Raw.Trb. | 6.82 | Cmb.Trb. | 0.078 | Total | 1049000 | 0 | 72000
29 | Pres. | 203705000 | 1889390 | 4468140 | 7170290 | 257409000 | 2223430 | 6875490 | 11545500 | 850000 | 26000 | 876000 | now | 1223694700 |  | 0 | 1 | now | 2720.4 | 3500.4 | 37.2 | 51 | 2852.8 | 3691.9 | 64.3 | 9.2 | "/lb | 2.9375 | 4.125 | 1.625 | 10 | 0 | Raw | 13.2 | 7.3 | ef.turb.1 | 0.045 | ef.turb.2 | x | Pres. | 507555000 | 288571680 | 172376000
| Prev | 202855000 | 1880390 | 4468140 | 7153290 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1222836200 |  |  |  | prev | 2709.8 | 3500.4 | 37.2 | 50.9 | 2841.8 | 3691.9 | 64.3 | 9.2 | Lbs. | 31.5488 | 9.075 | 0.40625 | 10 |  | Trtd | 15.1 | 7.68 | AC.1 | 1.688 | AC.2 | x | Prev. | 506617000 | 288571680 | 172376000
| Total | 850000 | 9000 | 0 | 17000 | 0 | 0 | 0 | 0 |  |  |  | Total | 858500 |  |  |  | Total | 10.6 | 0 | 0 | 0.1 | 11 | 0 | 0 | 0 | mg/L | 4.4504 | 1.2802 | 0.057307 | 1.4106 |  |  |  |  | Raw.Trb. | 3.64 | Cmb.Trb. | 0.035 | Total | 938000 | 0 | 0
30 | Pres. | 204597000 | 1899390 | 4501140 | 7189290 | 257409000 | 2223430 | 6875490 | 11545500 | 892000 | 62000 | 954000 | now | 1224536400 |  | 0.24 | 0.98 | now | 2731.7 | 3500.4 | 37.2 | 51.1 | 2864.5 | 3691.9 | 64.5 | 9.2 | "/lb | 2.125 | 4.5 | 1.875 | 12 | 0 | Raw | 14.3 | 7.32 | ef.turb.1 | 0.04 | ef.turb.2 | x | Pres. | 508556000 | 288571680 | 172411000
| Prev | 203705000 | 1889390 | 4468140 | 7170290 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1223694700 |  |  |  | prev | 2720.4 | 3500.4 | 37.2 | 51 | 2852.8 | 3691.9 | 64.3 | 9.2 | Lbs. | 22.8225 | 9.9 | 0.46875 | 12 |  | Trtd | 15.5 | 7.66 | AC.1 | 0.434 | AC.2 | x | Prev. | 507555000 | 288571680 | 172376000
| Total | 892000 | 10000 | 33000 | 19000 | 0 | 0 | 0 | 0 |  |  |  | Total | 841700 |  |  |  | Total | 11.3 | 0 | 0 | 0.1 | 11.7 | 0 | 0.2 | 0 | mg/L | 3.0678 | 1.3308 | 0.06301 | 1.6131 |  |  |  |  | Raw.Trb. | 1.8 | Cmb.Trb. | 0.028 | Total | 1001000 | 0 | 35000
[10 empty] | Totals | [6 empty] | AVG | [10 empty] | totals | [5 empty] | AVG TRTD |  |  |  | Avg.Cmb.Trb.
[10 empty] | 31902000 | 1850004 | 33752004 |  | 30117600 |  | 5.287 | 0.982 | [5 empty] | 334.4 | 102.5 |  |  |  | 1037.7525 | 337.7 | 14.5312 | 442 |  |  | 17.6833 | 7.8547 |  |  | 0.037567
[22 empty] | total- | 436.9

## Oct, 2021
October, 2021
Filters | [15 empty] | Rain | Cl2 | Pump Hours | [8 empty] | Chemicals | [5 empty] | Misc. |  |  | Turbidity |  |  |  | Meters
Day |  | CW.Tot.1 | Cla.Wst.1 | BW.Wst.1 | FTWst.1 | CW.Tot.2 | Cla.Wst.2 | BW.Wst.2 | FTWst.2 | Treated Total | Wastewater | Total Influent | Totalizer |  |  | Inches | Resid | Pump | Ef.Pmp.1 | Ef.Pmp.2 | Blo.1 | Blo.2 | URT.1 | URT.2 | BWP | SWP | Chem | ACH | SA | Poly | Cl2.1 | Cl2.2 | water | Temp | pH | F1 |  | F2 |  |  | RM1 | RM2 | BWM
1 | Pres. | 205409000 | 1909390 | 4501140 | 7197290 | 257409000 | 2223430 | 6875490 | 11545500 | 812000 | 18000 | 830000 | now | 1225386000 |  | 0 | 1.01 | now | 2742 | 3500.4 | 37.2 | 51.2 | 2875.2 | 3691.9 | 64.5 | 9.2 | "/lb | 2 | 4.125 | 2.25 | 10 | 0 | Raw | 13.5 | 7.35 | ef.turb.1 | 0.042 | ef.turb.2 | x | Pres. | 509449000 | 288571680 | 172411000
| Prev | 204597000 | 1899390 | 4501140 | 7189290 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1224536400 |  |  |  | prev | 2731.7 | 3500.4 | 37.2 | 51.1 | 2864.5 | 3691.9 | 64.5 | 9.2 | Lbs. | 21.48 | 9.075 | 0.5625 | 10 |  | Trtd | 15 | 7.89 | AC.1 | 0.502 | AC.2 | x | Prev. | 508556000 | 288571680 | 172411000
| Total | 812000 | 10000 | 0 | 8000 | 0 | 0 | 0 | 0 |  |  |  | Total | 849600 |  |  |  | Total | 10.3 | 0 | 0 | 0.1 | 10.7 | 0 | 0 | 0 | mg/L | 3.1718 | 1.3401 | 0.083062 | 1.4767 |  |  |  |  | Raw.Trb. | 1.57 | Cmb.Trb. | 0.032 | Total | 893000 | 0 | 0
2 | Pres. | 206306000 | 1919390 | 4533140 | 7217290 | 257409000 | 2223430 | 6875490 | 11545500 | 897000 | 62000 | 959000 | now | 1226153300 |  | 0 | 0.95 | now | 2753.4 | 3500.4 | 37.2 | 51.4 | 2887 | 3691.9 | 64.6 | 9.3 | "/lb | 2 | 4.75 | 1.9375 | 12 | 0 | Raw | 13.9 | 7.44 | ef.turb.1 | 0.039 | ef.turb.2 | x | Pres. | 510447000 | 288571680 | 172411000
| Prev | 205409000 | 1909390 | 4501140 | 7197290 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1225386000 |  |  |  | prev | 2742 | 3500.4 | 37.2 | 51.2 | 2875.2 | 3691.9 | 64.5 | 9.2 | Lbs. | 21.48 | 10.45 | 0.48438 | 12 |  | Trtd | 14.6 | 7.91 | AC.1 | 0.368 | AC.2 | x | Prev. | 509449000 | 288571680 | 172411000
| Total | 897000 | 10000 | 32000 | 20000 | 0 | 0 | 0 | 0 |  |  |  | Total | 767300 |  |  |  | Total | 11.4 | 0 | 0 | 0.2 | 11.8 | 0 | 0.1 | 0.1 | mg/L | 2.8713 | 1.3969 | 0.064748 | 1.6041 |  |  |  |  | Raw.Trb. | 1.32 | Cmb.Trb. | 0.028 | Total | 998000 | 0 | 0
10.6
3 | Pres. | 207245000 | 1919390 | 4533140 | 7225290 | 257409000 | 2223430 | 6875490 | 11545500 | 939000 | 8000 | 947000 | now | 1227069500 |  | 0 | 1.04 | now | 2765.4 | 3500.4 | 37.2 | 51.4 | 2899.1 | 3691.9 | 64.6 | 9.3 | "/lb | 2 | 5 | 1.75 | 12 | 0 | Raw | 12.8 | 7.44 | ef.turb.1 | 0.039 | ef.turb.2 | x | Pres. | 511465000 | 288571680 | 172447000
| Prev | 206306000 | 1919390 | 4533140 | 7217290 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1226153300 |  |  |  | prev | 2753.4 | 3500.4 | 37.2 | 51.4 | 2887 | 3691.9 | 64.6 | 9.3 | Lbs. | 21.48 | 11 | 0.4375 | 12 |  | Trtd | 13.5 | 7.85 | AC.1 | 0.473 | AC.2 | x | Prev. | 510447000 | 288571680 | 172411000
| Total | 939000 | 0 | 0 | 8000 | 0 | 0 | 0 | 0 |  |  |  | Total | 916200 |  |  |  | Total | 12 | 0 | 0 | 0 | 12.1 | 0 | 0 | 0 | mg/L | 2.7429 | 1.4046 | 0.055866 | 1.5323 |  |  |  |  | Raw.Trb. | 1.16 | Cmb.Trb. | 0.026 | Total | 1018000 | 0 | 36000
4 | Pres. | 208134000 | 1929390 | 4565130 | 7245290 | 257409000 | 2223430 | 6875490 | 11545500 | 889000 | 61990 | 950990 | now | 1227938000 |  | 0 | 1.05 | now | 2776.2 | 3500.4 | 37.2 | 51.5 | 2910.2 | 3691.9 | 64.8 | 9.3 | "/lb | 2 | 4.125 | 1.75 | 11 | 0 | Raw | 14.7 | 7.46 | ef.turb.1 | 0.04 | ef.turb.2 | x | Pres. | 512462000 | 288571680 | 172482000
| Prev | 207245000 | 1919390 | 4533140 | 7225290 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1227069500 |  |  |  | prev | 2765.4 | 3500.4 | 37.2 | 51.4 | 2899.1 | 3691.9 | 64.6 | 9.3 | Lbs. | 21.48 | 9.075 | 0.4375 | 11 |  | Trtd | 14.1 | 7.95 | AC.1 | 0.28 | AC.2 | x | Prev. | 511465000 | 288571680 | 172447000
| Total | 889000 | 10000 | 31990 | 20000 | 0 | 0 | 0 | 0 |  |  |  | Total | 868500 |  |  |  | Total | 10.8 | 0 | 0 | 0.1 | 11.1 | 0 | 0.2 | 0 | mg/L | 2.8971 | 1.224 | 0.059008 | 1.4836 |  |  |  |  | Raw.Trb. | 1.18 | Cmb.Trb. | 0.023 | Total | 997000 | 0 | 35000
5 | Pres. | 208980000 | 1938390 | 4565130 | 7253290 | 257409000 | 2223430 | 6875490 | 11545500 | 846000 | 17000 | 863000 | now | 1228762300 | 0 | 0.63 | 1.01 | now | 2786.6 | 3500.4 | 37.2 | 51.6 | 2920.8 | 3691.9 | 64.8 | 9.3 | "/lb | 2 | 4.125 | 1.625 | 10 | 0 | Raw | 14.3 | 7.22 | ef.turb.1 | 0.039 | ef.turb.2 | x | Pres. | 513393000 | 288571680 | 172482000
| Prev | 208134000 | 1929390 | 4565130 | 7245290 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1227938000 |  |  |  | prev | 2776.2 | 3500.4 | 37.2 | 51.5 | 2910.2 | 3691.9 | 64.8 | 9.3 | Lbs. | 21.48 | 9.075 | 0.40625 | 10 |  | Trtd | 14.9 | 7.71 | AC.1 | 0.381 | AC.2 | x | Prev. | 512462000 | 288571680 | 172482000
| Total | 846000 | 9000 | 0 | 8000 | 0 | 0 | 0 | 0 |  |  |  | Total | 824300 |  |  |  | Total | 10.4 | 0 | 0 | 0.1 | 10.6 | 0 | 0 | 0 | mg/L | 3.0444 | 1.2862 | 0.057578 | 1.4173 |  |  |  |  | Raw.Trb. | 1.05 | Cmb.Trb. | 0.025 | Total | 931000 | 0 | 0
6 | Pres. | 209908000 | 1948390 | 4598130 | 7273280 | 257409000 | 2223430 | 6875490 | 11545500 | 928000 | 62990 | 990990 | now | 1229584500 |  | 0 | 0.97 | now | 2798.1 | 3500.4 | 37.2 | 51.7 | 2932.7 | 3691.9 | 64.9 | 9.4 | "/lb | 3 | 4.625 | 1.875 | 11 | 0 | Raw | 13.5 | 7.34 | ef.turb.1 | 0.039 | ef.turb.2 | x | Pres. | 514427000 | 288571680 | 172518000
| Prev | 208980000 | 1938390 | 4565130 | 7253290 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1228762300 |  |  |  | prev | 2786.6 | 3500.4 | 37.2 | 51.6 | 2920.8 | 3691.9 | 64.8 | 9.3 | Lbs. | 32.22 | 10.175 | 0.46875 | 11 |  | Trtd | 15 | 7.57 | AC.1 | 0.515 | AC.2 | x | Prev. | 513393000 | 288571680 | 172482000
| Total | 928000 | 10000 | 33000 | 19990 | 0 | 0 | 0 | 0 |  |  |  | Total | 822200 |  |  |  | Total | 11.5 | 0 | 0 | 0.1 | 11.9 | 0 | 0.1 | 0.1 | mg/L | 4.163 | 1.3147 | 0.060566 | 1.4213 |  |  |  |  | Raw.Trb. | 1.77 | Cmb.Trb. | 0.025 | Total | 1034000 | 0 | 36000
7 | Pres. | 210620000 | 1948390 | 4598130 | 7290280 | 257409000 | 2223430 | 6875490 | 11545500 | 712000 | 17000 | 729000 | now | 1230395500 |  | 0 | 1.03 | now | 2806.9 | 3500.4 | 37.2 | 51.7 | 2941.7 | 3691.9 | 64.9 | 9.4 | "/lb | 1.75 | 3.375 | 1.375 | 9 | 0 | Raw | 12.8 | 7.34 | ef.turb.1 | 0.039 | ef.turb.2 | x | Pres. | 515210000 | 288571680 | 172518000
| Prev | 209908000 | 1948390 | 4598130 | 7273280 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1229584500 |  |  |  | prev | 2798.1 | 3500.4 | 37.2 | 51.7 | 2932.7 | 3691.9 | 64.9 | 9.4 | Lbs. | 18.795 | 7.425 | 0.34375 | 9 |  | Trtd | 14.2 | 7.67 | AC.1 | 0.367 | AC.2 | x | Prev. | 514427000 | 288571680 | 172518000
| Total | 712000 | 0 | 0 | 17000 | 0 | 0 | 0 | 0 |  |  |  | Total | 811000 |  |  |  | Total | 8.8 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | mg/L | 3.1652 | 1.2504 | 0.057889 | 1.5156 |  |  |  |  | Raw.Trb. | 1.14 | Cmb.Trb. | 0.025 | Total | 783000 | 0 | 0
8 | Pres. | 211503000 | 1950390 | 4630130 | 7309280 | 257409000 | 2223430 | 6875490 | 11545500 | 883000 | 53000 | 936000 | now | 1231248000 |  | 0 | 1.03 | now | 2817.8 | 3500.4 | 37.2 | 51.8 | 2953 | 3691.9 | 65.1 | 9.5 | "/lb | 2.375 | 4.125 | 2 | 11 | 0 | Raw | 12.7 | 7.4 | ef.turb.1 | 0.039 | ef.turb.2 | x | Pres. | 516190000 | 288571680 | 172518000
| Prev | 210620000 | 1948390 | 4598130 | 7290280 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1230395500 |  |  |  | prev | 2806.9 | 3500.4 | 37.2 | 51.7 | 2941.7 | 3691.9 | 64.9 | 9.4 | Lbs. | 25.5075 | 9.075 | 0.5 | 11 |  | Trtd | 14 | 7.78 | AC.1 | 0.292 | AC.2 | x | Prev. | 515210000 | 288571680 | 172518000
| Total | 883000 | 2000 | 32000 | 19000 | 0 | 0 | 0 | 0 |  |  |  | Total | 852500 |  |  |  | Total | 10.9 | 0 | 0 | 0.1 | 11.3 | 0 | 0.2 | 0.1 | mg/L | 3.4637 | 1.2323 | 0.067896 | 1.4937 |  |  |  |  | Raw.Trb. | 1.06 | Cmb.Trb. | 0.024 | Total | 980000 | 0 | 0
9 | Pres. | 212353000 | 1967390 | 4630130 | 7318280 | 257409000 | 2223430 | 6875490 | 11545500 | 850000 | 26000 | 876000 | now | 1232085200 |  | 0.08 | 0.94 | now | 2828.3 | 3500.4 | 37.2 | 51.9 | 2963.7 | 3691.9 | 65.1 | 9.5 | "/lb | 2 | 4.125 | 1.5 | 10 | 0 | Raw | 13.7 | 7.48 | ef.turb.1 | 0.049 | ef.turb.2 | x | Pres. | 517129000 | 288571680 | 172554000
| Prev | 211503000 | 1950390 | 4630130 | 7309280 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1231248000 |  |  |  | prev | 2817.8 | 3500.4 | 37.2 | 51.8 | 2953 | 3691.9 | 65.1 | 9.5 | Lbs. | 21.48 | 9.075 | 0.375 | 10 |  | Trtd | 12.1 | 8.08 | AC.1 | 0.21 | AC.2 | x | Prev. | 516190000 | 288571680 | 172518000
| Total | 850000 | 17000 | 0 | 9000 | 0 | 0 | 0 | 0 |  |  |  | Total | 837200 |  |  |  | Total | 10.5 | 0 | 0 | 0.1 | 10.7 | 0 | 0 | 0 | mg/L | 3.03 | 1.2802 | 0.052899 | 1.4106 |  |  |  |  | Raw.Trb. | 1.12 | Cmb.Trb. | 0.03 | Total | 939000 | 0 | 36000
10 | Pres. | 213304000 | 1977390 | 4662130 | 7338280 | 257409000 | 2223430 | 6875490 | 11545500 | 951000 | 62000 | 1013000 | now | 1232742600 |  | 0.05 | 0.96 | now | 2840 | 3500.4 | 37.2 | 52.1 | 2975.9 | 3691.9 | 65.3 | 9.5 | "/lb | 2.375 | 5.5 | 1.75 | 11 | 0 | Raw | 13.6 | 7.95 | ef.turb.1 | 0.04 | ef.turb.2 | x | Pres. | 518189000 | 288571680 | 172554000
| Prev | 212353000 | 1967390 | 4630130 | 7318280 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1232085200 |  |  |  | prev | 2828.3 | 3500.4 | 37.2 | 51.9 | 2963.7 | 3691.9 | 65.1 | 9.5 | Lbs. | 25.5075 | 12.1 | 0.4375 | 11 |  | Trtd | 12.5 | 8.01 | AC.1 | 0.401 | AC.2 | x | Prev. | 517129000 | 288571680 | 172554000
| Total | 951000 | 10000 | 32000 | 20000 | 0 | 0 | 0 | 0 |  |  |  | Total | 657400 |  |  |  | Total | 11.7 | 0 | 0 | 0.2 | 12.2 | 0 | 0.2 | 0 | mg/L | 3.216 | 1.5256 | 0.055161 | 1.3869 |  |  |  |  | Raw.Trb. | 1.06 | Cmb.Trb. | 0.027 | Total | 1060000 | 0 | 0
11 | Pres. | 213910000 | 1977390 | 4662130 | 7355280 | 257409000 | 2223430 | 6875490 | 11545500 | 606000 | 17000 | 623000 | now | 1233560000 |  | 0.01 | 0.99 | now | 2847.5 | 3500.4 | 37.2 | 52.1 | 2983.6 | 3691.9 | 65.3 | 9.5 | "/lb | 1.75 | 3 | 1.25 | 6 | 0 | Raw | 13.4 | 7.51 | ef.turb.1 | 0.04 | ef.turb.2 | x | Pres. | 518862000 | 288571680 | 172589000
| Prev | 213304000 | 1977390 | 4662130 | 7338280 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1232742600 |  |  |  | prev | 2840 | 3500.4 | 37.2 | 52.1 | 2975.9 | 3691.9 | 65.3 | 9.5 | Lbs. | 18.795 | 6.6 | 0.3125 | 6 |  | Trtd | 12.7 | 7.95 | AC.1 | 0.47 | AC.2 | x | Prev. | 518189000 | 288571680 | 172554000
| Total | 606000 | 0 | 0 | 17000 | 0 | 0 | 0 | 0 |  |  |  | Total | 817400 |  |  |  | Total | 7.5 | 0 | 0 | 0 | 7.7 | 0 | 0 | 0 | mg/L | 3.7188 | 1.3059 | 0.061832 | 1.1872 |  |  |  |  | Raw.Trb. | 1.15 | Cmb.Trb. | 0.028 | Total | 673000 | 0 | 35000
12 | Pres. | 214701000 | 1986390 | 4662130 | 7363280 | 257409000 | 2223430 | 6875490 | 11545500 | 791000 | 17000 | 808000 | now | 1234347700 |  | 0.07 | 1 | now | 2857.1 | 3500.4 | 37.2 | 52.2 | 2993.5 | 3691.9 | 65.3 | 9.5 | "/lb | 1.9375 | 3.75 | 1.5 | 9 | 0 | Raw | 12.3 | 7.5 | ef.turb.1 | 0.038 | ef.turb.2 | x | Pres. | 519740000 | 288571680 | 172589000
| Prev | 213910000 | 1977390 | 4662130 | 7355280 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1233560000 |  |  |  | prev | 2847.5 | 3500.4 | 37.2 | 52.1 | 2983.6 | 3691.9 | 65.3 | 9.5 | Lbs. | 20.8087 | 8.25 | 0.375 | 9 |  | Trtd | 12.6 | 7.96 | AC.1 | 0.302 | AC.2 | x | Prev. | 518862000 | 288571680 | 172589000
| Total | 791000 | 9000 | 0 | 8000 | 0 | 0 | 0 | 0 |  |  |  | Total | 787700 |  |  |  | Total | 9.6 | 0 | 0 | 0.1 | 9.9 | 0 | 0 | 0 | mg/L | 3.1543 | 1.2506 | 0.056845 | 1.3643 |  |  |  |  | Raw.Trb. | 1.09 | Cmb.Trb. | 0.023 | Total | 878000 | 0 | 0
13 | Pres. | 215519000 | 1996390 | 4695120 | 7384280 | 257409000 | 2223430 | 6875490 | 11545500 | 818000 | 63990 | 881990 | now | 1235110900 |  | 0.2 | 0.99 | now | 2867.3 | 3500.4 | 37.2 | 52.3 | 3004 | 3691.9 | 65.4 | 9.6 | "/lb | 2 | 4 | 1.5 | 9 | 0 | Raw | 11.2 | 7.37 | ef.turb.1 | 0.039 | ef.turb.2 | x | Pres. | 520652000 | 288571680 | 172625000
| Prev | 214701000 | 1986390 | 4662130 | 7363280 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1234347700 |  |  |  | prev | 2857.1 | 3500.4 | 37.2 | 52.2 | 2993.5 | 3691.9 | 65.3 | 9.5 | Lbs. | 21.48 | 8.8 | 0.375 | 9 |  | Trtd | 12.3 | 7.72 | AC.1 | 0.405 | AC.2 | x | Prev. | 519740000 | 288571680 | 172589000
| Total | 818000 | 10000 | 32990 | 21000 | 0 | 0 | 0 | 0 |  |  |  | Total | 763200 |  |  |  | Total | 10.2 | 0 | 0 | 0.1 | 10.5 | 0 | 0.1 | 0.1 | mg/L | 3.1486 | 1.2899 | 0.054968 | 1.3192 |  |  |  |  | Raw.Trb. | 1.03 | Cmb.Trb. | 0.023 | Total | 912000 | 0 | 36000
14 | Pres. | 216323000 | 1996390 | 4727120 | 7404280 | 257409000 | 2223430 | 6875490 | 11545500 | 804000 | 52000 | 856000 | now | 1235892900 |  | 0 | 0.95 | now | 2877.1 | 3500.4 | 37.2 | 52.3 | 3014.1 | 3691.9 | 65.6 | 9.7 | "/lb | 2.25 | 4 | 1.625 | 10 | 0 | Raw | 11 | 7.36 | ef.turb.1 | 0.032 | ef.turb.2 | x | Pres. | 521544000 | 288571680 | 172661000
| Prev | 215519000 | 1996390 | 4695120 | 7384280 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1235110900 |  |  |  | prev | 2867.3 | 3500.4 | 37.2 | 52.3 | 3004 | 3691.9 | 65.4 | 9.6 | Lbs. | 24.165 | 8.8 | 0.40625 | 10 |  | Trtd | 12 | 7.8 | AC.1 | 0.598 | AC.2 | x | Prev. | 520652000 | 288571680 | 172625000
| Total | 804000 | 0 | 32000 | 20000 | 0 | 0 | 0 | 0 |  |  |  | Total | 782000 |  |  |  | Total | 9.8 | 0 | 0 | 0 | 10.1 | 0 | 0.2 | 0.1 | mg/L | 3.6038 | 1.3124 | 0.060586 | 1.4913 |  |  |  |  | Raw.Trb. | 1.17 | Cmb.Trb. | 0.037 | Total | 892000 | 0 | 36000
15 | Pres. | 217112000 | 2006390 | 4727120 | 7412270 | 257409000 | 2223430 | 6875490 | 11545500 | 789000 | 17990 | 806990 | now | 1236704500 |  | 0 | 0.94 | now | 2886.8 | 3500.4 | 37.2 | 52.4 | 3024 | 3691.9 | 65.6 | 9.7 | "/lb | 1.9375 | 3.9375 | 1.625 | 10 | 0 | Raw | 11.8 | 7.29 | ef.turb.1 | 0.04 | ef.turb.2 | x | Pres. | 522414000 | 288571680 | 172661000
| Prev | 216323000 | 1996390 | 4727120 | 7404280 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1235892900 |  |  |  | prev | 2877.1 | 3500.4 | 37.2 | 52.3 | 3014.1 | 3691.9 | 65.6 | 9.7 | Lbs. | 20.8087 | 8.6625 | 0.40625 | 10 |  | Trtd | 12.2 | 7.74 | AC.1 | 0.322 | AC.2 | x | Prev. | 521544000 | 288571680 | 172661000
| Total | 789000 | 10000 | 0 | 7990 | 0 | 0 | 0 | 0 |  |  |  | Total | 811600 |  |  |  | Total | 9.7 | 0 | 0 | 0.1 | 9.9 | 0 | 0 | 0 | mg/L | 3.1623 | 1.3164 | 0.061738 | 1.5197 |  |  |  |  | Raw.Trb. | 1.21 | Cmb.Trb. | 0.026 | Total | 870000 | 0 | 0
16 | Pres. | 217875000 | 2006390 | 4759120 | 7433270 | 257409000 | 2223430 | 6875490 | 11545500 | 763000 | 53000 | 816000 | now | 1237377800 |  | 0 | 1.03 | now | 2896.1 | 3500.4 | 37.2 | 52.4 | 3033.6 | 3691.9 | 65.7 | 9.7 | "/lb | 1.875 | 3.9375 | 1.5 | 10 | 0 | Raw | 12.1 | 7.31 | ef.turb.1 | 0.04 | ef.turb.2 | x | Pres. | 523259000 | 288571680 | 172696000
| Prev | 217112000 | 2006390 | 4727120 | 7412270 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1236704500 |  |  |  | prev | 2886.8 | 3500.4 | 37.2 | 52.4 | 3024 | 3691.9 | 65.6 | 9.7 | Lbs. | 20.1375 | 8.6625 | 0.375 | 10 |  | Trtd | 11.9 | 7.85 | AC.1 | 0.385 | AC.2 | x | Prev. | 522414000 | 288571680 | 172661000
| Total | 763000 | 0 | 32000 | 21000 | 0 | 0 | 0 | 0 |  |  |  | Total | 673300 |  |  |  | Total | 9.3 | 0 | 0 | 0 | 9.6 | 0 | 0.1 | 0 | mg/L | 3.1646 | 1.3613 | 0.058931 | 1.5715 |  |  |  |  | Raw.Trb. | 1.01 | Cmb.Trb. | 0.026 | Total | 845000 | 0 | 35000
17 | Pres. | 218609000 | 2016390 | 4759120 | 7441270 | 257409000 | 2223430 | 6875490 | 11545500 | 734000 | 18000 | 752000 | now | 1238179800 |  | 0.23 | 0.94 | now | 2905.1 | 3500.4 | 37.2 | 52.5 | 3042.8 | 3691.9 | 65.7 | 9.7 | "/lb | 1.75 | 3.5 | 1.375 | 9 | 0 | Raw | 11.7 | 7.37 | ef.turb.1 | 0.043 | ef.turb.2 | x | Pres. | 524074000 | 288571680 | 172712000
| Prev | 217875000 | 2006390 | 4759120 | 7433270 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1237377800 |  |  |  | prev | 2896.1 | 3500.4 | 37.2 | 52.4 | 3033.6 | 3691.9 | 65.7 | 9.7 | Lbs. | 18.795 | 7.7 | 0.34375 | 9 |  | Trtd | 12.1 | 7.76 | AC.1 | 0.215 | AC.2 | x | Prev. | 523259000 | 288571680 | 172696000
| Total | 734000 | 10000 | 0 | 8000 | 0 | 0 | 0 | 0 |  |  |  | Total | 802000 |  |  |  | Total | 9 | 0 | 0 | 0.1 | 9.2 | 0 | 0 | 0 | mg/L | 3.0703 | 1.2578 | 0.056154 | 1.4702 |  |  |  |  | Raw.Trb. | 1.06 | Cmb.Trb. | 0.057 | Total | 815000 | 0 | 16000
18 | Pres. | 218609000 | 2016390 | 4759120 | 7441270 | 258330000 | 2232430 | 6907490 | 11595600 | 921000 | 91100 | 1012100 | now | 1238948800 |  | 0 | 1.04 | now | 2905.1 | 3511.3 | 37.2 | 52.6 | 3042.8 | 3704.1 | 65.7 | 9.7 | "/lb | 2.75 | 4.5 | 1.9375 | 0 | 11 | Raw | 12.3 | 7.54 | ef.turb.1 | 0.04 | ef.turb.2 | x | Pres. | 524074000 | 289655500 | 172731000
| Prev | 218609000 | 2016390 | 4759120 | 7441270 | 257409000 | 2223430 | 6875490 | 11545500 |  |  |  | prev | 1238179800 |  |  |  | prev | 2905.1 | 3500.4 | 37.2 | 52.5 | 3042.8 | 3691.9 | 65.7 | 9.7 | Lbs. | 29.535 | 9.9 | 0.48438 | 11 |  | Trtd | 12.1 | 8.13 | AC.1 | 0.39 | AC.2 | x | Prev. | 524074000 | 288571680 | 172712000
| Total | 0 | 0 | 0 | 0 | 921000 | 9000 | 32000 | 50100 |  |  |  | Total | 769000 |  |  |  | Total | 0 | 10.9 | 0 | 0.1 | 0 | 12.2 | 0 | 0 | mg/L | 3.8451 | 1.2889 | 0.06306 | 1.4321 |  |  |  |  | Raw.Trb. | 1.18 | Cmb.Trb. | 0.024 | Total | 0 | 1083820 | 19000
19 | Pres. | 218609000 | 2016390 | 4759120 | 7441270 | 258953000 | 2241430 | 6939490 | 11624600 | 623000 | 70000 | 693000 | now | 1239711600 |  | 0.09 | 1.02 | now | 2905.1 | 3518.9 | 37.4 | 52.8 | 3042.8 | 3712.2 | 66.1 | 9.7 | "/lb | 1.75 | 3 | 1.125 | 0 | 7 | Raw | 12.1 | 7.44 | ef.turb.1 | x | ef.turb.2 | 0.044 | Pres. | 524074000 | 290355900 | 172766000
| Prev | 218609000 | 2016390 | 4759120 | 7441270 | 258330000 | 2232430 | 6907490 | 11595600 |  |  |  | prev | 1238948800 |  |  |  | prev | 2905.1 | 3511.3 | 37.2 | 52.6 | 3042.8 | 3704.1 | 65.7 | 9.7 | Lbs. | 18.795 | 6.6 | 0.28125 | 7 |  | Trtd | 12.9 | 7.76 | AC.1 | x | AC.2 | 0.355 | Prev. | 524074000 | 289655500 | 172731000
| Total | 0 | 0 | 0 | 0 | 623000 | 9000 | 32000 | 29000 |  |  |  | Total | 762800 |  |  |  | Total | 0 | 7.6 | 0.2 | 0.2 | 0 | 8.1 | 0.4 | 0 | mg/L | 3.6173 | 1.2703 | 0.05413 | 1.3472 |  |  |  |  | Raw.Trb. | 1.03 | Cmb.Trb. | 0.025 | Total | 0 | 700400 | 35000
20 | Pres. | 218609000 | 2016390 | 4759120 | 7441270 | 259959000 | 2250430 | 6939490 | 11640600 | 1006000 | 25000 | 1031000 | now | 1240509900 |  | 0.03 | 1.01 | now | 2905.1 | 3531.2 | 37.4 | 52.9 | 3042.8 | 3724.7 | 66.1 | 9.7 | "/lb | 2.375 | 4.9375 | 2 | 0 | 12 | Raw | 12.8 | 7.48 | ef.turb.1 | x | ef.turb.2 | 0.046 | Pres. | 524074000 | 291439500 | 172766000
| Prev | 218609000 | 2016390 | 4759120 | 7441270 | 258953000 | 2241430 | 6939490 | 11624600 |  |  |  | prev | 1239711600 |  |  |  | prev | 2905.1 | 3518.9 | 37.4 | 52.8 | 3042.8 | 3712.2 | 66.1 | 9.7 | Lbs. | 25.5075 | 10.8625 | 0.5 | 12 |  | Trtd | 13.3 | 7.71 | AC.1 | x | AC.2 | 0.427 | Prev. | 524074000 | 290355900 | 172766000
| Total | 0 | 0 | 0 | 0 | 1006000 | 9000 | 0 | 16000 |  |  |  | Total | 798300 |  |  |  | Total | 0 | 12.3 | 0 | 0.1 | 0 | 12.5 | 0 | 0 | mg/L | 3.0402 | 1.2947 | 0.059594 | 1.4303 |  |  |  |  | Raw.Trb. | 1.01 | Cmb.Trb. | 0.026 | Total | 0 | 1083600 | 0
21 | Pres. | 218609000 | 2016390 | 4759120 | 7441270 | 260508000 | 2259430 | 6971490 | 11675600 | 549000 | 76000 | 625000 | now | 1241193900 |  | 0.81 | 0.97 | now | 2905.1 | 3538.4 | 37.6 | 52.9 | 3042.8 | 3732.4 | 66.3 | 9.7 | "/lb | 1.5 | 2.9375 | 1.25 | 0 | 7 | Raw | 13.5 | 7.37 | ef.turb.1 | x | ef.turb.2 | 0.053 | Pres. | 524074000 | 292068200 | 172801000
| Prev | 218609000 | 2016390 | 4759120 | 7441270 | 259959000 | 2250430 | 6939490 | 11640600 |  |  |  | prev | 1240509900 |  |  |  | prev | 2905.1 | 3531.2 | 37.4 | 52.9 | 3042.8 | 3724.7 | 66.1 | 9.7 | Lbs. | 16.11 | 6.4625 | 0.3125 | 7 |  | Trtd | 12.7 | 7.85 | AC.1 | x | AC.2 | 0.459 | Prev. | 524074000 | 291439500 | 172766000
| Total | 0 | 0 | 0 | 0 | 549000 | 9000 | 32000 | 35000 |  |  |  | Total | 684000 |  |  |  | Total | 0 | 7.2 | 0.2 | 0 | 0 | 7.7 | 0.2 | 0 | mg/L | 3.5185 | 1.4114 | 0.068251 | 1.5288 |  |  |  |  | Raw.Trb. | 1.09 | Cmb.Trb. | 0.026 | Total | 0 | 628700 | 35000
22 | Pres. | 218609000 | 2016390 | 4759120 | 7441270 | 261154000 | 2268430 | 7003490 | 11715600 | 646000 | 81000 | 727000 | now | 1242053200 |  | 0.11 | 0.91 | now | 2905.1 | 3547.3 | 37.7 | 53.1 | 3042.9 | 3741.9 | 66.4 | 9.7 | "/lb | 3.875 | 4 | 1.375 | 10 | 0 | Raw | 14 | 7.37 | ef.turb.1 | x | ef.turb.2 | 0.048 | Pres. | 524074000 | 292809250 | 172836000
| Prev | 218609000 | 2016390 | 4759120 | 7441270 | 260508000 | 2259430 | 6971490 | 11675600 |  |  |  | prev | 1241193900 |  |  |  | prev | 2905.1 | 3538.4 | 37.6 | 52.9 | 3042.8 | 3732.4 | 66.3 | 9.7 | Lbs. | 41.6175 | 8.8 | 0.34375 | 10 |  | Trtd | 13.2 | 7.85 | AC.1 | x | AC.2 | 0.526 | Prev. | 524074000 | 292068200 | 172801000
| Total | 0 | 0 | 0 | 0 | 646000 | 9000 | 32000 | 40000 |  |  |  | Total | 859300 |  |  |  | Total | 0 | 8.9 | 0.1 | 0.2 | 0.1 | 9.5 | 0.1 | 0 | mg/L | 7.7246 | 1.6334 | 0.063803 | 1.8561 |  |  |  |  | Raw.Trb. | 3.65 | Cmb.Trb. | 0.029 | Total | 0 | 741050 | 35000
23 | Pres. | 218609000 | 2016390 | 4759120 | 7441270 | 261970000 | 2277430 | 7003490 | 11723600 | 816000 | 17000 | 833000 | now | 1242828600 |  | 0.33 | 0.98 | now | 2905.1 | 3557.7 | 37.7 | 53.2 | 3042.9 | 3752.6 | 66.4 | 9.7 | "/lb | 3.25 | 4 | 1.625 | 10 | 0 | Raw | 10 | 7.39 | ef.turb.1 | x | ef.turb.2 | 0.05 | Pres. | 524074000 | 293687900 | 172836000
| Prev | 218609000 | 2016390 | 4759120 | 7441270 | 261154000 | 2268430 | 7003490 | 11715600 |  |  |  | prev | 1242053200 |  |  |  | prev | 2905.1 | 3547.3 | 37.7 | 53.1 | 3042.9 | 3741.9 | 66.4 | 9.7 | Lbs. | 34.905 | 8.8 | 0.40625 | 10 |  | Trtd | 11.9 | 7.85 | AC.1 | x | AC.2 | 0.88 | Prev. | 524074000 | 292809250 | 172836000
| Total | 0 | 0 | 0 | 0 | 816000 | 9000 | 0 | 8000 |  |  |  | Total | 775400 |  |  |  | Total | 0 | 10.4 | 0 | 0.1 | 0 | 10.7 | 0 | 0 | mg/L | 5.129 | 1.2931 | 0.059695 | 1.4694 |  |  |  |  | Raw.Trb. | 1.03 | Cmb.Trb. | 0.024 | Total | 0 | 878650 | 0
24 | Pres. | 218609000 | 2016390 | 4759120 | 7441270 | 262746000 | 2286430 | 7035480 | 11741600 | 776000 | 58990 | 834990 | now | 1243536400 |  | 0.27 | 0.93 | now | 2905.1 | 3567.9 | 37.7 | 53.3 | 3042.9 | 3762.9 | 66.4 | 9.7 | "/lb | 2.75 | 3.5 | 1.625 | 9 | 0 | Raw | 10.6 | 7.39 | ef.turb.1 | x | ef.turb.2 | 0.05 | Pres. | 524074000 | 294538700 | 172871000
| Prev | 218609000 | 2016390 | 4759120 | 7441270 | 261970000 | 2277430 | 7003490 | 11723600 |  |  |  | prev | 1242828600 |  |  |  | prev | 2905.1 | 3557.7 | 37.7 | 53.2 | 3042.9 | 3752.6 | 66.4 | 9.7 | Lbs. | 29.535 | 7.7 | 0.40625 | 9 |  | Trtd | 11.8 | 7.81 | AC.1 | x | AC.2 | 0.62 | Prev. | 524074000 | 293687900 | 172836000
| Total | 0 | 0 | 0 | 0 | 776000 | 9000 | 31990 | 18000 |  |  |  | Total | 707800 |  |  |  | Total | 0 | 10.2 | 0 | 0.1 | 0 | 10.3 | 0 | 0 | mg/L | 4.5636 | 1.1898 | 0.062772 | 1.3906 |  |  |  |  | Raw.Trb. | 2.15 | Cmb.Trb. | 0.024 | Total | 0 | 850800 | 35000
25 | Pres. | 219220000 | 2025390 | 4792120 | 7476270 | 262878000 | 2286430 | 7035480 | 11741600 | 743000 | 77000 | 820000 | now | 1244315900 |  | 0.07 | 0.92 | now | 2913.1 | 3569.4 | 38 | 53.3 | 3051.4 | 3764.6 | 66.8 | 9.8 | "/lb | 2.5 | 3.9375 | 1.5 | 7 | 1 | Raw | 12.1 | 7.38 | ef.turb.1 | x | ef.turb.2 | 0.047 | Pres. | 524767000 | 294675800 | 172907000
| Prev | 218609000 | 2016390 | 4759120 | 7441270 | 262746000 | 2286430 | 7035480 | 11741600 |  |  |  | prev | 1243536400 |  |  |  | prev | 2905.1 | 3567.9 | 37.7 | 53.3 | 3042.9 | 3762.9 | 66.4 | 9.7 | Lbs. | 26.85 | 8.6625 | 0.375 | 8 |  | Trtd | 11.9 | 7.73 | AC.1 | x | AC.2 | 1.19 | Prev. | 524074000 | 294538700 | 172871000
| Total | 611000 | 9000 | 33000 | 35000 | 132000 | 0 | 0 | 0 |  |  |  | Total | 779500 |  |  |  | Total | 8 | 1.5 | 0.3 | 0 | 8.5 | 1.7 | 0.4 | 0.1 | mg/L | 4.333 | 1.3979 | 0.060517 | 1.291 |  |  |  |  | Raw.Trb. | 6.18 | Cmb.Trb. | 0.029 | Total | 693000 | 137100 | 36000
26 | Pres. | 219978000 | 2035390 | 4824120 | 7496270 | 262878000 | 2286430 | 7035480 | 11741600 | 758000 | 62000 | 820000 | now | 1245057100 |  | 0.21 | 0.97 | now | 2922.8 | 3569.4 | 38.1 | 53.3 | 3061.5 | 3764.6 | 66.9 | 9.8 | "/lb | 2.625 | 3.75 | 1.5 | 9 | 0 | Raw | 12.9 | 7.29 | ef.turb.1 | 0.045 | ef.turb.2 | x | Pres. | 525630000 | 294675800 | 172943000
| Prev | 219220000 | 2025390 | 4792120 | 7476270 | 262878000 | 2286430 | 7035480 | 11741600 |  |  |  | prev | 1244315900 |  |  |  | prev | 2913.1 | 3569.4 | 38 | 53.3 | 3051.4 | 3764.6 | 66.8 | 9.8 | Lbs. | 28.1925 | 8.25 | 0.375 | 9 |  | Trtd | 12.2 | 7.72 | AC.1 | 0.878 | AC.2 | x | Prev. | 524767000 | 294675800 | 172907000
| Total | 758000 | 10000 | 32000 | 20000 | 0 | 0 | 0 | 0 |  |  |  | Total | 741200 |  |  |  | Total | 9.7 | 0 | 0.1 | 0 | 10.1 | 0 | 0.1 | 0 | mg/L | 4.4596 | 1.305 | 0.059319 | 1.4237 |  |  |  |  | Raw.Trb. | 4.41 | Cmb.Trb. | 0.027 | Total | 863000 | 0 | 36000
27 | Pres. | 220742000 | 2054390 | 4824120 | 7504270 | 262878000 | 2286430 | 7035480 | 11741600 | 764000 | 27000 | 791000 | now | 1245818800 |  | 0.04 | 0.97 | now | 2932.5 | 3569.4 | 38.3 | 53.3 | 3071.7 | 3764.6 | 66.9 | 9.8 | "/lb | 2.875 | 3.9375 | 1.5 | 9 | 0 | Raw | 13 | 7.24 | ef.turb.1 | 0.045 | ef.turb.2 | x | Pres. | 526483000 | 294675800 | 172943000
| Prev | 219978000 | 2035390 | 4824120 | 7496270 | 262878000 | 2286430 | 7035480 | 11741600 |  |  |  | prev | 1245057100 |  |  |  | prev | 2922.8 | 3569.4 | 38.1 | 53.3 | 3061.5 | 3764.6 | 66.9 | 9.8 | Lbs. | 30.8775 | 8.6625 | 0.375 | 9 |  | Trtd | 12.9 | 7.61 | AC.1 | 1.545 | AC.2 | x | Prev. | 525630000 | 294675800 | 172943000
| Total | 764000 | 19000 | 0 | 8000 | 0 | 0 | 0 | 0 |  |  |  | Total | 761700 |  |  |  | Total | 9.7 | 0 | 0.2 | 0 | 10.2 | 0 | 0 | 0 | mg/L | 4.846 | 1.3595 | 0.058853 | 1.4125 |  |  |  |  | Raw.Trb. | 8.59 | Cmb.Trb. | 0.028 | Total | 853000 | 0 | 0
28 | Pres. | 221597000 | 2063390 | 4857110 | 7527270 | 262878000 | 2286430 | 7035480 | 11741600 | 855000 | 64990 | 919990 | now | 1246596900 |  | 0.86 | 1.04 | now | 2943.4 | 3569.4 | 38.4 | 53.3 | 3083 | 3764.6 | 67.1 | 9.9 | "/lb | 2.5 | 4.5 | 1.75 | 10 | 0 | Raw | 13.3 | 7.33 | ef.turb.1 | 0.048 | ef.turb.2 | x | Pres. | 527448000 | 294675800 | 172978000
| Prev | 220742000 | 2054390 | 4824120 | 7504270 | 262878000 | 2286430 | 7035480 | 11741600 |  |  |  | prev | 1245818800 |  |  |  | prev | 2932.5 | 3569.4 | 38.3 | 53.3 | 3071.7 | 3764.6 | 66.9 | 9.8 | Lbs. | 26.85 | 9.9 | 0.4375 | 10 |  | Trtd | 13.1 | 7.58 | AC.1 | 0.726 | AC.2 | x | Prev. | 526483000 | 294675800 | 172943000
| Total | 855000 | 9000 | 32990 | 23000 | 0 | 0 | 0 | 0 |  |  |  | Total | 778100 |  |  |  | Total | 10.9 | 0 | 0.1 | 0 | 11.3 | 0 | 0.2 | 0.1 | mg/L | 3.7654 | 1.3884 | 0.061354 | 1.4024 |  |  |  |  | Raw.Trb. | 3.19 | Cmb.Trb. | 0.044 | Total | 965000 | 0 | 35000
29 | Pres. | 222401000 | 2073390 | 4890110 | 7561260 | 262878000 | 2286430 | 7035480 | 11741600 | 804000 | 76990 | 880990 | now | 1247378000 |  | 0 | 0.96 | now | 2953.6 | 3569.4 | 38.4 | 53.3 | 3093.8 | 3764.6 | 67.3 | 10 | "/lb | 3.75 | 4 | 2 | 10 | 0 | Raw | 14.4 | 7.29 | ef.turb.1 | 0.042 | ef.turb.2 | x | Pres. | 528352000 | 294675800 | 173015000
| Prev | 221597000 | 2063390 | 4857110 | 7527270 | 262878000 | 2286430 | 7035480 | 11741600 |  |  |  | prev | 1246596900 |  |  |  | prev | 2943.4 | 3569.4 | 38.4 | 53.3 | 3083 | 3764.6 | 67.1 | 9.9 | Lbs. | 40.275 | 8.8 | 0.5 | 10 |  | Trtd | 14 | 7.65 | AC.1 | 0.525 | AC.2 | x | Prev. | 527448000 | 294675800 | 172978000
| Total | 804000 | 10000 | 33000 | 33990 | 0 | 0 | 0 | 0 |  |  |  | Total | 781100 |  |  |  | Total | 10.2 | 0 | 0 | 0 | 10.8 | 0 | 0.2 | 0.1 | mg/L | 6.0064 | 1.3124 | 0.074567 | 1.4913 |  |  |  |  | Raw.Trb. | 3.11 | Cmb.Trb. | 0.026 | Total | 904000 | 0 | 37000
30 | Pres. | 223235000 | 2082390 | 4890110 | 7569260 | 262878000 | 2286430 | 7035480 | 11741600 | 834000 | 17000 | 851000 | now | 1248204000 |  | 0 | 1.01 | now | 2964.2 | 3569.4 | 38.7 | 53.3 | 3104.6 | 3764.6 | 67.3 | 10 | "/lb | 2.25 | 4.25 | 1.625 | 10 | 0 | Raw | 14.9 | 7.34 | ef.turb.1 | 0.05 | ef.turb.2 | x | Pres. | 529274000 | 294675800 | 173015000
| Prev | 222401000 | 2073390 | 4890110 | 7561260 | 262878000 | 2286430 | 7035480 | 11741600 |  |  |  | prev | 1247378000 |  |  |  | prev | 2953.6 | 3569.4 | 38.4 | 53.3 | 3093.8 | 3764.6 | 67.3 | 10 | Lbs. | 24.165 | 9.35 | 0.40625 | 10 |  | Trtd | 14.5 | 7.66 | AC.1 | 0.947 | AC.2 | x | Prev. | 528352000 | 294675800 | 173015000
| Total | 834000 | 9000 | 0 | 8000 | 0 | 0 | 0 | 0 |  |  |  | Total | 826000 |  |  |  | Total | 10.6 | 0 | 0.3 | 0 | 10.8 | 0 | 0 | 0 | mg/L | 3.4742 | 1.3442 | 0.058407 | 1.4377 |  |  |  |  | Raw.Trb. | 2.94 | Cmb.Trb. | 0.027 | Total | 922000 | 0 | 0
31 | Pres. | 224015000 | 2092390 | 4890110 | 7589260 | 262878000 | 2286430 | 7035480 | 11741600 | 780000 | 30000 | 810000 | now | 1248879400 |  | 0 | 1.03 | now | 2974.3 | 3569.4 | 38.7 | 53.3 | 3114.9 | 3764.6 | 67.4 | 10 | "/lb | 1.625 | 3.875 | 1.5 | 10 | 0 | Raw | 12.8 | 7.37 | ef.turb.1 | 0.042 | ef.turb.2 | x | Pres. | 530140000 | 294675800 | 173050000
| Prev | 223235000 | 2082390 | 4890110 | 7569260 | 262878000 | 2286430 | 7035480 | 11741600 |  |  |  | prev | 1248204000 |  |  |  | prev | 2964.2 | 3569.4 | 38.7 | 53.3 | 3104.6 | 3764.6 | 67.3 | 10 | Lbs. | 17.4525 | 8.525 | 0.375 | 10 |  | Trtd | 12.4 | 7.7 | AC.1 | 0.52 | AC.2 | x | Prev. | 529274000 | 294675800 | 173015000
| Total | 780000 | 10000 | 0 | 20000 | 0 | 0 | 0 | 0 |  |  |  | Total | 675400 |  |  |  | Total | 10.1 | 0 | 0 | 0 | 10.3 | 0 | 0.1 | 0 | mg/L | 2.6829 | 1.3105 | 0.057646 | 1.5372 |  |  |  |  | Raw.Trb. | 2.26 | Cmb.Trb. | 0.023 | Total | 866000 | 0 | 35000
[10 empty] | Totals | [6 empty] | AVG | [10 empty] | totals | [5 empty] | AVG TRTD |  |  |  | Avg.Cmb.Trb.
[10 empty] | 24887000 | 1401030 | 26288030 |  | 24343000 |  | 4.09 | 0.98677 | [5 empty] | 250.4 | 72.7 |  |  |  | 766.5675 | 275.275 | 12.625 | 302 |  |  | 13.0516 | 7.8003 |  |  | 0.027968
[22 empty] | total- | 323.1

## Nov, 2021
November, 2021
Filters | [15 empty] | Rain | Cl2 | Pump Hours | [8 empty] | Chemicals | [5 empty] | Misc. |  |  | Turbidity |  |  |  | Meters
Day |  | CW.Tot.1 | Cla.Wst.1 | BW.Wst.1 | FTWst.1 | CW.Tot.2 | Cla.Wst.2 | BW.Wst.2 | FTWst.2 | Treated Total | Wastewater | Total Influent | Totalizer |  |  | Inches | Resid | Pump | Ef.Pmp.1 | Ef.Pmp.2 | Blo.1 | Blo.2 | URT.1 | URT.2 | BWP | SWP | Chem | ACH | SA | Poly | Cl2.1 | Cl2.2 | water | Temp | pH | F1 |  | F2 |  |  | RM1 | RM2 | BWM
1 | Pres. | 224704000 | 2101390 | 4923110 | 7597260 | 262878000 | 2286430 | 7035480 | 11741600 | 689000 | 50000 | 739000 | now | 1249689000 |  | 0.15 | 1.05 | now | 2982.9 | 3569.4 | 38.9 | 53.3 | 3123.9 | 3764.6 | 67.4 | 10 | "/lb | 1.5 | 3.0625 | 1.25 | 8 | 0 | Raw | 8.5 | 7.25 | ef.turb.1 | 0.041 | ef.turb.2 | x | Pres. | 530909000 | 294675800 | 173050000
| Prev | 224015000 | 2092390 | 4890110 | 7589260 | 262878000 | 2286430 | 7035480 | 11741600 |  |  |  | prev | 1248879400 |  |  |  | prev | 2974.3 | 3569.4 | 38.7 | 53.3 | 3114.9 | 3764.6 | 67.4 | 10 | Lbs. | 16.11 | 6.7375 | 0.3125 | 8 |  | Trtd | 11.4 | 7.61 | AC.1 | 0.48 | AC.2 | x | Prev. | 530140000 | 294675800 | 173050000
| Total | 689000 | 9000 | 33000 | 8000 | 0 | 0 | 0 | 0 |  |  |  | Total | 809600 |  |  |  | Total | 8.6 | 0 | 0.2 | 0 | 9 | 0 | 0 | 0 | mg/L | 2.8036 | 1.1725 | 0.054383 | 1.3922 |  |  |  |  | Raw.Trb. | 2.15 | Cmb.Trb. | 0.024 | Total | 769000 | 0 | 0
3764.6
2 | Pres. | 225482000 | 2111390 | 4923110 | 7605260 | 262878000 | 2286430 | 7035480 | 11741600 | 778000 | 18000 | 796000 | now | 1250480500 |  | 0.03 | 1.03 | now | 2992.8 | 3569.4 | 39 | 53.3 | 3134 | 3764.6 | 67.4 | 10 | "/lb | 1.9375 | 3.9375 | 1.5625 | 9 | 0 | Raw | 11.9 | 7.34 | ef.turb.1 | 0.042 | ef.turb.2 | x | Pres. | 531759000 | 294675800 | 173050000
| Prev | 224704000 | 2101390 | 4923110 | 7597260 | 262878000 | 2286430 | 7035480 | 11741600 |  |  |  | prev | 1249689000 |  |  |  | prev | 2982.9 | 3569.4 | 38.9 | 53.3 | 3123.9 | 3764.6 | 67.4 | 10 | Lbs. | 20.8087 | 8.6625 | 0.39062 | 9 |  | Trtd | 12.2 | 7.65 | AC.1 | 0.575 | AC.2 | x | Prev. | 530909000 | 294675800 | 173050000
| Total | 778000 | 10000 | 0 | 8000 | 0 | 0 | 0 | 0 |  |  |  | Total | 791500 |  |  |  | Total | 9.9 | 0 | 0.1 | 0 | 10.1 | 0 | 0 | 0 | mg/L | 3.207 | 1.3351 | 0.060202 | 1.3871 |  |  |  |  | Raw.Trb. | 1.91 | Cmb.Trb. | 0.023 | Total | 850000 | 0 | 0
10.6
3 | Pres. | 225482000 | 2111390 | 4923110 | 7605260 | 263780000 | 2295430 | 7067480 | 11799600 | 902000 | 99000 | 1001000 | now | 1251253200 |  | 0.27 | 1.04 | now | 2992.8 | 3581.1 | 39 | 53.5 | 3134 | 3777.2 | 67.6 | 10 | "/lb | 2.125 | 4.875 | 1.9375 | 0 | 11 | Raw | 12.5 | 7.28 | ef.turb.1 | x | ef.turb.2 | 0.062 | Pres. | 531759000 | 295704900 | 173085000
| Prev | 225482000 | 2111390 | 4923110 | 7605260 | 262878000 | 2286430 | 7035480 | 11741600 |  |  |  | prev | 1250480500 |  |  |  | prev | 2992.8 | 3569.4 | 39 | 53.3 | 3134 | 3764.6 | 67.4 | 10 | Lbs. | 22.8225 | 10.725 | 0.48438 | 11 |  | Trtd | 12.2 | 7.59 | AC.1 | x | AC.2 | 0.49 | Prev. | 531759000 | 294675800 | 173050000
| Total | 0 | 0 | 0 | 0 | 902000 | 9000 | 32000 | 58000 |  |  |  | Total | 772700 |  |  |  | Total | 0 | 11.7 | 0 | 0.2 | 0 | 12.6 | 0.2 | 0 | mg/L | 3.0338 | 1.4257 | 0.064389 | 1.4622 |  |  |  |  | Raw.Trb. | 1.76 | Cmb.Trb. | 0.053 | Total | 0 | 1029100 | 35000
4 | Pres. | 225482000 | 2111390 | 4923110 | 7605260 | 264355000 | 2304430 | 7099480 | 11831600 | 575000 | 73000 | 648000 | now | 1252034200 |  | 0.32 | 1.01 | now | 2992.8 | 3588.6 | 39 | 53.7 | 3134 | 3785 | 67.8 | 10 | "/lb | 2.0625 | 3 | 1.25 | 0 | 7 | Raw | 13 | 7.27 | ef.turb.1 | x | ef.turb.2 | 0.045 | Pres. | 531759000 | 296357500 | 173120000
| Prev | 225482000 | 2111390 | 4923110 | 7605260 | 263780000 | 2295430 | 7067480 | 11799600 |  |  |  | prev | 1251253200 |  |  |  | prev | 2992.8 | 3581.1 | 39 | 53.5 | 3134 | 3777.2 | 67.6 | 10 | Lbs. | 22.1513 | 6.6 | 0.3125 | 7 |  | Trtd | 12.5 | 7.6 | AC.1 | x | AC.2 | 0.563 | Prev. | 531759000 | 295704900 | 173085000
| Total | 0 | 0 | 0 | 0 | 575000 | 9000 | 32000 | 32000 |  |  |  | Total | 781000 |  |  |  | Total | 0 | 7.5 | 0 | 0.2 | 0 | 7.8 | 0.2 | 0 | mg/L | 4.6192 | 1.3763 | 0.065165 | 1.4597 |  |  |  |  | Raw.Trb. | 1.95 | Cmb.Trb. | 0.023 | Total | 0 | 652600 | 35000
5 | Pres. | 225482000 | 2111390 | 4923110 | 7605260 | 265051000 | 2313420 | 7099480 | 11839700 | 696000 | 17090 | 713090 | now | 1252795500 | 0 | 0.19 | 0.96 | now | 2992.8 | 3597.5 | 39 | 53.8 | 3134 | 3794.2 | 67.8 | 10 | "/lb | 2.875 | 3.625 | 2.125 | 8 | 0 | Raw | 13.5 | 7.31 | ef.turb.1 | x | ef.turb.2 | 0.046 | Pres. | 531759000 | 297112600 | 173120000
| Prev | 225482000 | 2111390 | 4923110 | 7605260 | 264355000 | 2304430 | 7099480 | 11831600 |  |  |  | prev | 1252034200 |  |  |  | prev | 2992.8 | 3588.6 | 39 | 53.7 | 3134 | 3785 | 67.8 | 10 | Lbs. | 30.8775 | 7.975 | 0.53125 | 8 |  | Trtd | 12.6 | 7.65 | AC.1 | x | AC.2 | 0.699 | Prev. | 531759000 | 296357500 | 173120000
| Total | 0 | 0 | 0 | 0 | 696000 | 8990 | 0 | 8100 |  |  |  | Total | 761300 |  |  |  | Total | 0 | 8.9 | 0 | 0.1 | 0 | 9.2 | 0 | 0 | mg/L | 5.3195 | 1.3739 | 0.091522 | 1.3782 |  |  |  |  | Raw.Trb. | 2.89 | Cmb.Trb. | 0.024 | Total | 0 | 755100 | 0
6 | Pres. | 225482000 | 2111390 | 4923110 | 7605260 | 265901000 | 2322420 | 7131480 | 11879700 | 850000 | 81000 | 931000 | now | 1253645300 |  | 0.28 | 0.89 | now | 2992.8 | 3608.5 | 39.1 | 53.9 | 3134 | 3805.8 | 68 | 10 | "/lb | 3.5 | 4 | 1.75 | 10 | 0 | Raw | 10.9 | 7.21 | ef.turb.1 | x | ef.turb.2 | 0.05 | Pres. | 531759000 | 298062900 | 173155000
| Prev | 225482000 | 2111390 | 4923110 | 7605260 | 265051000 | 2313420 | 7099480 | 11839700 |  |  |  | prev | 1252795500 |  |  |  | prev | 2992.8 | 3597.5 | 39 | 53.8 | 3134 | 3794.2 | 67.8 | 10 | Lbs. | 37.59 | 8.8 | 0.4375 | 10 |  | Trtd | 11.6 | 7.63 | AC.1 | x | AC.2 | 0.46 | Prev. | 531759000 | 297112600 | 173120000
| Total | 0 | 0 | 0 | 0 | 850000 | 9000 | 32000 | 40000 |  |  |  | Total | 849800 |  |  |  | Total | 0 | 11 | 0.1 | 0.1 | 0 | 11.6 | 0.2 | 0 | mg/L | 5.3026 | 1.2414 | 0.061715 | 1.4106 |  |  |  |  | Raw.Trb. | 2.66 | Cmb.Trb. | 0.024 | Total | 0 | 950300 | 35000
7 | Pres. | 225482000 | 2111390 | 4923110 | 7605260 | 266752000 | 2331420 | 7131480 | 11896700 | 851000 | 26000 | 877000 | now | 1254476900 |  | 0.04 | 0.89 | now | 2992.8 | 3619.3 | 39.2 | 53.9 | 3134 | 3816.9 | 68 | 10 | "/lb | 2.375 | 4.5 | 1.75 | 10 | 0 | Raw | 7.8 | 7.28 | ef.turb.1 | x | ef.turb.2 | 0.05 | Pres. | 531759000 | 298990500 | 173155000
| Prev | 225482000 | 2111390 | 4923110 | 7605260 | 265901000 | 2322420 | 7131480 | 11879700 |  |  |  | prev | 1253645300 |  |  |  | prev | 2992.8 | 3608.5 | 39.1 | 53.9 | 3134 | 3805.8 | 68 | 10 | Lbs. | 25.5075 | 9.9 | 0.4375 | 10 |  | Trtd | 10.8 | 7.57 | AC.1 | x | AC.2 | 0.791 | Prev. | 531759000 | 298062900 | 173155000
| Total | 0 | 0 | 0 | 0 | 851000 | 9000 | 0 | 17000 |  |  |  | Total | 831600 |  |  |  | Total | 0 | 10.8 | 0.1 | 0 | 0 | 11.1 | 0 | 0 | mg/L | 3.594 | 1.3949 | 0.061643 | 1.409 |  |  |  |  | Raw.Trb. | 3.21 | Cmb.Trb. | 0.024 | Total | 0 | 927600 | 0
8 | Pres. | 225815000 | 2111390 | 4952110 | 7644260 | 267387000 | 2331420 | 7159470 | 11923700 | 968000 | 122990 | 1090990 | now | 1255211000 |  | 0.16 | 0.95 | now | 2997.5 | 3627.4 | 39.3 | 54 | 3139.2 | 3825.4 | 68.3 | 10.1 | "/lb | 2.75 | 5.375 | 2.125 | 7 | 3 | Raw | 7.5 | 7.32 | ef.turb.1 | x | ef.turb.2 | 0.04 | Pres. | 532172000 | 299686500 | 173218000
| Prev | 225482000 | 2111390 | 4923110 | 7605260 | 266752000 | 2331420 | 7131480 | 11896700 |  |  |  | prev | 1254476900 |  |  |  | prev | 2992.8 | 3619.3 | 39.2 | 53.9 | 3134 | 3816.9 | 68 | 10 | Lbs. | 29.535 | 11.825 | 0.53125 | 10 |  | Trtd | 10.4 | 7.6 | AC.1 | x | AC.2 | 0.93 | Prev. | 531759000 | 298990500 | 173155000
| Total | 333000 | 0 | 29000 | 39000 | 635000 | 0 | 27990 | 27000 |  |  |  | Total | 734100 |  |  |  | Total | 4.7 | 8.1 | 0.1 | 0.1 | 5.2 | 8.5 | 0.3 | 0.1 | mg/L | 3.6584 | 1.4647 | 0.065805 | 1.2387 |  |  |  |  | Raw.Trb. | 2.64 | Cmb.Trb. | 0.024 | Total | 413000 | 696000 | 63000
9 | Pres. | 226411000 | 2120390 | 4952110 | 7661260 | 267387000 | 2331420 | 7159470 | 11923700 | 596000 | 26000 | 622000 | now | 1256011900 |  | 0.12 | 0.9 | now | 3005 | 3627.4 | 39.3 | 54.1 | 3147.2 | 3825.4 | 68.3 | 10.1 | "/lb | 2 | 3.0625 | 1.25 | 8 | 0 | Raw | 11.3 | 7.3 | ef.turb.1 | 0.05 | ef.turb.2 | x | Pres. | 532842000 | 299686500 | 173218000
| Prev | 225815000 | 2111390 | 4952110 | 7644260 | 267387000 | 2331420 | 7159470 | 11923700 |  |  |  | prev | 1255211000 |  |  |  | prev | 2997.5 | 3627.4 | 39.3 | 54 | 3139.2 | 3825.4 | 68.3 | 10.1 | Lbs. | 21.48 | 6.7375 | 0.3125 | 8 |  | Trtd | 11 | 7.62 | AC.1 | 0.557 | AC.2 | x | Prev. | 532172000 | 299686500 | 173218000
| Total | 596000 | 9000 | 0 | 17000 | 0 | 0 | 0 | 0 |  |  |  | Total | 800900 |  |  |  | Total | 7.5 | 0 | 0 | 0.1 | 8 | 0 | 0 | 0 | mg/L | 4.3214 | 1.3555 | 0.062869 | 1.6095 |  |  |  |  | Raw.Trb. | 2.68 | Cmb.Trb. | 0.025 | Total | 670000 | 0 | 0
10 | Pres. | 227216000 | 2130380 | 4985100 | 7710250 | 267387000 | 2331420 | 7159470 | 11923700 | 805000 | 91970 | 896970 | now | 1256779400 |  | 0.3 | 0.93 | now | 3015.3 | 3627.4 | 39.3 | 54.2 | 3158.2 | 3825.4 | 68.4 | 10.1 | "/lb | 2.125 | 4 | 1.875 | 10 | 0 | Raw | 10.8 | 7.26 | ef.turb.1 | 0.043 | ef.turb.2 | x | Pres. | 533772000 | 299686500 | 173254000
| Prev | 226411000 | 2120390 | 4952110 | 7661260 | 267387000 | 2331420 | 7159470 | 11923700 |  |  |  | prev | 1256011900 |  |  |  | prev | 3005 | 3627.4 | 39.3 | 54.1 | 3147.2 | 3825.4 | 68.3 | 10.1 | Lbs. | 22.8225 | 8.8 | 0.46875 | 10 |  | Trtd | 11 | 7.61 | AC.1 | 0.651 | AC.2 | x | Prev. | 532842000 | 299686500 | 173218000
| Total | 805000 | 9990 | 32990 | 48990 | 0 | 0 | 0 | 0 |  |  |  | Total | 767500 |  |  |  | Total | 10.3 | 0 | 0 | 0.1 | 11 | 0 | 0.1 | 0 | mg/L | 3.3994 | 1.3108 | 0.06982 | 1.4895 |  |  |  |  | Raw.Trb. | 2.25 | Cmb.Trb. | 0.022 | Total | 930000 | 0 | 36000
11 | Pres. | 228126000 | 2148380 | 5017100 | 7848240 | 267387000 | 2331420 | 7159470 | 11923700 | 910000 | 187990 | 1097990 | now | 1257540700 |  | 0.94 | 1.01 | now | 3027.9 | 3627.4 | 39.3 | 54.5 | 3173 | 3825.4 | 68.6 | 10.2 | "/lb | 1.25 | 5.25 | 2 | 11 | 0 | Raw | 10.5 | 7.3 | ef.turb.1 | 0.044 | ef.turb.2 | x | Pres. | 534492400 | 299686500 | 173290000
| Prev | 227216000 | 2130380 | 4985100 | 7710250 | 267387000 | 2331420 | 7159470 | 11923700 |  |  |  | prev | 1256779400 |  |  |  | prev | 3015.3 | 3627.4 | 39.3 | 54.2 | 3158.2 | 3825.4 | 68.4 | 10.1 | Lbs. | 13.425 | 11.55 | 0.5 | 11 |  | Trtd | 10.9 | 7.65 | AC.1 | 1.734 | AC.2 | x | Prev. | 533772000 | 299686500 | 173254000
| Total | 910000 | 18000 | 32000 | 137990 | 0 | 0 | 0 | 0 |  |  |  | Total | 761300 |  |  |  | Total | 12.6 | 0 | 0 | 0.3 | 14.8 | 0 | 0.2 | 0.1 | mg/L | 1.7689 | 1.5219 | 0.065881 | 1.4494 |  |  |  |  | Raw.Trb. | 9.58 | Cmb.Trb. | 0.024 | Total | 720400 | 0 | 36000
12 | Pres. | 228900000 | 2148380 | 5017100 | 7863240 | 267387000 | 2331420 | 7159470 | 11923700 | 774000 | 15000 | 789000 | now | 1258292000 |  | 0.55 | 0.96 | now | 3038.5 | 3627.4 | 39.3 | 54.5 | 3183.9 | 3825.4 | 68.6 | 10.2 | "/lb | 0.75 | 6 | 1 | 12 |  | Raw | 15.7 | 6.53 | ef.turb.1 | 0.051 | ef.turb.2 | x | Pres. | 535767000 | 299686500 | 173290000
| Prev | 228126000 | 2148380 | 5017100 | 7848240 | 267387000 | 2331420 | 7159470 | 11923700 |  |  |  | prev | 1257540700 |  |  |  | prev | 3027.9 | 3627.4 | 39.3 | 54.5 | 3173 | 3825.4 | 68.6 | 10.2 | Lbs. | 8.055 | 13.2 | 0.25 | 12 |  | Trtd | 13.2 | 7.04 | AC.1 | 0.651 | AC.2 | x | Prev. | 534492400 | 299686500 | 173290000
| Total | 774000 | 0 | 0 | 15000 | 0 | 0 | 0 | 0 |  |  |  | Total | 751300 |  |  |  | Total | 10.6 | 0 | 0 | 0 | 10.9 | 0 | 0 | 0 | mg/L | 1.2478 | 2.0449 | 0.038729 | 1.859 |  |  |  |  | Raw.Trb. | 1.28 | Cmb.Trb. | 0.03 | Total | 1274600 | 0 | 0
13 | Pres. | 229546000 | 2158380 | 5050100 | 7899240 | 267387000 | 2331420 | 7159470 | 11923700 | 646000 | 79000 | 725000 | now | 1259078800 |  | 0.4 | 0.99 | now | 3047.5 | 3627.4 | 39.3 | 54.6 | 3193.5 | 3825.4 | 68.8 | 10.3 | "/lb | 0.5 | 5.625 | 0.875 | 10 | 0 | Raw | 15.2 | 6.46 | ef.turb.1 | 0.046 | ef.turb.2 | x | Pres. | 536450000 | 299686500 | 173326000
| Prev | 228900000 | 2148380 | 5017100 | 7863240 | 267387000 | 2331420 | 7159470 | 11923700 |  |  |  | prev | 1258292000 |  |  |  | prev | 3038.5 | 3627.4 | 39.3 | 54.5 | 3183.9 | 3825.4 | 68.6 | 10.2 | Lbs. | 5.37 | 12.375 | 0.21875 | 10 |  | Trtd | 13.6 | 6.98 | AC.1 | 0.591 | AC.2 | x | Prev. | 535767000 | 299686500 | 173290000
| Total | 646000 | 10000 | 33000 | 36000 | 0 | 0 | 0 | 0 |  |  |  | Total | 786800 |  |  |  | Total | 9 | 0 | 0 | 0.1 | 9.6 | 0 | 0.2 | 0.1 | mg/L | 0.99673 | 2.2969 | 0.040602 | 1.8561 |  |  |  |  | Raw.Trb. | 1.2 | Cmb.Trb. | 0.025 | Total | 683000 | 0 | 36000
14 | Pres. | 230274000 | 2177380 | 5082100 | 8015240 | 267387000 | 2331420 | 7159470 | 11923700 | 728000 | 167000 | 895000 | now | 1259887500 |  | 0.14 | 1.07 | now | 3057.5 | 3627.4 | 39.3 | 54.8 | 3205.4 | 3825.4 | 68.9 | 10.3 | "/lb | 3 | 4.0625 | 2.0625 | 8 | 0 | Raw | 14.6 | 6.49 | ef.turb.1 | 0.057 | ef.turb.2 | x | Pres. | 537454000 | 299686500 | 173361000
| Prev | 229546000 | 2158380 | 5050100 | 7899240 | 267387000 | 2331420 | 7159470 | 11923700 |  |  |  | prev | 1259078800 |  |  |  | prev | 3047.5 | 3627.4 | 39.3 | 54.6 | 3193.5 | 3825.4 | 68.8 | 10.3 | Lbs. | 32.22 | 8.9375 | 0.51562 | 8 |  | Trtd | 14.2 | 6.8 | AC.1 | 2.731 | AC.2 | x | Prev. | 536450000 | 299686500 | 173326000
| Total | 728000 | 19000 | 32000 | 116000 | 0 | 0 | 0 | 0 |  |  |  | Total | 808700 |  |  |  | Total | 10 | 0 | 0 | 0.2 | 11.9 | 0 | 0.1 | 0 | mg/L | 5.3067 | 1.472 | 0.084925 | 1.3176 |  |  |  |  | Raw.Trb. | 1.47 | Cmb.Trb. | 0.036 | Total | 1004000 | 0 | 35000
15 | Pres. | 231122000 | 2177380 | 5082100 | 8046250 | 267387000 | 2331420 | 7159470 | 11923700 | 848000 | 31010 | 879010 | now | 1260654400 |  | 0.06 | 1.02 | now | 3068.3 | 3627.4 | 39.3 | 54.8 | 3216.7 | 3825.4 | 68.9 | 10.3 | "/lb | 2.25 | 4.375 | 1.875 | 8 | 0 | Raw | 13.1 | 7.17 | ef.turb.1 | 0.057 | ef.turb.2 | x | Pres. | 538403000 | 299686500 | 173361000
| Prev | 230274000 | 2177380 | 5082100 | 8015240 | 267387000 | 2331420 | 7159470 | 11923700 |  |  |  | prev | 1259887500 |  |  |  | prev | 3057.5 | 3627.4 | 39.3 | 54.8 | 3205.4 | 3825.4 | 68.9 | 10.3 | Lbs. | 24.165 | 9.625 | 0.46875 | 8 |  | Trtd | 13.5 | 6.93 | AC.1 | 1.548 | AC.2 | x | Prev. | 537454000 | 299686500 | 173361000
| Total | 848000 | 0 | 0 | 31010 | 0 | 0 | 0 | 0 |  |  |  | Total | 766900 |  |  |  | Total | 10.8 | 0 | 0 | 0 | 11.3 | 0 | 0 | 0 | mg/L | 3.4168 | 1.3609 | 0.06628 | 1.1312 |  |  |  |  | Raw.Trb. | 4.18 | Cmb.Trb. | 0.025 | Total | 949000 | 0 | 0
16 | Pres. | 232008000 | 2186380 | 5114090 | 8078260 | 267387000 | 2331420 | 7159470 | 11923700 | 886000 | 73000 | 959000 | now | 1261450400 |  | 0.04 | 0.97 | now | 3078.9 | 3627.4 | 39.3 | 54.9 | 3227.8 | 3825.4 | 69.1 | 10.4 | "/lb | 1.9375 | 4.25 | 1.625 | 8 | 0 | Raw | 10.7 | 7.22 | ef.turb.1 | 0.043 | ef.turb.2 | x | Pres. | 539404000 | 299686500 | 173397000
| Prev | 231122000 | 2177380 | 5082100 | 8046250 | 267387000 | 2331420 | 7159470 | 11923700 |  |  |  | prev | 1260654400 |  |  |  | prev | 3068.3 | 3627.4 | 39.3 | 54.8 | 3216.7 | 3825.4 | 68.9 | 10.3 | Lbs. | 20.8087 | 9.35 | 0.40625 | 8 |  | Trtd | 11.9 | 6.97 | AC.1 | 0.818 | AC.2 | x | Prev. | 538403000 | 299686500 | 173361000
| Total | 886000 | 9000 | 31990 | 32010 | 0 | 0 | 0 | 0 |  |  |  | Total | 796000 |  |  |  | Total | 10.6 | 0 | 0 | 0.1 | 11.1 | 0 | 0.2 | 0.1 | mg/L | 2.8161 | 1.2654 | 0.054979 | 1.0827 |  |  |  |  | Raw.Trb. | 2.88 | Cmb.Trb. | 0.02 | Total | 1001000 | 0 | 36000
17 | Pres. | 232008000 | 2186380 | 5114090 | 8078260 | 268265000 | 2340420 | 7159470 | 11947700 | 878000 | 33000 | 911000 | now | 1262222100 |  | 0.04 | 0.92 | now | 3078.9 | 3638.6 | 39.3 | 55.1 | 3227.8 | 3837.1 | 69.1 | 10.4 | "/lb | 2.125 | 4.625 | 1.875 | 0 | 10 | Raw | 8.8 | 7.26 | ef.turb.1 | 0.044 | ef.turb.2 | x | Pres. | 539404000 | 300656400 | 173397000
| Prev | 232008000 | 2186380 | 5114090 | 8078260 | 267387000 | 2331420 | 7159470 | 11923700 |  |  |  | prev | 1261450400 |  |  |  | prev | 3078.9 | 3627.4 | 39.3 | 54.9 | 3227.8 | 3825.4 | 69.1 | 10.4 | Lbs. | 22.8225 | 10.175 | 0.46875 | 10 |  | Trtd | 10.8 | 7.17 | AC.1 | 0.639 | AC.2 | x | Prev. | 539404000 | 299686500 | 173397000
| Total | 0 | 0 | 0 | 0 | 878000 | 9000 | 0 | 24000 |  |  |  | Total | 771700 |  |  |  | Total | 0 | 11.2 | 0 | 0.2 | 0 | 11.7 | 0 | 0 | mg/L | 3.1168 | 1.3895 | 0.064015 | 1.3657 |  |  |  |  | Raw.Trb. | 2.34 | Cmb.Trb. | 0.018 | Total | 0 | 969900 | 0
18 | Pres. | 232008000 | 2186380 | 5114090 | 8078260 | 268873000 | 2349420 | 7191470 | 11993700 | 608000 | 87000 | 695000 | now | 1263044000 |  | 0.11 | 0.96 | now | 3078.9 | 3646.5 | 39.3 | 55.2 | 3227.8 | 3845.7 | 69.2 | 10.4 | "/lb | 1.25 | 3.625 | 1.25 | 0 | 7 | Raw | 11.1 | 7.38 | ef.turb.1 | X | ef.turb.2 | 0.04 | Pres. | 539404000 | 301359200 | 173432000
| Prev | 232008000 | 2186380 | 5114090 | 8078260 | 268265000 | 2340420 | 7159470 | 11947700 |  |  |  | prev | 1262222100 |  |  |  | prev | 3078.9 | 3638.6 | 39.3 | 55.1 | 3227.8 | 3837.1 | 69.1 | 10.4 | Lbs. | 13.425 | 7.975 | 0.3125 | 7 |  | Trtd | 10 | 7.13 | AC.1 | X | AC.2 | 0.58 | Prev. | 539404000 | 300656400 | 173397000
| Total | 0 | 0 | 0 | 0 | 608000 | 9000 | 32000 | 46000 |  |  |  | Total | 821900 |  |  |  | Total | 0 | 7.9 | 0 | 0.1 | 0 | 8.6 | 0.1 | 0 | mg/L | 2.6476 | 1.5728 | 0.061628 | 1.3805 |  |  |  |  | Raw.Trb. | 2.23 | Cmb.Trb. | 0.027 | Total | 0 | 702800 | 35000
19 | Pres. | 232008000 | 2186380 | 5114090 | 8078260 | 269593000 | 2358420 | 7223470 | 12022700 | 720000 | 70000 | 790000 | now | 1263877500 |  | 0.08 | 0.99 | now | 3078.9 | 3656 | 39.4 | 55.4 | 3227.8 | 3855.6 | 69.4 | 10.4 | "/lb | 2.375 | 4.75 | 1.375 | 8 | 0 | Raw | 11.7 | 7.24 | ef.turb.1 | x | ef.turb.2 | 0.044 | Pres. | 539404000 | 302161000 | 173466000
| Prev | 232008000 | 2186380 | 5114090 | 8078260 | 268873000 | 2349420 | 7191470 | 11993700 |  |  |  | prev | 1263044000 |  |  |  | prev | 3078.9 | 3646.5 | 39.3 | 55.2 | 3227.8 | 3845.7 | 69.2 | 10.4 | Lbs. | 25.5075 | 10.45 | 0.34375 | 8 |  | Trtd | 11.3 | 7.05 | AC.1 | x | AC.2 | 0.623 | Prev. | 539404000 | 301359200 | 173432000
| Total | 0 | 0 | 0 | 0 | 720000 | 9000 | 32000 | 29000 |  |  |  | Total | 833500 |  |  |  | Total | 0 | 9.5 | 0.1 | 0.2 | 0 | 9.9 | 0.2 | 0 | mg/L | 4.2479 | 1.7403 | 0.057246 | 1.3323 |  |  |  |  | Raw.Trb. | 1.89 | Cmb.Trb. | 0.027 | Total | 0 | 801800 | 34000
20 | Pres. | 232008000 | 2186380 | 5114090 | 8078260 | 270285000 | 2358420 | 7223470 | 12037000 | 692000 | 14300 | 706300 | now | 1264638400 |  | 0.1 | 0.97 | now | 3078.9 | 3665.1 | 39.4 | 55.4 | 3227.8 | 3864.8 | 69.4 | 10.4 | "/lb | 1.625 | 3.5 | 1.375 | 0 | 8 | Raw | 8.5 | 7.22 | ef.turb.1 | x | ef.turb.2 | 0.043 | Pres. | 539404000 | 302900400 | 173466000
| Prev | 232008000 | 2186380 | 5114090 | 8078260 | 269593000 | 2358420 | 7223470 | 12022700 |  |  |  | prev | 1263877500 |  |  |  | prev | 3078.9 | 3656 | 39.4 | 55.4 | 3227.8 | 3855.6 | 69.4 | 10.4 | Lbs. | 17.4525 | 7.7 | 0.34375 | 8 |  | Trtd | 11.6 | 6.68 | AC.1 | x | AC.2 | 0.68 | Prev. | 539404000 | 302161000 | 173466000
| Total | 0 | 0 | 0 | 0 | 692000 | 0 | 0 | 14300 |  |  |  | Total | 760900 |  |  |  | Total | 0 | 9.1 | 0 | 0 | 0 | 9.2 | 0 | 0 | mg/L | 3.024 | 1.3342 | 0.059562 | 1.3862 |  |  |  |  | Raw.Trb. | 2.24 | Cmb.Trb. | 0.024 | Total | 0 | 739400 | 0
21 | Pres. | 232008000 | 2186380 | 5114090 | 8078260 | 271293000 | 2366420 | 7255470 | 12063700 | 1008000 | 66700 | 1074700 | now | 1265393600 |  | 0.21 | 0.92 | now | 3078.9 | 3678.3 | 39.6 | 55.5 | 3227.8 | 3878.4 | 69.6 | 10.4 | "/lb | 3.125 | 6.75 | 2.125 | 12 | 0 | Raw | 8.7 | 7.35 | ef.turb.1 | x | ef.turb.2 | 0.055 | Pres. | 539404000 | 304012400 | 173501000
| Prev | 232008000 | 2186380 | 5114090 | 8078260 | 270285000 | 2358420 | 7223470 | 12037000 |  |  |  | prev | 1264638400 |  |  |  | prev | 3078.9 | 3665.1 | 39.4 | 55.4 | 3227.8 | 3864.8 | 69.4 | 10.4 | Lbs. | 33.5625 | 14.85 | 0.53125 | 12 |  | Trtd | 10.8 | 6.72 | AC.1 | x | AC.2 | 0.88 | Prev. | 539404000 | 302900400 | 173466000
| Total | 0 | 0 | 0 | 0 | 1008000 | 8000 | 32000 | 26700 |  |  |  | Total | 755200 |  |  |  | Total | 0 | 13.2 | 0.2 | 0.1 | 0 | 13.6 | 0.2 | 0 | mg/L | 3.9923 | 1.7664 | 0.063193 | 1.4274 |  |  |  |  | Raw.Trb. | 2.21 | Cmb.Trb. | 0.04 | Total | 0 | 1112000 | 35000
22 | Pres. | 232008000 | 2186380 | 5114090 | 8078260 | 272006000 | 2366420 | 7255470 | 12079700 | 713000 | 16000 | 729000 | now | 1266263400 |  | 0.14 | 1 | now | 3078.9 | 3687.4 | 39.6 | 55.5 | 3227.8 | 3887.8 | 69.6 | 10.4 | "/lb | 1.375 | 5.75 | 1.125 | 8 | 0 | Raw | 6.8 | 7.27 | ef.turb.1 | x | ef.turb.2 | 0.042 | Pres. | 539404000 | 304780300 | 173501000
| Prev | 232008000 | 2186380 | 5114090 | 8078260 | 271293000 | 2366420 | 7255470 | 12063700 |  |  |  | prev | 1265393600 |  |  |  | prev | 3078.9 | 3678.3 | 39.6 | 55.5 | 3227.8 | 3878.4 | 69.6 | 10.4 | Lbs. | 14.7675 | 12.65 | 0.28125 | 8 |  | Trtd | 9.7 | 6.91 | AC.1 | x | AC.2 | 0.61 | Prev. | 539404000 | 304012400 | 173501000
| Total | 0 | 0 | 0 | 0 | 713000 | 0 | 0 | 16000 |  |  |  | Total | 869800 |  |  |  | Total | 0 | 9.1 | 0 | 0 | 0 | 9.4 | 0 | 0 | mg/L | 2.4834 | 2.1273 | 0.047297 | 1.3453 |  |  |  |  | Raw.Trb. | 1.75 | Cmb.Trb. | 0.024 | Total | 0 | 767900 | 0
23 | Pres. | 232008000 | 2186380 | 5114090 | 8078260 | 272606000 | 2375420 | 7287470 | 12113800 | 600000 | 75100 | 675100 | now | 1266971500 |  | 0.07 | 0.97 | now | 3078.9 | 3695.3 | 39.7 | 55.5 | 3227.8 | 3896.1 | 69.8 | 10.4 | "/lb | 1.75 | 5 | 1.375 | 0 | 7 | Raw | 8.3 | 7.3 | ef.turb.1 | x | ef.turb.2 | 0.04 | Pres. | 539404000 | 305460900 | 173537000
| Prev | 232008000 | 2186380 | 5114090 | 8078260 | 272006000 | 2366420 | 7255470 | 12079700 |  |  |  | prev | 1266263400 |  |  |  | prev | 3078.9 | 3687.4 | 39.6 | 55.5 | 3227.8 | 3887.8 | 69.6 | 10.4 | Lbs. | 18.795 | 11 | 0.34375 | 7 |  | Trtd | 9.6 | 7 | AC.1 | x | AC.2 | 0.54 | Prev. | 539404000 | 304780300 | 173501000
| Total | 0 | 0 | 0 | 0 | 600000 | 9000 | 32000 | 34100 |  |  |  | Total | 708100 |  |  |  | Total | 0 | 7.9 | 0.1 | 0 | 0 | 8.3 | 0.2 | 0 | mg/L | 3.756 | 2.1982 | 0.068695 | 1.3989 |  |  |  |  | Raw.Trb. | 1.81 | Cmb.Trb. | 0.024 | Total | 0 | 680600 | 36000
24 | Pres. | 232008000 | 2186380 | 5114090 | 8078260 | 273419000 | 2384420 | 7319460 | 12144800 | 813000 | 71990 | 884990 | now | 1267888500 |  | 0.04 | 0.95 | now | 3078.9 | 3705.7 | 39.9 | 55.6 | 3227.8 | 3907 | 70 | 10.4 | "/lb | 1.9375 | 6.5 | 1.625 | 0 | 10 | Raw | 9.3 | 7.29 | ef.turb.1 | x | ef.turb.2 | 0.044 | Pres. | 539404000 | 306363900 | 173572000
| Prev | 232008000 | 2186380 | 5114090 | 8078260 | 272606000 | 2375420 | 7287470 | 12113800 |  |  |  | prev | 1266971500 |  |  |  | prev | 3078.9 | 3695.3 | 39.7 | 55.5 | 3227.8 | 3896.1 | 69.8 | 10.4 | Lbs. | 20.8087 | 14.3 | 0.40625 | 10 |  | Trtd | 9.7 | 7.36 | AC.1 | x | AC.2 | 0.576 | Prev. | 539404000 | 305460900 | 173537000
| Total | 0 | 0 | 0 | 0 | 813000 | 9000 | 31990 | 31000 |  |  |  | Total | 917000 |  |  |  | Total | 0 | 10.4 | 0.2 | 0.1 | 0 | 10.9 | 0.2 | 0 | mg/L | 3.0689 | 2.109 | 0.059915 | 1.4748 |  |  |  |  | Raw.Trb. | 1.85 | Cmb.Trb. | 0.027 | Total | 0 | 903000 | 35000
25 | Pres. | 232008000 | 2186380 | 5114090 | 8078260 | 274206000 | 2384420 | 7319460 | 12152800 | 787000 | 8000 | 795000 | now | 1268643800 |  | 0.03 | 1 | now | 3078.9 | 3715.7 | 39.9 | 55.6 | 3227.8 | 3917.2 | 70 | 10.4 | "/lb | 1.5 | 6.25 | 1.625 | 0 | 10 | Raw | 9.7 | 7.21 | ef.turb.1 | x | ef.turb.2 | 0.045 | Pres. | 539404000 | 307202800 | 173572000
| Prev | 232008000 | 2186380 | 5114090 | 8078260 | 273419000 | 2384420 | 7319460 | 12144800 |  |  |  | prev | 1267888500 |  |  |  | prev | 3078.9 | 3705.7 | 39.9 | 55.6 | 3227.8 | 3907 | 70 | 10.4 | Lbs. | 16.11 | 13.75 | 0.40625 | 10 |  | Trtd | 9.9 | 7.42 | AC.1 | x | AC.2 | 0.614 | Prev. | 539404000 | 306363900 | 173572000
| Total | 0 | 0 | 0 | 0 | 787000 | 0 | 0 | 8000 |  |  |  | Total | 755300 |  |  |  | Total | 0 | 10 | 0 | 0 | 0 | 10.2 | 0 | 0 | mg/L | 2.4545 | 2.0949 | 0.061895 | 1.5236 |  |  |  |  | Raw.Trb. | 1.79 | Cmb.Trb. | 0.027 | Total | 0 | 838900 | 0
26 | Pres. | 232008000 | 2186380 | 5114090 | 8078260 | 274736000 | 2393420 | 7351460 | 12182800 | 530000 | 71000 | 601000 | now | 1269375800 |  | 0.04 | 1.01 | now | 3078.9 | 3722.5 | 40.1 | 55.7 | 3227.8 | 3924.4 | 70.2 | 10.4 | "/lb | 1.9375 | 4.25 | 1.125 | 0 | 6 | Raw | 10.1 | 7.26 | ef.turb.1 | x | ef.turb.2 | 0.044 | Pres. | 539404000 | 307808000 | 173607000
| Prev | 232008000 | 2186380 | 5114090 | 8078260 | 274206000 | 2384420 | 7319460 | 12152800 |  |  |  | prev | 1268643800 |  |  |  | prev | 3078.9 | 3715.7 | 39.9 | 55.6 | 3227.8 | 3917.2 | 70 | 10.4 | Lbs. | 20.8087 | 9.35 | 0.28125 | 6 |  | Trtd | 9.5 | 7.4 | AC.1 | x | AC.2 | 0.589 | Prev. | 539404000 | 307202800 | 173572000
| Total | 0 | 0 | 0 | 0 | 530000 | 9000 | 32000 | 30000 |  |  |  | Total | 732000 |  |  |  | Total | 0 | 6.8 | 0.2 | 0.1 | 0 | 7.2 | 0.2 | 0 | mg/L | 4.7076 | 2.1153 | 0.063628 | 1.3574 |  |  |  |  | Raw.Trb. | 2.78 | Cmb.Trb. | 0.027 | Total | 0 | 605200 | 35000
27 | Pres. | 232008000 | 2186380 | 5114090 | 8078260 | 275664000 | 2393420 | 7351460 | 12190800 | 928000 | 8000 | 936000 | now | 1270141700 |  | 0.03 | 0.98 | now | 3078.9 | 3734.3 | 40.1 | 55.7 | 3227.8 | 3936.3 | 70.2 | 10.4 | "/lb | 2 | 7.625 | 2.125 | 0 | 12 | Raw | 10.6 | 7.32 | ef.turb.1 | x | ef.turb.2 | 0.077 | Pres. | 539404000 | 308792600 | 173607000
| Prev | 232008000 | 2186380 | 5114090 | 8078260 | 274736000 | 2393420 | 7351460 | 12182800 |  |  |  | prev | 1269375800 |  |  |  | prev | 3078.9 | 3722.5 | 40.1 | 55.7 | 3227.8 | 3924.4 | 70.2 | 10.4 | Lbs. | 21.48 | 16.775 | 0.53125 | 12 |  | Trtd | 9.9 | 7.48 | AC.1 | x | AC.2 | 0.54 | Prev. | 539404000 | 307808000 | 173607000
| Total | 0 | 0 | 0 | 0 | 928000 | 0 | 0 | 8000 |  |  |  | Total | 765900 |  |  |  | Total | 0 | 11.8 | 0 | 0 | 0 | 11.9 | 0 | 0 | mg/L | 2.7754 | 2.1674 | 0.068641 | 1.5505 |  |  |  |  | Raw.Trb. | 1.91 | Cmb.Trb. | 0.052 | Total | 0 | 984600 | 0
28 | Pres. | 232008000 | 2186380 | 5114090 | 8078260 | 276268000 | 2402420 | 7383460 | 12211800 | 604000 | 62000 | 666000 | now | 1270845500 |  | 0.02 | 1 | now | 3078.9 | 3742.1 | 40.3 | 55.7 | 3227.8 | 3944.4 | 70.3 | 10.4 | "/lb | 2 | 5.625 | 1.5 | 8 | 0 | Raw | 12.1 | 7.33 | ef.turb.1 | x | ef.turb.2 | 0.045 | Pres. | 539404000 | 309461984 | 173642000
| Prev | 232008000 | 2186380 | 5114090 | 8078260 | 275664000 | 2393420 | 7351460 | 12190800 |  |  |  | prev | 1270141700 |  |  |  | prev | 3078.9 | 3734.3 | 40.1 | 55.7 | 3227.8 | 3936.3 | 70.2 | 10.4 | Lbs. | 21.48 | 12.375 | 0.375 | 8 |  | Trtd | 12.2 | 7.52 | AC.1 | x | AC.2 | 0.442 | Prev. | 539404000 | 308792600 | 173607000
| Total | 0 | 0 | 0 | 0 | 604000 | 9000 | 32000 | 21000 |  |  |  | Total | 703800 |  |  |  | Total | 0 | 7.8 | 0.2 | 0 | 0 | 8.1 | 0.1 | 0 | mg/L | 4.2641 | 2.4566 | 0.074444 | 1.5881 |  |  |  |  | Raw.Trb. | 2.08 | Cmb.Trb. | 0.027 | Total | 0 | 669384 | 35000
29 | Pres. | 232785000 | 2196380 | 5143090 | 8117280 | 276268000 | 2402420 | 7383460 | 12211800 | 777000 | 78020 | 855020 | now | 1271620400 |  | 0.03 | 1 | now | 3088.9 | 3742.1 | 40.4 | 55.7 | 3238.3 | 3944.4 | 70.5 | 10.4 | "/lb | 1.875 | 5 | 1.25 | 8 | 0 | Raw | 9.8 | 7.2 | ef.turb.1 | x | ef.turb.2 | 0.05 | Pres. | 540291000 | 309461984 | 173677000
| Prev | 232008000 | 2186380 | 5114090 | 8078260 | 276268000 | 2402420 | 7383460 | 12211800 |  |  |  | prev | 1270845500 |  |  |  | prev | 3078.9 | 3742.1 | 40.3 | 55.7 | 3227.8 | 3944.4 | 70.3 | 10.4 | Lbs. | 20.1375 | 11 | 0.3125 | 8 |  | Trtd | 9.2 | 7.43 | AC.1 | x | AC.2 | 0.52 | Prev. | 539404000 | 309461984 | 173642000
| Total | 777000 | 10000 | 29000 | 39020 | 0 | 0 | 0 | 0 |  |  |  | Total | 774900 |  |  |  | Total | 10 | 0 | 0.1 | 0 | 10.5 | 0 | 0.2 | 0 | mg/L | 3.1076 | 1.6975 | 0.048224 | 1.2345 |  |  |  |  | Raw.Trb. | 2.04 | Cmb.Trb. | 0.03 | Total | 887000 | 0 | 35000
30 | Pres. | 233617000 | 2196380 | 5147090 | 8126280 | 276268000 | 2402420 | 7383460 | 12211800 | 832000 | 13000 | 845000 | now | 1272406900 |  | 0.02 | 1.01 | now | 3099.5 | 3742.1 | 40.4 | 55.7 | 3249.1 | 3944.4 | 70.5 | 10.4 | "/lb | 1.75 | 7 | 1.75 | 10 | 0 | Raw | 9.3 | 7.11 | ef.turb.1 | 0.05 | ef.turb.2 | x | Pres. | 541196000 | 309461984 | 173677000
| Prev | 232785000 | 2196380 | 5143090 | 8117280 | 276268000 | 2402420 | 7383460 | 12211800 |  |  |  | prev | 1271620400 |  |  |  | prev | 3088.9 | 3742.1 | 40.4 | 55.7 | 3238.3 | 3944.4 | 70.5 | 10.4 | Lbs. | 18.795 | 15.4 | 0.4375 | 10 |  | Trtd | 9.3 | 7.4 | AC.1 | 0.65 | AC.2 | x | Prev. | 540291000 | 309461984 | 173677000
| Total | 832000 | 0 | 4000 | 9000 | 0 | 0 | 0 | 0 |  |  |  | Total | 786500 |  |  |  | Total | 10.6 | 0 | 0 | 0 | 10.8 | 0 | 0 | 0 | mg/L | 2.7087 | 2.2194 | 0.063051 | 1.4412 |  |  |  |  | Raw.Trb. | 2.58 | Cmb.Trb. | 0.03 | Total | 905000 | 0 | 0
[10 empty] | Totals | [6 empty] | AVG | [10 empty] | totals | [5 empty] | AVG TRTD |  |  |  | Avg.Cmb.Trb.
[10 empty] | 22992000 | 1832160 | 24824160 |  | 23527500 |  | 4.95 | 0.97833 | [5 empty] | 134.2 | 179.8 |  |  |  | 639.7013 | 319.55 | 11.9531 | 272 |  |  | 11.2167 | 7.3057 |  |  | 0.027667
[22 empty] | total- | 314

## Dec, 2021
December, 2021
Filters | [15 empty] | Rain | Cl2 | Pump Hours | [8 empty] | Chemicals | [5 empty] | Misc. |  |  | Turbidity |  |  |  | Meters
Day |  | CW.Tot.1 | Cla.Wst.1 | BW.Wst.1 | FTWst.1 | CW.Tot.2 | Cla.Wst.2 | BW.Wst.2 | FTWst.2 | Treated Total | Wastewater | Total Influent | Totalizer |  |  | Inches | Resid | Pump | Ef.Pmp.1 | Ef.Pmp.2 | Blo.1 | Blo.2 | URT.1 | URT.2 | BWP | SWP | Chem | ACH | SA | Poly | Cl2.1 | Cl2.2 | water | Temp | pH | F1 |  | F2 |  |  | RM1 | RM2 | BWM
1 | Pres. | 233617000 | 2196380 | 5147090 | 8126280 | 277070000 | 2402420 | 7416460 | 12267800 | 802000 | 89000 | 891000 | now | 1273179700 |  | 0.02 | 1.03 | now | 3099.5 | 3752.4 | 40.4 | 55.8 | 3249.1 | 3955.4 | 70.7 | 10.4 | "/lb | 1.9375 | 6.75 | 1.75 | 0 | 9 | Raw | 9.4 | 7.13 | ef.turb.1 | 0.05 | ef.turb.2 | x | Pres. | 541196000 | 310372500 | 173713000
| Prev | 233617000 | 2196380 | 5147090 | 8126280 | 276268000 | 2402420 | 7383460 | 12211800 |  |  |  | prev | 1272406900 |  |  |  | prev | 3099.5 | 3742.1 | 40.4 | 55.7 | 3249.1 | 3944.4 | 70.5 | 10.4 | Lbs. | 20.8087 | 14.85 | 0.4375 | 9 |  | Trtd | 10.9 | 7.49 | AC.1 | 0.451 | AC.2 | x | Prev. | 541196000 | 309461984 | 173677000
| Total | 0 | 0 | 0 | 0 | 802000 | 0 | 33000 | 56000 |  |  |  | Total | 772800 |  |  |  | Total | 0 | 10.3 | 0 | 0.1 | 0 | 11 | 0.2 | 0 | mg/L | 3.111 | 2.2202 | 0.065409 | 1.3456 |  |  |  |  | Raw.Trb. | 2.19 | Cmb.Trb. | 0.02 | Total | 0 | 910516 | 36000
2 | Pres. | 233617000 | 2196380 | 5147090 | 8126280 | 277766000 | 2411420 | 7416460 | 12275800 | 696000 | 17000 | 713000 | now | 1273948000 |  | 0.02 | 1.02 | now | 3099.5 | 3761.3 | 40.4 | 55.9 | 3249.1 | 3964.5 | 70.7 | 10.4 | "/lb | 1.5 | 5.75 | 1.375 | 0 | 8 | Raw | 12.1 | 7.28 | ef.turb.1 | x | ef.turb.2 | 0.046 | Pres. | 541196000 | 311125500 | 173713000
| Prev | 233617000 | 2196380 | 5147090 | 8126280 | 277070000 | 2402420 | 7416460 | 12267800 |  |  |  | prev | 1273179700 |  |  |  | prev | 3099.5 | 3752.4 | 40.4 | 55.8 | 3249.1 | 3955.4 | 70.7 | 10.4 | Lbs. | 16.11 | 12.65 | 0.34375 | 8 |  | Trtd | 11.4 | 7.67 | AC.1 | x | AC.2 | 0.384 | Prev. | 541196000 | 310372500 | 173713000
| Total | 0 | 0 | 0 | 0 | 696000 | 9000 | 0 | 8000 |  |  |  | Total | 768300 |  |  |  | Total | 0 | 8.9 | 0 | 0.1 | 0 | 9.1 | 0 | 0 | mg/L | 2.7754 | 2.1793 | 0.05922 | 1.3782 |  |  |  |  | Raw.Trb. | 2.12 | Cmb.Trb. | 0.029 | Total | 0 | 753000 | 0
10.6
3 | Pres. | 233617000 | 2196380 | 5147090 | 8126280 | 278692000 | 2420420 | 7448450 | 12321800 | 926000 | 86990 | 1012990 | now | 1274901000 |  | 0.01 | 1.03 | now | 3099.5 | 3773.2 | 40.5 | 56.1 | 3249.1 | 3977 | 70.7 | 10.4 | "/lb | 1.625 | 7.5 | 2.5 | 11 | 0 | Raw | 10.8 | 7.32 | ef.turb.1 | x | ef.turb.2 | 0.043 | Pres. | 541196000 | 312154500 | 173748000
| Prev | 233617000 | 2196380 | 5147090 | 8126280 | 277766000 | 2411420 | 7416460 | 12275800 |  |  |  | prev | 1273948000 |  |  |  | prev | 3099.5 | 3761.3 | 40.4 | 55.9 | 3249.1 | 3964.5 | 70.7 | 10.4 | Lbs. | 17.4525 | 16.5 | 0.625 | 11 |  | Trtd | 10.9 | 7.78 | AC.1 | x | AC.2 | 0.46 | Prev. | 541196000 | 311125500 | 173713000
| Total | 0 | 0 | 0 | 0 | 926000 | 9000 | 31990 | 46000 |  |  |  | Total | 953000 |  |  |  | Total | 0 | 11.9 | 0.1 | 0.2 | 0 | 12.5 | 0 | 0 | mg/L | 2.2599 | 2.1365 | 0.080929 | 1.4243 |  |  |  |  | Raw.Trb. | 1.29 | Cmb.Trb. | 0.026 | Total | 0 | 1029000 | 35000
4 | Pres. | 233617000 | 2196380 | 5147090 | 8126280 | 279210000 | 2420420 | 7448450 | 12321800 | 518000 | 0 | 518000 | now | 1275591500 |  | 0.02 | 0.99 | now | 3099.5 | 3779.5 | 40.5 | 56.1 | 3249.1 | 3983.7 | 70.8 | 10.4 | "/lb | 1 | 4.25 | 1.0625 | 5 | 0 | Raw | 7.3 | 7.44 | ef.turb.1 | x | ef.turb.2 | 0.06 | Pres. | 541196000 | 312709400 | 173748000
| Prev | 233617000 | 2196380 | 5147090 | 8126280 | 278692000 | 2420420 | 7448450 | 12321800 |  |  |  | prev | 1274901000 |  |  |  | prev | 3099.5 | 3773.2 | 40.5 | 56.1 | 3249.1 | 3977 | 70.7 | 10.4 | Lbs. | 10.74 | 9.35 | 0.26562 | 5 |  | Trtd | 10.2 | 7.56 | AC.1 | x | AC.2 | 0.44 | Prev. | 541196000 | 312154500 | 173748000
| Total | 0 | 0 | 0 | 0 | 518000 | 0 | 0 | 0 |  |  |  | Total | 690500 |  |  |  | Total | 0 | 6.3 | 0 | 0 | 0 | 6.7 | 0.1 | 0 | mg/L | 2.486 | 2.1643 | 0.061486 | 1.1574 |  |  |  |  | Raw.Trb. | 1.28 | Cmb.Trb. | 0.05 | Total | 0 | 554900 | 0
5 | Pres. | 233617000 | 2196380 | 5147090 | 8126280 | 280141000 | 2429420 | 7448450 | 12329800 | 931000 | 17000 | 948000 | now | 1276329100 | 0 | 0.01 | 0.94 | now | 3099.5 | 3791.8 | 40.6 | 56.1 | 3249.1 | 3995.8 | 70.8 | 10.4 | "/lb | 2 | 7.5 | 2 | 10 | 0 | Raw | 9.1 | 7.26 | ef.turb.1 | x | ef.turb.2 | 0.055 | Pres. | 541196000 | 313711400 | 173748000
| Prev | 233617000 | 2196380 | 5147090 | 8126280 | 279210000 | 2420420 | 7448450 | 12321800 |  |  |  | prev | 1275591500 |  |  |  | prev | 3099.5 | 3779.5 | 40.5 | 56.1 | 3249.1 | 3983.7 | 70.8 | 10.4 | Lbs. | 21.48 | 16.5 | 0.5 | 10 |  | Trtd | 10.1 | 7.54 | AC.1 | x | AC.2 | 0.38 | Prev. | 541196000 | 312709400 | 173748000
| Total | 0 | 0 | 0 | 0 | 931000 | 9000 | 0 | 8000 |  |  |  | Total | 737600 |  |  |  | Total | 0 | 12.3 | 0.1 | 0 | 0 | 12.1 | 0 | 0 | mg/L | 2.7664 | 2.125 | 0.064395 | 1.2879 |  |  |  |  | Raw.Trb. | 1.42 | Cmb.Trb. | 0.03 | Total | 0 | 1002000 | 0
6 | Pres. | 233617000 | 2196380 | 5147090 | 8126280 | 280710000 | 2429420 | 7480450 | 12370900 | 569000 | 73100 | 642100 | now | 1277096800 |  | 0.01 | 0.95 | now | 3099.5 | 3799.2 | 40.7 | 56.1 | 3249.1 | 4003.7 | 71 | 10.4 | "/lb | 1.5 | 5.125 | 1.375 | 0 | 6 | Raw | 9.9 | 7.52 | ef.turb.1 | 1.31 | ef.turb.2 | 0.041 | Pres. | 541196000 | 314354800 | 173783000
| Prev | 233617000 | 2196380 | 5147090 | 8126280 | 280141000 | 2429420 | 7448450 | 12329800 |  |  |  | prev | 1276329100 |  |  |  | prev | 3099.5 | 3791.8 | 40.6 | 56.1 | 3249.1 | 3995.8 | 70.8 | 10.4 | Lbs. | 16.11 | 11.275 | 0.34375 | 6 |  | Trtd | 9.3 | 7.81 | AC.1 | x | AC.2 | 0.39 | Prev. | 541196000 | 313711400 | 173748000
| Total | 0 | 0 | 0 | 0 | 569000 | 0 | 32000 | 41100 |  |  |  | Total | 767700 |  |  |  | Total | 0 | 7.4 | 0.1 | 0 | 0 | 7.9 | 0.2 | 0 | mg/L | 3.3948 | 2.376 | 0.072438 | 1.2644 |  |  |  |  | Raw.Trb. | x | Cmb.Trb. | 0.024 | Total | 0 | 643400 | 35000
7 | Pres. | 234386000 | 2205380 | 5179090 | 8156300 | 280710000 | 2429420 | 7480450 | 12370900 | 769000 | 71020 | 840020 | now | 1277867300 |  | 0.01 | 1.01 | now | 3109.4 | 3799.2 | 40.7 | 56.2 | 3259.5 | 4003.7 | 71.2 | 10.5 | "/lb | 2.375 | 7.25 | 1.75 | 9 | 0 | Raw | 10.8 | 7.3 | ef.turb.1 | 0.05 | ef.turb.2 | x | Pres. | 542070000 | 314354800 | 173819000
| Prev | 233617000 | 2196380 | 5147090 | 8126280 | 280710000 | 2429420 | 7480450 | 12370900 |  |  |  | prev | 1277096800 |  |  |  | prev | 3099.5 | 3799.2 | 40.7 | 56.1 | 3249.1 | 4003.7 | 71 | 10.4 | Lbs. | 25.5075 | 15.95 | 0.4375 | 9 |  | Trtd | 10.8 | 7.57 | AC.1 | 0.319 | AC.2 | x | Prev. | 541196000 | 314354800 | 173783000
| Total | 769000 | 9000 | 32000 | 30020 | 0 | 0 | 0 | 0 |  |  |  | Total | 770500 |  |  |  | Total | 9.9 | 0 | 0 | 0.1 | 10.4 | 0 | 0.2 | 0.1 | mg/L | 3.9772 | 2.487 | 0.068216 | 1.4033 |  |  |  |  | Raw.Trb. | 1.93 | Cmb.Trb. | 0.031 | Total | 874000 | 0 | 36000
8 | Pres. | 234386000 | 2205380 | 5179090 | 8156300 | 281498000 | 2438420 | 7480450 | 12394900 | 788000 | 33000 | 821000 | now | 1278664000 |  | 0.01 | 0.99 | now | 3109.4 | 3809.2 | 40.7 | 56.4 | 3259.5 | 4014.2 | 71.2 | 10.5 | "/lb | 1.9375 | 5.5 | 1.5 | 0 | 7 | Raw | 10.8 | 7.26 | ef.turb.1 | x | ef.turb.2 | 0.046 | Pres. | 542070000 | 315225600 | 173819000
| Prev | 234386000 | 2205380 | 5179090 | 8156300 | 280710000 | 2429420 | 7480450 | 12370900 |  |  |  | prev | 1277867300 |  |  |  | prev | 3109.4 | 3799.2 | 40.7 | 56.2 | 3259.5 | 4003.7 | 71.2 | 10.5 | Lbs. | 20.8087 | 12.1 | 0.375 | 7 |  | Trtd | 10.4 | 7.64 | AC.1 | x | AC.2 | 0.36 | Prev. | 542070000 | 314354800 | 173819000
| Total | 0 | 0 | 0 | 0 | 788000 | 9000 | 0 | 24000 |  |  |  | Total | 796700 |  |  |  | Total | 0 | 10 | 0 | 0.2 | 0 | 10.5 | 0 | 0 | mg/L | 3.1663 | 1.8412 | 0.057061 | 1.0651 |  |  |  |  | Raw.Trb. | 1.77 | Cmb.Trb. | 0.027 | Total | 0 | 870800 | 0
9 | Pres. | 234386000 | 2205380 | 5179090 | 8156300 | 282202000 | 2447410 | 7513450 | 12424900 | 704000 | 71990 | 775990 | now | 1279433000 |  | 0.01 | 0.96 | now | 3109.4 | 3818.3 | 40.7 | 56.5 | 3259.5 | 4023.7 | 71.4 | 10.5 | "/lb | 1.75 | 5.75 | 1.5 | 0 | 8 | Raw | 9.2 | 7.19 | ef.turb.1 | x | ef.turb.2 | 0.043 | Pres. | 542070000 | 316010900 | 173854000
| Prev | 234386000 | 2205380 | 5179090 | 8156300 | 281498000 | 2438420 | 7480450 | 12394900 |  |  |  | prev | 1278664000 |  |  |  | prev | 3109.4 | 3809.2 | 40.7 | 56.4 | 3259.5 | 4014.2 | 71.2 | 10.5 | Lbs. | 18.795 | 12.65 | 0.375 | 8 |  | Trtd | 10.2 | 7.68 | AC.1 | x | AC.2 | 0.421 | Prev. | 542070000 | 315225600 | 173819000
| Total | 0 | 0 | 0 | 0 | 704000 | 8990 | 33000 | 30000 |  |  |  | Total | 769000 |  |  |  | Total | 0 | 9.1 | 0 | 0.1 | 0 | 9.5 | 0.2 | 0 | mg/L | 3.2011 | 2.1545 | 0.063869 | 1.3625 |  |  |  |  | Raw.Trb. | 1.86 | Cmb.Trb. | 0.026 | Total | 0 | 785300 | 35000
10 | Pres. | 234386000 | 2205380 | 5179090 | 8156300 | 282983000 | 2456410 | 7513450 | 12432900 | 781000 | 17000 | 798000 | now | 1280186400 |  | 0.02 | 0.95 | now | 3109.4 | 3828.2 | 40.9 | 56.5 | 3259.5 | 4033.9 | 71.4 | 10.5 | "/lb | 1.5 | 6.25 | 2.125 | 0 | 10 | Raw | 8.9 | 7.2 | ef.turb.1 | x | ef.turb.2 | 0.046 | Pres. | 542070000 | 316853700 | 173854000
| Prev | 234386000 | 2205380 | 5179090 | 8156300 | 282202000 | 2447410 | 7513450 | 12424900 |  |  |  | prev | 1279433000 |  |  |  | prev | 3109.4 | 3818.3 | 40.7 | 56.5 | 3259.5 | 4023.7 | 71.4 | 10.5 | Lbs. | 16.11 | 13.75 | 0.53125 | 10 |  | Trtd | 9.7 | 7.74 | AC.1 | x | AC.2 | 0.466 | Prev. | 542070000 | 316010900 | 173854000
| Total | 0 | 0 | 0 | 0 | 781000 | 9000 | 0 | 8000 |  |  |  | Total | 753400 |  |  |  | Total | 0 | 9.9 | 0.2 | 0 | 0 | 10.2 | 0 | 0 | mg/L | 2.4733 | 2.111 | 0.081561 | 1.5353 |  |  |  |  | Raw.Trb. | 1.45 | Cmb.Trb. | 0.028 | Total | 0 | 842800 | 0
11 | Pres. | 234386000 | 2205380 | 5179090 | 8156300 | 283715000 | 2483410 | 7545450 | 12463900 | 732000 | 90000 | 822000 | now | 1280958100 |  | 0.02 | 0.98 | now | 3109.4 | 3837.7 | 40.9 | 57 | 3259.5 | 4044.1 | 71.5 | 10.5 | "/lb | 2.5 | 6.125 | 1.625 | 0 | 10 | Raw | 8.5 | 7.33 | ef.turb.1 | x | ef.turb.2 | 0.043 | Pres. | 542070000 | 317691900 | 173889000
| Prev | 234386000 | 2205380 | 5179090 | 8156300 | 282983000 | 2456410 | 7513450 | 12432900 |  |  |  | prev | 1280186400 |  |  |  | prev | 3109.4 | 3828.2 | 40.9 | 56.5 | 3259.5 | 4033.9 | 71.4 | 10.5 | Lbs. | 26.85 | 13.475 | 0.40625 | 10 |  | Trtd | 10.1 | 7.65 | AC.1 | x | AC.2 | 0.505 | Prev. | 542070000 | 316853700 | 173854000
| Total | 0 | 0 | 0 | 0 | 732000 | 27000 | 32000 | 31000 |  |  |  | Total | 771700 |  |  |  | Total | 0 | 9.5 | 0 | 0.5 | 0 | 10.2 | 0.1 | 0 | mg/L | 4.3981 | 2.2073 | 0.066545 | 1.638 |  |  |  |  | Raw.Trb. | 1.556 | Cmb.Trb. | 0.025 | Total | 0 | 838200 | 35000
12 | Pres. | 234386000 | 2205380 | 5179090 | 8156300 | 284386000 | 2483410 | 7545450 | 12471900 | 671000 | 8000 | 679000 | now | 1281735900 |  | 0.11 | 1 | now | 3109.4 | 3846.3 | 40.9 | 57 | 3259.5 | 4052.8 | 71.5 | 10.5 | "/lb | 2.25 | 5.375 | 1.5 | 0 | 8 | Raw | 10 | 7.37 | ef.turb.1 | x | ef.turb.2 | 0.047 | Pres. | 542070000 | 318409200 | 173889000
| Prev | 234386000 | 2205380 | 5179090 | 8156300 | 283715000 | 2483410 | 7545450 | 12463900 |  |  |  | prev | 1280958100 |  |  |  | prev | 3109.4 | 3837.7 | 40.9 | 57 | 3259.5 | 4044.1 | 71.5 | 10.5 | Lbs. | 24.165 | 11.825 | 0.375 | 8 |  | Trtd | 9.2 | 7.75 | AC.1 | x | AC.2 | 2.688 | Prev. | 542070000 | 317691900 | 173889000
| Total | 0 | 0 | 0 | 0 | 671000 | 0 | 0 | 8000 |  |  |  | Total | 777800 |  |  |  | Total | 0 | 8.6 | 0 | 0 | 0 | 8.7 | 0 | 0 | mg/L | 4.3182 | 2.1131 | 0.06701 | 1.4296 |  |  |  |  | Raw.Trb. | 8.4 | Cmb.Trb. | 0.031 | Total | 0 | 717300 | 0
13 | Pres. | 234386000 | 2205380 | 5179090 | 8156300 | 285203000 | 2501410 | 7577440 | 12526900 | 817000 | 104990 | 921990 | now | 1282522500 |  | 0.19 | 1 | now | 3109.4 | 3856.7 | 40.9 | 57.3 | 3259.5 | 4064.1 | 71.7 | 10.5 | "/lb | 1.375 | 7.125 | 1.875 | 0 | 10 | Raw | 7.3 | 7.37 | ef.turb.1 | x | ef.turb.2 | 0.04 | Pres. | 542070000 | 319354600 | 173925000
| Prev | 234386000 | 2205380 | 5179090 | 8156300 | 284386000 | 2483410 | 7545450 | 12471900 |  |  |  | prev | 1281735900 |  |  |  | prev | 3109.4 | 3846.3 | 40.9 | 57 | 3259.5 | 4052.8 | 71.5 | 10.5 | Lbs. | 14.7675 | 15.675 | 0.46875 | 10 |  | Trtd | 8.9 | 7.89 | AC.1 | x | AC.2 | 0.96 | Prev. | 542070000 | 318409200 | 173889000
| Total | 0 | 0 | 0 | 0 | 817000 | 18000 | 31990 | 55000 |  |  |  | Total | 786600 |  |  |  | Total | 0 | 10.4 | 0 | 0.3 | 0 | 11.3 | 0.2 | 0 | mg/L | 2.1673 | 2.3005 | 0.068794 | 1.4676 |  |  |  |  | Raw.Trb. | 4.4 | Cmb.Trb. | 0.024 | Total | 0 | 945400 | 36000
14 | Pres. | 234386000 | 2205380 | 5179090 | 8156300 | 285861000 | 2502410 | 7609440 | 12568900 | 658000 | 75000 | 733000 | now | 1283286200 |  | 0.03 | 1.09 | now | 3109.4 | 3865.2 | 40.9 | 57.4 | 3259.5 | 4073.1 | 72.1 | 10.6 | "/lb | 1.625 | 5.875 | 1.875 | 0 | 8 | Raw | 8.5 | 7.21 | ef.turb.1 | x | ef.turb.2 | 0.041 | Pres. | 542070000 | 320093600 | 173996000
| Prev | 234386000 | 2205380 | 5179090 | 8156300 | 285203000 | 2501410 | 7577440 | 12526900 |  |  |  | prev | 1282522500 |  |  |  | prev | 3109.4 | 3856.7 | 40.9 | 57.3 | 3259.5 | 4064.1 | 71.7 | 10.5 | Lbs. | 17.4525 | 12.925 | 0.46875 | 8 |  | Trtd | 8.7 | 7.71 | AC.1 | x | AC.2 | 1.43 | Prev. | 542070000 | 319354600 | 173925000
| Total | 0 | 0 | 0 | 0 | 658000 | 1000 | 32000 | 42000 |  |  |  | Total | 763700 |  |  |  | Total | 0 | 8.5 | 0 | 0.1 | 0 | 9 | 0.4 | 0.1 | mg/L | 3.1803 | 2.3553 | 0.085418 | 1.4578 |  |  |  |  | Raw.Trb. | 3.4 | Cmb.Trb. | 0.026 | Total | 0 | 739000 | 71000
15 | Pres. | 234593000 | 2205380 | 5212090 | 8185310 | 286492000 | 2510410 | 7609440 | 12585000 | 838000 | 86110 | 924110 | now | 1284072700 |  | 0.19 | 0.98 | now | 3112.5 | 3873.2 | 40.9 | 57.4 | 3263 | 4081.4 | 72.1 | 10.6 | "/lb | 1.375 | 6.75 | 1.625 | 2 | 5 | Raw | 8.9 | 7.26 | ef.turb.1 | x | ef.turb.2 | 0.044 | Pres. | 542326000 | 320786400 | 173996000
| Prev | 234386000 | 2205380 | 5179090 | 8156300 | 285861000 | 2502410 | 7609440 | 12568900 |  |  |  | prev | 1283286200 |  |  |  | prev | 3109.4 | 3865.2 | 40.9 | 57.4 | 3259.5 | 4073.1 | 72.1 | 10.6 | Lbs. | 14.7675 | 14.85 | 0.40625 | 7 |  | Trtd | 8.7 | 7.66 | AC.1 | x | AC.2 | 1.662 | Prev. | 542070000 | 320093600 | 173996000
| Total | 207000 | 0 | 33000 | 29010 | 631000 | 8000 | 0 | 16100 |  |  |  | Total | 786500 |  |  |  | Total | 3.1 | 8 | 0 | 0 | 3.5 | 8.3 | 0 | 0 | mg/L | 2.113 | 2.1248 | 0.058128 | 1.0016 |  |  |  |  | Raw.Trb. | 3.04 | Cmb.Trb. | 0.034 | Total | 256000 | 692800 | 0
16 | Pres. | 234593000 | 2205380 | 5212090 | 8185310 | 287255000 | 2519410 | 7609440 | 12593000 | 763000 | 17000 | 780000 | now | 1284862900 |  | 0.08 | 1.01 | now | 3112.5 | 3882.9 | 40.9 | 57.6 | 3263 | 4091.5 | 72.1 | 10.6 | "/lb | 1.75 | 6.125 | 1.625 | 0 | 9 | Raw | 9.4 | 7.23 | ef.turb.1 | x | ef.turb.2 | 0.039 | Pres. | 542326000 | 321609200 | 173996000
| Prev | 234593000 | 2205380 | 5212090 | 8185310 | 286492000 | 2510410 | 7609440 | 12585000 |  |  |  | prev | 1284072700 |  |  |  | prev | 3112.5 | 3873.2 | 40.9 | 57.4 | 3263 | 4081.4 | 72.1 | 10.6 | Lbs. | 18.795 | 13.475 | 0.40625 | 9 |  | Trtd | 9.2 | 7.63 | AC.1 | x | AC.2 | 0.72 | Prev. | 542326000 | 320786400 | 173996000
| Total | 0 | 0 | 0 | 0 | 763000 | 9000 | 0 | 8000 |  |  |  | Total | 790200 |  |  |  | Total | 0 | 9.7 | 0 | 0.2 | 0 | 10.1 | 0 | 0 | mg/L | 2.9536 | 2.1176 | 0.063841 | 1.4143 |  |  |  |  | Raw.Trb. | 2.38 | Cmb.Trb. | 0.026 | Total | 0 | 822800 | 0
17 | Pres. | 234593000 | 2205380 | 5212090 | 8185310 | 288030000 | 2528410 | 7641440 | 12593000 | 775000 | 41000 | 816000 | now | 1285726700 |  | 0 | 0.97 | now | 3112.5 | 3892.8 | 40.9 | 57.7 | 3263 | 4101.9 | 72.2 | 10.6 | "/lb | 1.5 | 6.25 | 1.875 | 0 | 9 | Raw | 9 | 7.26 | ef.turb.1 | x | ef.turb.2 | 0.038 | Pres. | 542326000 | 322479400 | 174031000
| Prev | 234593000 | 2205380 | 5212090 | 8185310 | 287255000 | 2519410 | 7609440 | 12593000 |  |  |  | prev | 1284862900 |  |  |  | prev | 3112.5 | 3882.9 | 40.9 | 57.6 | 3263 | 4091.5 | 72.1 | 10.6 | Lbs. | 16.11 | 13.75 | 0.46875 | 9 |  | Trtd | 8.4 | 7.7 | AC.1 | x | AC.2 | 0.722 | Prev. | 542326000 | 321609200 | 173996000
| Total | 0 | 0 | 0 | 0 | 775000 | 9000 | 32000 | 0 |  |  |  | Total | 863800 |  |  |  | Total | 0 | 9.9 | 0 | 0.1 | 0 | 10.4 | 0.1 | 0 | mg/L | 2.4925 | 2.1273 | 0.072523 | 1.3924 |  |  |  |  | Raw.Trb. | 2.19 | Cmb.Trb. | 0.025 | Total | 0 | 870200 | 35000
18 | Pres. | 234593000 | 2205380 | 5212090 | 8185310 | 288667000 | 2537410 | 7641440 | 12639000 | 637000 | 55000 | 692000 | now | 1286416100 |  | 1.47 | 0.97 | now | 3112.5 | 3900.8 | 40.9 | 57.9 | 3263 | 4110.1 | 72.2 | 10.6 | "/lb | 1.1875 | 5.25 | 1.25 | 7 | 0 | Raw | 7.3 | 7.63 | ef.turb.1 | x | ef.turb.2 | 0.035 | Pres. | 542326000 | 323170940 | 174031000
| Prev | 234593000 | 2205380 | 5212090 | 8185310 | 288030000 | 2528410 | 7641440 | 12593000 |  |  |  | prev | 1285726700 |  |  |  | prev | 3112.5 | 3892.8 | 40.9 | 57.7 | 3263 | 4101.9 | 72.2 | 10.6 | Lbs. | 12.7538 | 11.55 | 0.3125 | 7 |  | Trtd | 8.4 | 7.85 | AC.1 | x | AC.2 | 0.63 | Prev. | 542326000 | 322479400 | 174031000
| Total | 0 | 0 | 0 | 0 | 637000 | 9000 | 0 | 46000 |  |  |  | Total | 689400 |  |  |  | Total | 0 | 8 | 0 | 0.2 | 0 | 8.2 | 0 | 0 | mg/L | 2.4007 | 2.1741 | 0.058823 | 1.3176 |  |  |  |  | Raw.Trb. | 2.01 | Cmb.Trb. | 0.024 | Total | 0 | 691540 | 0
19 | Pres. | 234593000 | 2205380 | 5212090 | 8185310 | 289549000 | 2546410 | 7674440 | 12672000 | 882000 | 75000 | 957000 | now | 1287195100 |  | 1.47 | 0.97 | now | 3112.5 | 3912.8 | 41 | 58 | 3263 | 4122.5 | 72.4 | 10.6 | "/lb | 4.25 | 7.375 | 2 | 11 | 0 | Raw | 10.3 | 7.25 | ef.turb.1 | x | ef.turb.2 | 0.037 | Pres. | 542326000 | 324147100 | 174066000
| Prev | 234593000 | 2205380 | 5212090 | 8185310 | 288667000 | 2537410 | 7641440 | 12639000 |  |  |  | prev | 1286416100 |  |  |  | prev | 3112.5 | 3900.8 | 40.9 | 57.9 | 3263 | 4110.1 | 72.2 | 10.6 | Lbs. | 45.645 | 16.225 | 0.5 | 11 |  | Trtd | 8.5 | 7.86 | AC.1 | x | AC.2 | 1.6 | Prev. | 542326000 | 323170940 | 174031000
| Total | 0 | 0 | 0 | 0 | 882000 | 9000 | 33000 | 33000 |  |  |  | Total | 779000 |  |  |  | Total | 0 | 12 | 0.1 | 0.1 | 0 | 12.4 | 0.2 | 0 | mg/L | 6.2052 | 2.2057 | 0.067973 | 1.4954 |  |  |  |  | Raw.Trb. | 7.07 | Cmb.Trb. | 0.024 | Total | 0 | 976160 | 35000
20 | Pres. | 234593000 | 2205380 | 5212090 | 8185310 | 290249000 | 2564410 | 7674440 | 12706000 | 700000 | 52000 | 752000 | now | 1288017000 |  | 0.39 | 0.99 | now | 3112.5 | 3922.7 | 41.2 | 58 | 3263 | 4133.2 | 72.4 | 10.6 | "/lb | 1 | 6.5 | 1.75 | 0 | 9 | Raw | 7.9 | 7.32 | ef.turb.1 | x | ef.turb.2 | 0.04 | Pres. | 542326000 | 324943800 | 174066000
| Prev | 234593000 | 2205380 | 5212090 | 8185310 | 289549000 | 2546410 | 7674440 | 12672000 |  |  |  | prev | 1287195100 |  |  |  | prev | 3112.5 | 3912.8 | 41 | 58 | 3263 | 4122.5 | 72.4 | 10.6 | Lbs. | 10.74 | 14.3 | 0.4375 | 9 |  | Trtd | 8.3 | 7.84 | AC.1 | x | AC.2 | 5.29 | Prev. | 542326000 | 324147100 | 174066000
| Total | 0 | 0 | 0 | 0 | 700000 | 18000 | 0 | 34000 |  |  |  | Total | 821900 |  |  |  | Total | 0 | 9.9 | 0.2 | 0 | 0 | 10.7 | 0 | 0 | mg/L | 1.8397 | 2.4495 | 0.07494 | 1.5416 |  |  |  |  | Raw.Trb. | 20.05 | Cmb.Trb. | 0.032 | Total | 0 | 796700 | 0
21 | Pres. | 234593000 | 2205380 | 5212090 | 8185310 | 290904000 | 2573410 | 7705430 | 12748000 | 655000 | 81990 | 736990 | now | 1288782800 |  | 0.18 | 1.04 | now | 3112.5 | 3931.2 | 41.4 | 58.1 | 3263 | 4142.2 | 72.4 | 10.6 | "/lb | 1.9375 | 5.375 | 1.5 | 0 | 6 | Raw | 9.7 | 7.08 | ef.turb.1 | x | ef.turb.2 | 0.049 | Pres. | 542326000 | 325690900 | 174100000
| Prev | 234593000 | 2205380 | 5212090 | 8185310 | 290249000 | 2564410 | 7674440 | 12706000 |  |  |  | prev | 1288017000 |  |  |  | prev | 3112.5 | 3922.7 | 41.2 | 58 | 3263 | 4133.2 | 72.4 | 10.6 | Lbs. | 20.8087 | 11.825 | 0.375 | 6 |  | Trtd | 9.4 | 7.01 | AC.1 | x | AC.2 | 3.367 | Prev. | 542326000 | 324943800 | 174066000
| Total | 0 | 0 | 0 | 0 | 655000 | 9000 | 30990 | 42000 |  |  |  | Total | 765800 |  |  |  | Total | 0 | 8.5 | 0.2 | 0.1 | 0 | 9 | 0 | 0 | mg/L | 3.8092 | 2.1647 | 0.068647 | 1.0984 |  |  |  |  | Raw.Trb. | 12.63 | Cmb.Trb. | 0.035 | Total | 0 | 747100 | 34000
22 | Pres. | 234593000 | 2205380 | 5212090 | 8185310 | 291725000 | 2582410 | 7737430 | 12789000 | 821000 | 82000 | 903000 | now | 1289576200 |  | 0.52 | 1.01 | now | 3112.5 | 3941.8 | 41.6 | 58.2 | 3263 | 4153.4 | 72.8 | 10.6 | "/lb | 1.9375 | 6.875 | 1.75 | 0 | 10 | Raw | 10.4 | 7.18 | ef.turb.1 | x | ef.turb.2 | 0.043 | Pres. | 542326000 | 326611800 | 174136000
| Prev | 234593000 | 2205380 | 5212090 | 8185310 | 290904000 | 2573410 | 7705430 | 12748000 |  |  |  | prev | 1288782800 |  |  |  | prev | 3112.5 | 3931.2 | 41.4 | 58.1 | 3263 | 4142.2 | 72.4 | 10.6 | Lbs. | 20.8087 | 15.125 | 0.4375 | 10 |  | Trtd | 10.1 | 7.06 | AC.1 | x | AC.2 | 1.164 | Prev. | 542326000 | 325690900 | 174100000
| Total | 0 | 0 | 0 | 0 | 821000 | 9000 | 32000 | 41000 |  |  |  | Total | 793400 |  |  |  | Total | 0 | 10.6 | 0.2 | 0.1 | 0 | 11.2 | 0.4 | 0 | mg/L | 3.039 | 2.209 | 0.063895 | 1.4605 |  |  |  |  | Raw.Trb. | 5.69 | Cmb.Trb. | 0.029 | Total | 0 | 920900 | 36000
23 | Pres. | 234593000 | 2205380 | 5212090 | 8185310 | 292615000 | 2591400 | 7770430 | 12825000 | 890000 | 77990 | 967990 | now | 1290513600 |  | 0.31 | 1 | now | 3112.5 | 3953.2 | 41.6 | 58.3 | 3263 | 4165.3 | 73 | 10.6 | "/lb | 2.5 | 7.375 | 0 | 0 | 10 | Raw | 9.9 | 7.22 | ef.turb.1 | x | ef.turb.2 | 0.041 | Pres. | 542326000 | 327601500 | 174171000
| Prev | 234593000 | 2205380 | 5212090 | 8185310 | 291725000 | 2582410 | 7737430 | 12789000 |  |  |  | prev | 1289576200 |  |  |  | prev | 3112.5 | 3941.8 | 41.6 | 58.2 | 3263 | 4153.4 | 72.8 | 10.6 | Lbs. | 26.85 | 16.225 | 0 | 10 |  | Trtd | 9.7 | 7.13 | AC.1 | x | AC.2 | 1.505 | Prev. | 542326000 | 326611800 | 174136000
| Total | 0 | 0 | 0 | 0 | 890000 | 8990 | 33000 | 36000 |  |  |  | Total | 937400 |  |  |  | Total | 0 | 11.4 | 0 | 0.1 | 0 | 11.9 | 0.2 | 0 | mg/L | 3.6173 | 2.1859 | 0 | 1.3472 |  |  |  |  | Raw.Trb. | 6.89 | Cmb.Trb. | 0.026 | Total | 0 | 989700 | 35000
24 | Pres. | 234593000 | 2205380 | 5212090 | 8185310 | 293302000 | 2600400 | 7770430 | 12834100 | 687000 | 18100 | 705100 | now | 1291215400 |  | 0.25 | 1.03 | now | 3112.5 | 3961.9 | 41.6 | 58.5 | 3263 | 4174.3 | 73 | 10.6 | "/lb | 1.625 | 5.75 | 1.75 | 0 | 7 | Raw | 8.2 | 7.39 | ef.turb.1 | x | ef.turb.2 | 0.04 | Pres. | 542326000 | 328345400 | 174171000
| Prev | 234593000 | 2205380 | 5212090 | 8185310 | 292615000 | 2591400 | 7770430 | 12825000 |  |  |  | prev | 1290513600 |  |  |  | prev | 3112.5 | 3953.2 | 41.6 | 58.3 | 3263 | 4165.3 | 73 | 10.6 | Lbs. | 17.4525 | 12.65 | 0.4375 | 7 |  | Trtd | 8.8 | 7.25 | AC.1 | x | AC.2 | 1.003 | Prev. | 542326000 | 327601500 | 174171000
| Total | 0 | 0 | 0 | 0 | 687000 | 9000 | 0 | 9100 |  |  |  | Total | 701800 |  |  |  | Total | 0 | 8.7 | 0 | 0.2 | 0 | 9 | 0 | 0 | mg/L | 3.046 | 2.2078 | 0.076358 | 1.2217 |  |  |  |  | Raw.Trb. | 3.9 | Cmb.Trb. | 0.027 | Total | 0 | 743900 | 0
25 | Pres. | 234593000 | 2205380 | 5212090 | 8185310 | 293937000 | 2609400 | 7801430 | 12880100 | 635000 | 86000 | 721000 | now | 1291956200 |  | 0.06 | 1.04 | now | 3112.5 | 3970.1 | 41.8 | 58.5 | 3263 | 4183.1 | 73.1 | 10.6 | "/lb | 1.5 | 5.25 | 1.5 | 0 | 6 | Raw | 8.6 | 7.24 | ef.turb.1 | x | ef.turb.2 | 0.04 | Pres. | 542326000 | 329075800 | 174206000
| Prev | 234593000 | 2205380 | 5212090 | 8185310 | 293302000 | 2600400 | 7770430 | 12834100 |  |  |  | prev | 1291215400 |  |  |  | prev | 3112.5 | 3961.9 | 41.6 | 58.5 | 3263 | 4174.3 | 73 | 10.6 | Lbs. | 16.11 | 11.55 | 0.375 | 6 |  | Trtd | 8.7 | 7.37 | AC.1 | x | AC.2 | 1.184 | Prev. | 542326000 | 328345400 | 174171000
| Total | 0 | 0 | 0 | 0 | 635000 | 9000 | 31000 | 46000 |  |  |  | Total | 740800 |  |  |  | Total | 0 | 8.2 | 0.2 | 0 | 0 | 8.8 | 0.1 | 0 | mg/L | 3.042 | 2.1809 | 0.070809 | 1.133 |  |  |  |  | Raw.Trb. | 3.62 | Cmb.Trb. | 0.025 | Total | 0 | 730400 | 35000
26 | Pres. | 234593000 | 2205380 | 5212090 | 8185310 | 294611000 | 2609400 | 7801430 | 12880100 | 674000 | 0 | 674000 | now | 1292717200 |  | 0.01 | 1.02 | now | 3112.5 | 3978.6 | 41.8 | 58.8 | 3263 | 4191.6 | 73.1 | 10.6 | "/lb | 1.5 | 6.25 | 1.5 | 8 | 0 | Raw | 8 | 7.19 | ef.turb.1 | x | ef.turb.2 | 0.039 | Pres. | 542326000 | 329785100 | 174206000
| Prev | 234593000 | 2205380 | 5212090 | 8185310 | 293937000 | 2609400 | 7801430 | 12880100 |  |  |  | prev | 1291956200 |  |  |  | prev | 3112.5 | 3970.1 | 41.8 | 58.5 | 3263 | 4183.1 | 73.1 | 10.6 | Lbs. | 16.11 | 13.75 | 0.375 | 8 |  | Trtd | 7.7 | 7.39 | AC.1 | x | AC.2 | 1.555 | Prev. | 542326000 | 329075800 | 174206000
| Total | 0 | 0 | 0 | 0 | 674000 | 0 | 0 | 0 |  |  |  | Total | 761000 |  |  |  | Total | 0 | 8.5 | 0 | 0.3 | 0 | 8.5 | 0 | 0 | mg/L | 2.866 | 2.4461 | 0.066712 | 1.4232 |  |  |  |  | Raw.Trb. | 3.11 | Cmb.Trb. | 0.026 | Total | 0 | 709300 | 0
27 | Pres. | 235502000 | 2214380 | 5212090 | 8357380 | 294611000 | 2609400 | 7801430 | 12880100 | 909000 | 181070 | 1090070 | now | 1293510900 |  | 0 | 1.04 | now | 3123.5 | 3978.6 | 41.9 | 58.8 | 3276.3 | 4191.6 | 73.1 | 10.6 | "/lb | 1.75 | 6.375 | 1.875 | 8 | 0 | Raw | 4.6 | 7.48 | ef.turb.1 | 0.06 | ef.turb.2 | x | Pres. | 543507000 | 329785100 | 174206000
| Prev | 234593000 | 2205380 | 5212090 | 8185310 | 294611000 | 2609400 | 7801430 | 12880100 |  |  |  | prev | 1292717200 |  |  |  | prev | 3112.5 | 3978.6 | 41.8 | 58.8 | 3263 | 4191.6 | 73.1 | 10.6 | Lbs. | 18.795 | 14.025 | 0.46875 | 8 |  | Trtd | 7.4 | 7.4 | AC.1 | 0.62 | AC.2 | x | Prev. | 542326000 | 329785100 | 174206000
| Total | 909000 | 9000 | 0 | 172070 | 0 | 0 | 0 | 0 |  |  |  | Total | 793700 |  |  |  | Total | 11 | 0 | 0.1 | 0 | 13.3 | 0 | 0 | 0 | mg/L | 2.4792 | 1.85 | 0.061832 | 1.0553 |  |  |  |  | Raw.Trb. | 2.7 | Cmb.Trb. | 0.033 | Total | 1181000 | 0 | 0
28 | Pres. | 236353000 | 2214380 | 5244080 | 8422400 | 294611000 | 2609400 | 7801430 | 12880100 | 851000 | 97010 | 948010 | now | 1294328800 |  | 0.21 | 1.03 | now | 3134.3 | 3978.6 | 41.9 | 58.8 | 3288.1 | 4191.6 | 73.3 | 10.6 | "/lb | 1.75 | 7.125 | 2 | 8 | 0 | Raw | 4.4 | 7.48 | ef.turb.1 | 0.045 | ef.turb.2 | x | Pres. | 544502000 | 329785100 | 174241000
| Prev | 235502000 | 2214380 | 5212090 | 8357380 | 294611000 | 2609400 | 7801430 | 12880100 |  |  |  | prev | 1293510900 |  |  |  | prev | 3123.5 | 3978.6 | 41.9 | 58.8 | 3276.3 | 4191.6 | 73.1 | 10.6 | Lbs. | 18.795 | 15.675 | 0.5 | 8 |  | Trtd | 6.6 | 7.45 | AC.1 | 0.94 | AC.2 | x | Prev. | 543507000 | 329785100 | 174206000
| Total | 851000 | 0 | 31990 | 65020 | 0 | 0 | 0 | 0 |  |  |  | Total | 817900 |  |  |  | Total | 10.8 | 0 | 0 | 0 | 11.8 | 0 | 0.2 | 0 | mg/L | 2.6482 | 2.2086 | 0.070449 | 1.1272 |  |  |  |  | Raw.Trb. | 1.94 | Cmb.Trb. | 0.03 | Total | 995000 | 0 | 35000
29 | Pres. | 237119000 | 2224380 | 5276080 | 8484430 | 294611000 | 2609400 | 7801430 | 12880100 | 766000 | 104030 | 870030 | now | 1295128200 |  | 0.04 | 1.01 | now | 3144.1 | 3978.6 | 42.1 | 58.8 | 3298.8 | 4191.6 | 73.5 | 10.7 | "/lb | 1.25 | 6.25 | 1.625 | 7 | 0 | Raw | 8.5 | 7.22 | ef.turb.1 | 0.05 | ef.turb.2 | x | Pres. | 545403000 | 329785100 | 174276000
| Prev | 236353000 | 2214380 | 5244080 | 8422400 | 294611000 | 2609400 | 7801430 | 12880100 |  |  |  | prev | 1294328800 |  |  |  | prev | 3134.3 | 3978.6 | 41.9 | 58.8 | 3288.1 | 4191.6 | 73.3 | 10.6 | Lbs. | 13.425 | 13.75 | 0.40625 | 7 |  | Trtd | 7.9 | 7.45 | AC.1 | 0.566 | AC.2 | x | Prev. | 544502000 | 329785100 | 174241000
| Total | 766000 | 10000 | 32000 | 62030 | 0 | 0 | 0 | 0 |  |  |  | Total | 799400 |  |  |  | Total | 9.8 | 0 | 0.2 | 0 | 10.7 | 0 | 0.2 | 0.1 | mg/L | 2.1015 | 2.1523 | 0.063591 | 1.0957 |  |  |  |  | Raw.Trb. | 1.82 | Cmb.Trb. | 0.028 | Total | 901000 | 0 | 35000
30 | Pres. | 238122000 | 2224380 | 5276080 | 8492430 | 294611000 | 2609400 | 7801430 | 12880100 | 1003000 | 8000 | 1011000 | now | 1296063200 |  | 0.04 | 0.99 | now | 3156.2 | 3978.6 | 42.1 | 58.8 | 3311.8 | 4191.6 | 73.5 | 10.7 | "/lb | 1.5 | 8.3125 | 2 | 10 | 0 | Raw | 5.7 | 7.35 | ef.turb.1 | 0.07 | ef.turb.2 | x | Pres. | 546495000 | 329785100 | 174312000
| Prev | 237119000 | 2224380 | 5276080 | 8484430 | 294611000 | 2609400 | 7801430 | 12880100 |  |  |  | prev | 1295128200 |  |  |  | prev | 3144.1 | 3978.6 | 42.1 | 58.8 | 3298.8 | 4191.6 | 73.5 | 10.7 | Lbs. | 16.11 | 18.2875 | 0.5 | 10 |  | Trtd | 6.4 | 7.51 | AC.1 | 0.85 | AC.2 | x | Prev. | 545403000 | 329785100 | 174276000
| Total | 1003000 | 0 | 0 | 8000 | 0 | 0 | 0 | 0 |  |  |  | Total | 935000 |  |  |  | Total | 12.1 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | mg/L | 1.9259 | 2.1862 | 0.059773 | 1.1955 |  |  |  |  | Raw.Trb. | 1.63 | Cmb.Trb. | 0.04 | Total | 1092000 | 0 | 36000
31 | Pres. | 238690000 | 2224380 | 5308080 | 8544450 | 294611000 | 2609400 | 7801430 | 12880100 | 568000 | 84020 | 652020 | now | 1296806900 |  | 0.05 | 1.02 | now | 3164.2 | 3978.6 | 42.2 | 58.8 | 3319.8 | 4191.6 | 73.6 | 10.7 | "/lb | 1 | 4.5 | 1.125 | 6 | 0 | Raw | 5 | 7.59 | ef.turb.1 | 0.045 | ef.turb.2 | x | Pres. | 547177000 | 329785100 | 174312000
| Prev | 238122000 | 2224380 | 5276080 | 8492430 | 294611000 | 2609400 | 7801430 | 12880100 |  |  |  | prev | 1296063200 |  |  |  | prev | 3156.2 | 3978.6 | 42.1 | 58.8 | 3311.8 | 4191.6 | 73.5 | 10.7 | Lbs. | 10.74 | 9.9 | 0.28125 | 6 |  | Trtd | 6.3 | 7.62 | AC.1 | 0.69 | AC.2 | x | Prev. | 546495000 | 329785100 | 174312000
| Total | 568000 | 0 | 32000 | 52020 | 0 | 0 | 0 | 0 |  |  |  | Total | 743700 |  |  |  | Total | 8 | 0 | 0.1 | 0 | 8 | 0 | 0.1 | 0 | mg/L | 2.2672 | 2.0899 | 0.059372 | 1.2666 |  |  |  |  | Raw.Trb. | 1.7 | Cmb.Trb. | 0.024 | Total | 682000 | 0 | 0
[10 empty] | Totals | [6 empty] | AVG | [10 empty] | totals | [5 empty] | AVG TRTD |  |  |  | Avg.Cmb.Trb.
[10 empty] | 23416000 | 1900410 | 25316410 |  | 24400000 |  | 5.76 | 1.0019 | [5 empty] | 70.7 | 247.2 |  |  |  | 581.9738 | 426.3875 | 12.6406 | 257 |  |  | 9.0742 | 7.5697 |  |  | 0.028548
[22 empty] | total- | 317.9