## Jan
January, 2020
Day | Value | Influent | Influent 2 | Combined Inf | Backwash | Backwash 2 | Comb. BW | Totalizer | EP-1 | FE-1 | FE-2 | BWP-1 | BWP-2 | SWP-1 | SWP-2 | BL-1 | Residual | Rain | Value | ACH | ACH-2 | Comb Lbs. | SA | SA-2 | Comb Lbs. | Polymer | Chlorine | Chlorine2 | Comb. Cl2 | Value | Raw | Finished
1 | Present | 111009 | 388877 | 953000 | 154873 | 123676 | 35000 | 525726400 | 4185.7 | 42478.9 | 37192.2 | 385.8 | 931.5 | 330.3 | 691 | 222.7 | 0.99 | 0.14 | inches | 1 | 0 | 35.195 | 7.625 | 0 | 16.775 | 2 | 9 | 0 | 9 | Turbidity | 1.56 | 0.036
| Previous | 110056 | 388877 |  | 154838 | 123676 |  | 524834600 | 4174.1 | 42478.9 | 37192.2 | 385.7 | 931.5 | 330.3 | 691 | 222.7 |  |  | Lbs. | 35.195 | 0 |  | 16.775 | 0 |  | 0.5 |  |  |  | Temp. | 10.4 | 8.3
| Total | 953000 | 0 |  | 35000 | 0 |  | 891800 | 11.6 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 |  |  | mg/L | 4.4281 | 0 |  | 2.1106 | 0 |  | 0.062909 | 1.1324 | 0 |  | pH | 7.38 | 7.55
2 | Present | 112080 | 388877 | 1071000 | 154908 | 123676 | 35000 | 526702900 | 4198.9 | 42478.9 | 37192.2 | 385.9 | 931.5 | 330.4 | 691 | 222.7 | 1.01 | 0 | inches | 1 | 0 | 35.195 | 9.25 | 0 | 20.35 | 2.5 | 11 | 0 | 11 | Turbidity | 2.06 | 0.035
| Total | 1071000 | 0 |  | 35000 | 0 |  | 976500 | 13.2 | 0 | 0 | 0.1 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 35.195 | 0 |  | 20.35 | 0 |  | 0.625 |  |  |  | Temp. | 10.5 | 8.5
[19 empty] | mg/L | 3.9403 | 0 |  | 2.2783 | 0 |  | 0.069972 | 1.2315 | 0 |  | pH | 7.28 | 7.49
3 | Present | 112882 | 388877 | 802000 | 154908 | 123676 | 0 | 527699100 | 4208.6 | 42478.9 | 37192.2 | 385.9 | 931.5 | 330.4 | 691 | 222.8 | 0.97 | 0.53 | inches | 0.4375 | 0 | 15.3978 | 6.625 | 0 | 14.575 | 2.375 | 8 | 0 | 8 | Turbidity | 1.59 | 0.032
| Total | 802000 | 0 |  | 0 | 0 |  | 996200 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 15.3978 | 0 |  | 14.575 | 0 |  | 0.59375 |  |  |  | Temp. | 10.5 | 11.1
[19 empty] | mg/L | 2.3021 | 0 |  | 2.1791 | 0 |  | 0.088769 | 1.1961 | 0 |  | pH | 7.46 | 7.51
4 | Present | 114100 | 388877 | 1218000 | 154944 | 123676 | 36000 | 528627600 | 4223.7 | 42478.9 | 37192.2 | 386.1 | 931.5 | 330.4 | 691 | 222.8 | 0.98 | 0.21 | inches | 0.875 | 0 | 30.7956 | 10.5 | 0 | 23.1 | 2.5 | 13 | 0 | 13 | Turbidity | 1.44 | 0.033
| Total | 1218000 | 0 |  | 36000 | 0 |  | 928500 | 15.1 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 |  |  | Lbs. | 30.7956 | 0 |  | 23.1 | 0 |  | 0.625 |  |  |  | Temp. | 9.9 | 10.5
[19 empty] | mg/L | 3.0316 | 0 |  | 2.274 | 0 |  | 0.061527 | 1.2798 | 0 |  | pH | 7.39 | 7.55
5 | Present | 114972 | 388877 | 872000 | 154944 | 123676 | 0 | 529600500 | 4234.4 | 42478.9 | 37192.2 | 386.1 | 931.5 | 330.4 | 691 | 222.9 | 1.02 | 0.27 | inches | 0.625 | 0 | 21.9969 | 6.75 | 0 | 14.85 | 1.625 | 9 | 0 | 9 | Turbidity | 2.18 | 0.037
| Total | 872000 | 0 |  | 0 | 0 |  | 972900 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 21.9969 | 0 |  | 14.85 | 0 |  | 0.40625 |  |  |  | Temp. | 8 | 10.2
[19 empty] | mg/L | 3.0247 | 0 |  | 2.0419 | 0 |  | 0.055861 | 1.2375 | 0 |  | pH | 7.44 | 7.7
6 | Present | 116050 | 388877 | 1078000 | 154979 | 123676 | 35000 | 530596900 | 4247.5 | 42478.9 | 37192.2 | 386.3 | 931.5 | 330.5 | 691 | 222.9 | 1.02 | 0.03 | inches | 0.875 | 0 | 30.7956 | 9.25 | 0 | 20.35 | 2.375 | 12 | 0 | 12 | Turbidity | 2.16 | 0.037
| Total | 1078000 | 0 |  | 35000 | 0 |  | 996400 | 13.1 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 30.7956 | 0 |  | 20.35 | 0 |  | 0.59375 |  |  |  | Temp. | 9.7 | 8.3
[19 empty] | mg/L | 3.4253 | 0 |  | 2.2635 | 0 |  | 0.066042 | 1.3347 | 0 |  | pH | 7.32 | 7.68
7 | Present | 116869 | 388877 | 819000 | 154979 | 123676 | 0 | 531568900 | 4257.6 | 42478.9 | 37192.2 | 386.3 | 931.5 | 330.5 | 691 | 222.9 | 0.93 | 0.32 | inches | 0.625 | 0 | 21.9969 | 7 | 0 | 15.4 | 1.875 | 9 | 0 | 9 | Turbidity | 2.78 | 0.034
| Total | 819000 | 0 |  | 0 | 0 |  | 972000 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 21.9969 | 0 |  | 15.4 | 0 |  | 0.46875 |  |  |  | Temp. | 10.1 | 9.7
[19 empty] | mg/L | 3.2204 | 0 |  | 2.2546 | 0 |  | 0.068626 | 1.3176 | 0 |  | pH | 7.37 | 7.55
8 | Present | 116869 | 389841 | 964000 | 154979 | 123711 | 35000 | 532537100 | 4257.6 | 42490.9 | 37204.2 | 386.3 | 931.8 | 330.5 | 691.3 | 222.9 | 0.99 | 0.29 | inches | 0 | 6.875 | 36.0938 | 0 | 4 | 8.8 | 0.875 | 0 | 15 | 15 | Turbidity | 5.32 | 0.05
| Total | 0 | 964000 |  | 0 | 35000 |  | 968200 | 0 | 12 | 12 | 0 | 0.3 | 0 | 0.3 | 0 |  |  | Lbs. | 0 | 36.0938 |  | 0 | 8.8 |  | 0.21875 |  |  |  | Temp. | 11.1 | 9.4
[19 empty] | mg/L | 0 | 4.4894 |  | 0 | 1.0946 |  | 0.027209 | 0 | 1.8657 |  | pH | 7.35 | 7.56
9 | Present | 117976 | 389841 | 1107000 | 155014 | 123711 | 35000 | 533543900 | 4271.1 | 42490.9 | 37204.2 | 386.4 | 931.8 | 330.6 | 691.3 | 223 | 1.03 | 0 | inches | 0.875 | 0 | 30.7956 | 9.25 | 0 | 20.35 | 2.375 | 11 | 0 | 11 | Turbidity | 6.03 | 0.038
| Total | 1107000 | 0 |  | 35000 | 0 |  | 1006800 | 13.5 | 0 | 0 | 0.1 | 0 | 0.1 | 0 | 0.1 |  |  | Lbs. | 30.7956 | 0 |  | 20.35 | 0 |  | 0.59375 |  |  |  | Temp. | 9.5 | 9.7
[19 empty] | mg/L | 3.3356 | 0 |  | 2.2042 | 0 |  | 0.064312 | 1.1915 | 0 |  | pH | 7.04 | 7.34
10 | Present | 118746 | 389841 | 770000 | 155049 | 123711 | 35000 | 534340100 | 4280.5 | 42490.9 | 37204.2 | 386.7 | 931.8 | 330.7 | 691.3 | 223 | 1.02 | 0.6 | inches | 0.5 | 0 | 17.5975 | 6.25 | 0 | 13.75 | 1.75 | 8 | 0 | 8 | Turbidity | 2.34 | 0.037
| Total | 770000 | 0 |  | 35000 | 0 |  | 796200 | 9.4 | 0 | 0 | 0.3 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 17.5975 | 0 |  | 13.75 | 0 |  | 0.4375 |  |  |  | Temp. | 8.5 | 10.5
[19 empty] | mg/L | 2.7403 | 0 |  | 2.1411 | 0 |  | 0.068127 | 1.2458 | 0 |  | pH | 7.39 | 7.42
11 | Present | 120008 | 389841 | 1262000 | 155084 | 123711 | 35000 | 535575100 | 4295.7 | 42490.9 | 37204.2 | 386.8 | 931.8 | 330.8 | 691.3 | 223.2 | 0.96 | 0.22 | inches | 1.5 | 0 | 52.7925 | 10.375 | 0 | 22.825 | 2.625 | 13 | 0 | 13 | Turbidity | 7.48 | 0.037
| Total | 1262000 | 0 |  | 35000 | 0 |  | 1235000 | 15.2 | 0 | 0 | 0.1 | 0 | 0.1 | 0 | 0.2 |  |  | Lbs. | 52.7925 | 0 |  | 22.825 | 0 |  | 0.65625 |  |  |  | Temp. | 9.5 | 8.7
[19 empty] | mg/L | 5.0159 | 0 |  | 2.1686 | 0 |  | 0.062351 | 1.2351 | 0 |  | pH | 7.18 | 7.39
12 | Present | 120910 | 389841 | 902000 | 155084 | 123711 | 0 | 536453600 | 4306.8 | 42490.9 | 37204.2 | 386.8 | 931.8 | 330.8 | 691.3 | 223.3 | 0.91 | 0.25 | inches | 1.75 | 0 | 61.5913 | 7.5 | 0 | 16.5 | 1.875 | 10 | 0 | 10 | Turbidity | 4.82 | 0.035
| Total | 902000 | 0 |  | 0 | 0 |  | 878500 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 61.5913 | 0 |  | 16.5 | 0 |  | 0.46875 |  |  |  | Temp. | 9.4 | 8.1
[19 empty] | mg/L | 8.1874 | 0 |  | 2.1934 | 0 |  | 0.062312 | 1.3293 | 0 |  | pH | 7.12 | 7.32
13 | Present | 122018 | 389841 | 1108000 | 155120 | 123711 | 36000 | 537428000 | 4320.2 | 42490.9 | 37204.2 | 386.9 | 931.8 | 330.8 | 691.3 | 223.3 | 0.92 | 0.22 | inches | 0.875 | 0 | 30.7956 | 9.125 | 0 | 20.075 | 2.375 | 13 | 0 | 13 | Turbidity | 4.73 | 0.032
| Total | 1108000 | 0 |  | 36000 | 0 |  | 974400 | 13.4 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 |  |  | Lbs. | 30.7956 | 0 |  | 20.075 | 0 |  | 0.59375 |  |  |  | Temp. | 9.6 | 8.3
[19 empty] | mg/L | 3.3326 | 0 |  | 2.1724 | 0 |  | 0.064254 | 1.4068 | 0 |  | pH | 7.21 | 7.4
14 | Present | 122917 | 389841 | 899000 | 155155 | 123711 | 35000 | 538419500 | 4331.1 | 42490.9 | 37204.2 | 387.1 | 931.8 | 330.9 | 691.3 | 223.4 | 0.95 | 0.01 | inches | 0.625 | 0 | 21.9969 | 7.375 | 0 | 16.225 | 2 | 11 | 0 | 11 | Turbidity | 3.62 | 0.033
| Total | 899000 | 0 |  | 35000 | 0 |  | 991500 | 10.9 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0.1 |  |  | Lbs. | 21.9969 | 0 |  | 16.225 | 0 |  | 0.5 |  |  |  | Temp. | 9.1 | 8.6
[19 empty] | mg/L | 2.9338 | 0 |  | 2.164 | 0 |  | 0.066687 | 1.4671 | 0 |  | pH | 7.33 | 7.6
15 | Present | 123893 | 389841 | 976000 | 155155 | 123711 | 0 | 539378400 | 4343.3 | 42490.9 | 37204.2 | 387.1 | 931.8 | 330.9 | 691.3 | 223.4 | 0.99 | 0.41 | inches | 0.625 | 0 | 21.9969 | 8.25 | 0 | 18.15 | 2.125 | 12 | 0 | 12 | Turbidity | 2.99 | 0.049
| Total | 976000 | 0 |  | 0 | 0 |  | 958900 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 21.9969 | 0 |  | 18.15 | 0 |  | 0.53125 |  |  |  | Temp. | 8.8 | 8
[19 empty] | mg/L | 2.7024 | 0 |  | 2.2298 | 0 |  | 0.065265 | 1.4742 | 0 |  | pH | 7.38 | 7.69
16 | Present | 125022 | 389841 | 1129000 | 155190 | 123711 | 35000 | 540412000 | 4357 | 42490.9 | 37204.2 | 387.3 | 931.8 | 331 | 691.3 | 223.5 | 1.08 | 0.03 | inches | 0.875 | 0 | 30.7956 | 9.375 | 0 | 20.625 | 2.5 | 13 | 0 | 13 | Turbidity | 2.67 | 0.034
| Total | 1129000 | 0 |  | 35000 | 0 |  | 1033600 | 13.7 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0.1 |  |  | Lbs. | 30.7956 | 0 |  | 20.625 | 0 |  | 0.625 |  |  |  | Temp. | 9.5 | 8.2
[19 empty] | mg/L | 3.2706 | 0 |  | 2.1905 | 0 |  | 0.066377 | 1.3806 | 0 |  | pH | 7.26 | 7.69
17 | Present | 125858 | 389841 | 836000 | 155190 | 123711 | 0 | 541279400 | 4367.4 | 42490.9 | 37204.2 | 387.3 | 931.8 | 331 | 691.3 | 223.5 | 1.07 | 0.09 | inches | 0.625 | 0 | 21.9969 | 7.125 | 0 | 15.675 | 2.125 | 10 | 0 | 10 | Turbidity | 2.68 | 0.03
| Total | 836000 | 0 |  | 0 | 0 |  | 867400 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 21.9969 | 0 |  | 15.675 | 0 |  | 0.53125 |  |  |  | Temp. | 9.4 | 8.7
[19 empty] | mg/L | 3.1549 | 0 |  | 2.2482 | 0 |  | 0.076195 | 1.4343 | 0 |  | pH | 7.32 | 7.6
18 | Present | 126864 | 389841 | 1006000 | 155225 | 123711 | 35000 | 542339400 | 4379.6 | 42490.9 | 37204.2 | 387.4 | 931.8 | 331 | 691.3 | 223.5 | 1.09 | 0.01 | inches | 0.625 | 0 | 21.9969 | 9.5 | 0 | 20.9 | 2.125 | 11 | 0 | 11 | Turbidity | 2.43 | 0.031
| Total | 1006000 | 0 |  | 35000 | 0 |  | 1060000 | 12.2 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 |  |  | Lbs. | 21.9969 | 0 |  | 20.9 | 0 |  | 0.53125 |  |  |  | Temp. | 9 | 9.8
[19 empty] | mg/L | 2.6218 | 0 |  | 2.491 | 0 |  | 0.063319 | 1.3111 | 0 |  | pH | 7.4 | 7.61
19 | Present | 128031 | 389841 | 1167000 | 155260 | 123711 | 35000 | 543224500 | 4393.8 | 42490.9 | 37204.2 | 387.6 | 931.8 | 331.1 | 691.3 | 223.7 | 1.02 | 0 | inches | 0.75 | 0 | 26.3963 | 9.25 | 0 | 20.35 | 2.5 | 13 | 0 | 13 | Turbidity | 2.26 | 0.03
| Total | 1167000 | 0 |  | 35000 | 0 |  | 885100 | 14.2 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0.2 |  |  | Lbs. | 26.3963 | 0 |  | 20.35 | 0 |  | 0.625 |  |  |  | Temp. | 10.6 | 9.9
[19 empty] | mg/L | 2.7121 | 0 |  | 2.0909 | 0 |  | 0.064216 | 1.3357 | 0 |  | pH | 7.38 | 7.6
20 | Present | 128884 | 389841 | 853000 | 155296 | 123711 | 36000 | 544282100 | 4404.3 | 42490.9 | 37204.2 | 387.8 | 931.8 | 331.2 | 691.3 | 223.7 | 1.02 | 0.23 | inches | 0.625 | 0 | 21.9969 | 6.625 | 0 | 14.575 | 1.75 | 10 | 0 | 10 | Turbidity | 2.06 | 0.029
| Total | 853000 | 0 |  | 36000 | 0 |  | 1057600 | 10.5 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 21.9969 | 0 |  | 14.575 | 0 |  | 0.4375 |  |  |  | Temp. | 10.9 | 10.7
[19 empty] | mg/L | 3.092 | 0 |  | 2.0488 | 0 |  | 0.061498 | 1.4057 | 0 |  | pH | 7.41 | 7.58
21 | Present | 129899 | 389841 | 1015000 | 155331 | 123711 | 35000 | 545291500 | 4416.8 | 42490.9 | 37204.2 | 387.9 | 931.8 | 331.2 | 691.3 | 223.7 | 1.02 | 0.01 | inches | 0.75 | 0 | 26.3963 | 8.625 | 0 | 18.975 | 2.25 | 12 | 0 | 12 | Turbidity | 1.95 | 0.028
| Total | 1015000 | 0 |  | 35000 | 0 |  | 1009400 | 12.5 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 |  |  | Lbs. | 26.3963 | 0 |  | 18.975 | 0 |  | 0.5625 |  |  |  | Temp. | 10.7 | 8.9
[19 empty] | mg/L | 3.1182 | 0 |  | 2.2416 | 0 |  | 0.066449 | 1.4176 | 0 |  | pH | 7.27 | 7.6
22 | Present | 131015 | 389841 | 1116000 | 155366 | 123711 | 35000 | 546234400 | 4430.4 | 42490.9 | 37204.2 | 388.1 | 931.8 | 331.3 | 691.3 | 223.8 | 1.01 | 0.04 | inches | 0.875 | 0 | 30.7956 | 9.5 | 0 | 20.9 | 2.375 | 13 | 0 | 13 | Turbidity | 2.15 | 0.03
| Total | 1116000 | 0 |  | 35000 | 0 |  | 942900 | 13.6 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0.1 |  |  | Lbs. | 30.7956 | 0 |  | 20.9 | 0 |  | 0.59375 |  |  |  | Temp. | 9.7 | 9.4
[19 empty] | mg/L | 3.3087 | 0 |  | 2.2455 | 0 |  | 0.063793 | 1.3967 | 0 |  | pH | 7.53 | 7.76
23 | Present | 131979 | 389841 | 964000 | 155401 | 123711 | 35000 | 547235900 | 4441.8 | 42490.9 | 37204.2 | 388.3 | 931.8 | 331.4 | 691.3 | 223.9 | 1.07 | 0.42 | inches | 1 | 0 | 35.195 | 8.125 | 0 | 17.875 | 2.25 | 11 | 0 | 11 | Turbidity | 4.8 | 0.029
| Total | 964000 | 0 |  | 35000 | 0 |  | 1001500 | 11.4 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0.1 |  |  | Lbs. | 35.195 | 0 |  | 17.875 | 0 |  | 0.5625 |  |  |  | Temp. | 10.9 | 9.4
[19 empty] | mg/L | 4.3776 | 0 |  | 2.2233 | 0 |  | 0.069965 | 1.3682 | 0 |  | pH | 7.36 | 7.75
24 | Present | 132963 | 389841 | 984000 | 155436 | 123711 | 35000 | 548338800 | 4453.8 | 42490.9 | 37204.2 | 388.4 | 931.8 | 331.6 | 691.3 | 224.1 | 1.05 | 0.05 | inches | 0.75 | 0 | 26.3963 | 8.125 | 0 | 17.875 | 2.5 | 11 | 0 | 11 | Turbidity | 13.66 | 0.036
| Total | 984000 | 0 |  | 35000 | 0 |  | 1102900 | 12 | 0 | 0 | 0.1 | 0 | 0.2 | 0 | 0.2 |  |  | Lbs. | 26.3963 | 0 |  | 17.875 | 0 |  | 0.625 |  |  |  | Temp. | 10.6 | 9.5
[19 empty] | mg/L | 3.2165 | 0 |  | 2.1781 | 0 |  | 0.076159 | 1.3404 | 0 |  | pH | 7.37 | 7.74
25 | Present | 134020 | 389841 | 1057000 | 155436 | 123711 | 0 | 549317351 | 4466.3 | 42490.9 | 37204.2 | 388.5 | 931.8 | 331.6 | 691.3 | 224.2 | 1.06 | 0.25 | inches | 0.75 | 0 | 26.3963 | 8.625 | 0 | 18.975 | 2.125 | 10 | 0 | 10 | Turbidity | 3.69 | 0.036
| Total | 1057000 | 0 |  | 0 | 0 |  | 978551 | 12.5 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 26.3963 | 0 |  | 18.975 | 0 |  | 0.53125 |  |  |  | Temp. | 10.6 | 9.8
[19 empty] | mg/L | 2.9943 | 0 |  | 2.1525 | 0 |  | 0.060264 | 1.1344 | 0 |  | pH | 7.26 | 7.7
26 | Present | 134935 | 389841 | 915000 | 155471 | 123711 | 35000 | 550255200 | 4477.9 | 42490.9 | 37204.2 | 388.6 | 931.8 | 331.6 | 691.3 | 224.3 | 1.13 | 0.08 | inches | 0.75 | 0 | 26.3963 | 7.5 | 0 | 16.5 | 2.125 | 10 | 0 | 10 | Turbidity | 4.12 | 0.037
| Total | 915000 | 0 |  | 35000 | 0 |  | 937849 | 11.6 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 26.3963 | 0 |  | 16.5 | 0 |  | 0.53125 |  |  |  | Temp. | 10.7 | 9.5
[19 empty] | mg/L | 3.459 | 0 |  | 2.1622 | 0 |  | 0.069616 | 1.3104 | 0 |  | pH | 7.36 | 7.61
27 | Present | 134935 | 391157 | 1316000 | 155471 | 123746 | 35000 | 551244100 | 4477.9 | 42507.3 | 37220.5 | 388.6 | 932.1 | 331.6 | 691.5 | 224.3 | 1.1 | 0.68 | inches | 0 | 7.125 | 37.4062 | 0 | 5.5 | 12.1 | 0.75 | 0 | 15 | 15 | Turbidity | 2.86 | 0.037
| Total | 0 | 1316000 |  | 0 | 35000 |  | 988900 | 0 | 16.4 | 16.3 | 0 | 0.3 | 0 | 0.2 | 0 |  |  | Lbs. | 0 | 37.4062 |  | 0 | 12.1 |  | 0.1875 |  |  |  | Temp. | 10.2 | 8.6
[19 empty] | mg/L | 0 | 3.4082 |  | 0 | 1.1025 |  | 0.068334 | 0 | 1.3667 |  | pH | 7.35 | 7.6
28 | Present | 135713 | 391157 | 778000 | 155507 | 123746 | 36000 | 552274600 | 4487.1 | 42507.3 | 37220.5 | 388.8 | 932.1 | 331.6 | 691.5 | 224.3 | 1.13 | 0.13 | inches | 0.75 | 0 | 26.3963 | 6.375 | 0 | 14.025 | 1.5 | 8 | 0 | 8 | Turbidity | 12.16 | 0.064
| Total | 778000 | 0 |  | 36000 | 0 |  | 1030500 | 9.2 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 |  |  | Lbs. | 26.3963 | 0 |  | 14.025 | 0 |  | 0.375 |  |  |  | Temp. | 11.3 | 10.2
[19 empty] | mg/L | 4.0681 | 0 |  | 2.1615 | 0 |  | 0.057794 | 1.2329 | 0 |  | pH | 7.33 | 7.55
29 | Present | 136726 | 391157 | 1013000 | 155542 | 123746 | 35000 | 553258400 | 4499.3 | 42507.3 | 37220.5 | 388.9 | 932.1 | 331.7 | 691.5 | 224.5 | 1.12 | 0.41 | inches | 0.625 | 0 | 21.9969 | 8.375 | 0 | 18.425 | 3.375 | 10 | 0 | 10 | Turbidity | 7.45 | 0.032
| Total | 1013000 | 0 |  | 35000 | 0 |  | 983800 | 12.2 | 0 | 0 | 0.1 | 0 | 0.1 | 0 | 0.2 |  |  | Lbs. | 21.9969 | 0 |  | 18.425 | 0 |  | 0.84375 |  |  |  | Temp. | 11.3 | 10.3
[19 empty] | mg/L | 2.6037 | 0 |  | 2.1809 | 0 |  | 0.099871 | 1.1837 | 0 |  | pH | 7.25 | 7.5
30 | Present | 137847 | 391157 | 1121000 | 155577 | 123746 | 35000 | 554279300 | 4512.9 | 42507.3 | 37220.5 | 389.1 | 932.1 | 331.8 | 691.5 | 224.5 | 1.1 | 0.04 | inches | 0.625 | 0 | 21.9969 | 9.375 | 0 | 20.625 | 3.875 | 11 | 0 | 11 | Turbidity | 4.03 | 0.032
| Total | 1121000 | 0 |  | 35000 | 0 |  | 1020900 | 13.6 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 21.9969 | 0 |  | 20.625 | 0 |  | 0.96875 |  |  |  | Temp. | 10.9 | 10
[19 empty] | mg/L | 2.3528 | 0 |  | 2.2061 | 0 |  | 0.10362 | 1.1766 | 0 |  | pH | 7.26 | 7.49
31 | Present | 138682 | 391157 | 835000 | 155577 | 123746 | 0 | 555238200 | 4523.2 | 42507.3 | 37220.5 | 389.1 | 932.1 | 331.8 | 691.5 | 224.5 | 1.08 | 0.1 | inches | 0.625 | 0 | 21.9969 | 7 | 0 | 15.4 | 2.25 | 8 | 0 | 8 | Turbidity | 2.95 | 0.048
| Total | 835000 | 0 |  | 0 | 0 |  | 958900 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 21.9969 | 0 |  | 15.4 | 0 |  | 0.5625 |  |  |  | Temp. | 12.4 | 10.1
[19 empty] | mg/L | 3.1587 | 0 |  | 2.2114 | 0 |  | 0.080774 | 1.1488 | 0 |  | pH | 7.37 | 7.46
| Total | 28626000 | 2280000 | 30906000 | 739000 | 70000 | 809000 | 30403600 | 349.1 | 28.4 | 28.3 | 3.4 | 0.6 | 1.5 | 0.5 | 1.8 | N/A | 6.07 | Total Lbs. | 816.0841 | 73.5 | 889.5841 | 524.975 | 20.9 | 545.875 | 16.9062 | 0 | 0 | 340 | Avg Turb. | 3.8384 | 0.035032
| Average | 923419.3548 | 73548.3871 | 996967.7419 | 23838.7097 | 2258.0645 | 26096.7742 | 980761.2903 | 11.2613 | 0.91613 | 0.9129 | 0.10968 | 0.019355 | 0.048387 | 0.016129 | 0.058065 | 1.0271 | 0.19581 | Avg Lbs. | 26.3253 | 2.371 | 28.6963 | 16.9347 | 0.67419 | 17.6089 | 0.54536 | 0 | 0 | 10.9677 | Avg. Temp. | 9.7548 | 9.0613
| High | 1262000 | 1316000 | 2134000 | 36000 | 35000 | 70000 | 1235000 | 15.2 | 16.4 | 16.3 | 0.3 | 0.3 | 0.2 | 0.3 | 0.2 | 1.13 | 0.68 | High Lbs. | 61.5913 | 37.4062 | 61.5913 | 23.1 | 12.1 | 23.1 | 0.96875 | 0 | 0 | 15 | Avg pH | 7.0923 | 7.3258
| Low | 0 | 0 | 770000 | 0 | 0 | 0 | 796200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91 | 0 | Low Lbs. | 0 | 0 | 15.3978 | 0 | 0 | 8.8 | 0.1875 | 0 | 0 | 8
[19 empty] | Avg mg/L | 3.1977 | 0.25476 |  | 2.0551 | 0.070872 |  | 0.067822 | 1.2147 | 0.10427 |  | High Turb. | 13.66 | 0.064
[19 empty] | High mg/L | 8.1874 | 4.4894 |  | 2.491 | 1.1025 |  | 0.10362 | 1.4742 | 1.8657 |  | High Temp. | 12.4 | 11.1
[19 empty] | Low mg/L | 0 | 0 |  | 0 | 0 |  | 0.027209 | 0 | 0 |  | High pH | 7.53 | 7.76
*Averages, Highs and Lows represent only days the plant was in operation
[30 empty] | Low Turb. | 1.44 | 0.028
[30 empty] | Low Temp. | 8 | 8
[30 empty] | Low pH | 7.04 | 7.32

## JanTotals
January, 2020
Combined Plant Daily Totals
Day | Gallons |  |  |  | Plant Hours | Rain Inches | Chemical Usage |  |  |  |  | Finished Water |  |  | Residual Chlorine
| Influent | Backwash | Flush | Totalizer |  |  | Value | ACH | SodaAsh | Polymer | NaOCl | Turbidity | pH | Temp
1 | 953000 | 35000 | 0 | 891800 | 11.6 | 0.14 | Lbs. | 35.195 | 16.775 | 0.5 | 9 | 0.036 | 7.55 | 8.3 | 0.99
[7 empty] | mg/L | 4.4281 | 2.1106 | 0.062909 | 1.1324
2 | 1071000 | 35000 | 0 | 976500 | 13.2 | 0 | Lbs. | 35.195 | 20.35 | 0.625 | 11 | 0.035 | 7.49 | 8.5 | 1.01
[7 empty] | mg/L | 3.9403 | 2.2783 | 0.069972 | 1.2315
3 | 802000 | 0 | 15000 | 996200 | 9.7 | 0.53 | Lbs. | 15.3978 | 14.575 | 0.59375 | 8 | 0.032 | 7.51 | 11.1 | 0.97
[7 empty] | mg/L | 2.3021 | 2.1791 | 0.088769 | 1.1961
4 | 1218000 | 36000 | 0 | 928500 | 15.1 | 0.21 | Lbs. | 30.7956 | 23.1 | 0.625 | 13 | 0.033 | 7.55 | 10.5 | 0.98
[7 empty] | mg/L | 3.0316 | 2.274 | 0.061527 | 1.2798
5 | 872000 | 0 | 15000 | 972900 | 10.7 | 0.27 | Lbs. | 21.9969 | 14.85 | 0.40625 | 9 | 0.037 | 7.7 | 10.2 | 1.02
[7 empty] | mg/L | 3.0247 | 2.0419 | 0.055861 | 1.2375
6 | 1078000 | 35000 | 0 | 996400 | 13.1 | 0.03 | Lbs. | 30.7956 | 20.35 | 0.59375 | 12 | 0.037 | 7.68 | 8.3 | 1.02
[7 empty] | mg/L | 3.4253 | 2.2635 | 0.066042 | 1.3347
7 | 819000 | 0 | 0 | 972000 | 10.1 | 0.32 | Lbs. | 21.9969 | 15.4 | 0.46875 | 9 | 0.034 | 7.55 | 9.7 | 0.93
[7 empty] | mg/L | 3.2204 | 2.2546 | 0.068626 | 1.3176
8 | 964000 | 35000 | 0 | 968200 | 12 | 0.29 | Lbs. | 36.0938 | 8.8 | 0.21875 | 15 | 0.05 | 7.56 | 9.4 | 0.99
[7 empty] | mg/L | 2.2447 | 0.54728 | 0.027209 | 0.93286
9 | 1107000 | 35000 | 15000 | 1006800 | 13.5 | 0 | Lbs. | 30.7956 | 20.35 | 0.59375 | 11 | 0.038 | 7.34 | 9.7 | 1.03
[7 empty] | mg/L | 3.3356 | 2.2042 | 0.064312 | 1.1915
10 | 770000 | 35000 | 0 | 796200 | 9.4 | 0.6 | Lbs. | 17.5975 | 13.75 | 0.4375 | 8 | 0.037 | 7.42 | 10.5 | 1.02
[7 empty] | mg/L | 2.7403 | 2.1411 | 0.068127 | 1.2458
11 | 1262000 | 35000 | 30000 | 1235000 | 15.2 | 0.22 | Lbs. | 52.7925 | 22.825 | 0.65625 | 13 | 0.037 | 7.39 | 8.7 | 0.96
[7 empty] | mg/L | 5.0159 | 2.1686 | 0.062351 | 1.2351
12 | 902000 | 0 | 15000 | 878500 | 11.1 | 0.25 | Lbs. | 61.5913 | 16.5 | 0.46875 | 10 | 0.035 | 7.32 | 8.1 | 0.91
[7 empty] | mg/L | 8.1874 | 2.1934 | 0.062312 | 1.3293
13 | 1108000 | 36000 | 0 | 974400 | 13.4 | 0.22 | Lbs. | 30.7956 | 20.075 | 0.59375 | 13 | 0.032 | 7.4 | 8.3 | 0.92
[7 empty] | mg/L | 3.3326 | 2.1724 | 0.064254 | 1.4068
14 | 899000 | 35000 | 15000 | 991500 | 10.9 | 0.01 | Lbs. | 21.9969 | 16.225 | 0.5 | 11 | 0.033 | 7.6 | 8.6 | 0.95
[7 empty] | mg/L | 2.9338 | 2.164 | 0.066687 | 1.4671
15 | 976000 | 0 | 0 | 958900 | 12.2 | 0.41 | Lbs. | 21.9969 | 18.15 | 0.53125 | 12 | 0.049 | 7.69 | 8 | 0.99
[7 empty] | mg/L | 2.7024 | 2.2298 | 0.065265 | 1.4742
16 | 1129000 | 35000 | 15000 | 1033600 | 13.7 | 0.03 | Lbs. | 30.7956 | 20.625 | 0.625 | 13 | 0.034 | 7.69 | 8.2 | 1.08
[7 empty] | mg/L | 3.2706 | 2.1905 | 0.066377 | 1.3806
17 | 836000 | 0 | 0 | 867400 | 10.4 | 0.09 | Lbs. | 21.9969 | 15.675 | 0.53125 | 10 | 0.03 | 7.6 | 8.7 | 1.07
[7 empty] | mg/L | 3.1549 | 2.2482 | 0.076195 | 1.4343
18 | 1006000 | 35000 | 0 | 1060000 | 12.2 | 0.01 | Lbs. | 21.9969 | 20.9 | 0.53125 | 11 | 0.031 | 7.61 | 9.8 | 1.09
[7 empty] | mg/L | 2.6218 | 2.491 | 0.063319 | 1.3111
19 | 1167000 | 35000 | 30000 | 885100 | 14.2 | 0 | Lbs. | 26.3963 | 20.35 | 0.625 | 13 | 0.03 | 7.6 | 9.9 | 1.02
[7 empty] | mg/L | 2.7121 | 2.0909 | 0.064216 | 1.3357
20 | 853000 | 36000 | 0 | 1057600 | 10.5 | 0.23 | Lbs. | 21.9969 | 14.575 | 0.4375 | 10 | 0.029 | 7.58 | 10.7 | 1.02
[7 empty] | mg/L | 3.092 | 2.0488 | 0.061498 | 1.4057
21 | 1015000 | 35000 | 0 | 1009400 | 12.5 | 0.01 | Lbs. | 26.3963 | 18.975 | 0.5625 | 12 | 0.028 | 7.6 | 8.9 | 1.02
[7 empty] | mg/L | 3.1182 | 2.2416 | 0.066449 | 1.4176
22 | 1116000 | 35000 | 15000 | 942900 | 13.6 | 0.04 | Lbs. | 30.7956 | 20.9 | 0.59375 | 13 | 0.03 | 7.76 | 9.4 | 1.01
[7 empty] | mg/L | 3.3087 | 2.2455 | 0.063793 | 1.3967
23 | 964000 | 35000 | 15000 | 1001500 | 11.4 | 0.42 | Lbs. | 35.195 | 17.875 | 0.5625 | 11 | 0.029 | 7.75 | 9.4 | 1.07
[7 empty] | mg/L | 4.3776 | 2.2233 | 0.069965 | 1.3682
24 | 984000 | 35000 | 30000 | 1102900 | 12 | 0.05 | Lbs. | 26.3963 | 17.875 | 0.625 | 11 | 0.036 | 7.74 | 9.5 | 1.05
[7 empty] | mg/L | 3.2165 | 2.1781 | 0.076159 | 1.3404
25 | 1057000 | 0 | 15000 | 978551 | 12.5 | 0.25 | Lbs. | 26.3963 | 18.975 | 0.53125 | 10 | 0.036 | 7.7 | 9.8 | 1.06
[7 empty] | mg/L | 2.9943 | 2.1525 | 0.060264 | 1.1344
26 | 915000 | 35000 | 15000 | 937849 | 11.6 | 0 | Lbs. | 26.3963 | 16.5 | 0.53125 | 10 | 0.037 | 7.61 | 9.5 | 1.13
[7 empty] | mg/L | 3.459 | 2.1622 | 0.069616 | 1.3104
27 | 1316000 | 35000 | 0 | 988900 | 16.4 | 0.68 | Lbs. | 37.4062 | 12.1 | 0.1875 | 15 | 0.037 | 7.6 | 8.6 | 1.1
[7 empty] | mg/L | 1.7041 | 0.55123 | 0.068334 | 0.68334
28 | 778000 | 36000 | 0 | 1030500 | 9.2 | 0.13 | Lbs. | 26.3963 | 14.025 | 0.375 | 8 | 0.064 | 7.55 | 10.2 | 1.13
[7 empty] | mg/L | 4.0681 | 2.1615 | 0.057794 | 1.2329
29 | 1013000 | 35000 | 30000 | 983800 | 12.2 | 0.41 | Lbs. | 21.9969 | 18.425 | 0.84375 | 10 | 0.032 | 7.5 | 10.3 | 1.12
[7 empty] | mg/L | 2.6037 | 2.1809 | 0.099871 | 1.1837
30 | 1121000 | 35000 | 0 | 1020900 | 13.6 | 0.04 | Lbs. | 21.9969 | 20.625 | 0.96875 | 11 | 0.032 | 7.49 | 10 | 1.1
[7 empty] | mg/L | 2.3528 | 2.2061 | 0.10362 | 1.1766
31 | 835000 | 0 | 0 | 958900 | 10.3 | 0.1 | Lbs. | 21.9969 | 15.4 | 0.5625 | 8 | 0.048 | 7.46 | 10.1 | 1.08
[7 empty] | mg/L | 3.1587 | 2.2114 | 0.080774 | 1.1488
Monthly Totals
| 30906000 | 809000 | 270000 | 30403600 | 377.5 | 5.99 | Lbs. | 889.5841 | 545.875 | 16.9062 | 340 | N/A | N/A | N/A | N/A
[7 empty] | mg/L | N/A | N/A | N/A | N/A
Daily Averages
| 996967.7419 | 26096.7742 | 8709.6774 | 980761.2903 | 12.1774 | 0.19323 | Lbs. | 28.6963 | 17.6089 | 0.54536 | 10.9677 | 0.036065 | 7.5674 | 9.3839 | 1.0271
[7 empty] | mg/L | 3.3251 | 2.0905 | 0.067822 | 1.2669
Maximum Daily Totals
| 1316000 | 36000 | 30000 | 1235000 | 16.4 | 0.68 | Lbs. | 61.5913 | 23.1 | 0.96875 | 15 | 0.064 | 7.76 | 11.1 | 1.13
[7 empty] | mg/L | 8.1874 | 2.491 | 0.10362 | 1.4742
Minimum Daily Totals
| 770000 | 0 | 0 | 796200 | 9.2 | 0 | Lbs. | 15.3978 | 8.8 | 0.1875 | 8 | 0.028 | 7.32 | 8 | 0.91
[7 empty] | mg/L | 1.7041 | 0.54728 | 0.027209 | 0.68334

## Feb
February, 2020
Day | Value | Influent | Influent 2 | Combined Inf | Backwash | Backwash 2 | Comb. BW | Totalizer | EP-1 | FE-1 | FE-2 | BWP-1 | BWP-2 | SWP-1 | SWP-2 | BL-1 | Residual | Rain | Value | ACH | ACH-2 | Comb Lbs. | SA | SA-2 | Comb Lbs. | Polymer | Chlorine | Chlorine2 | Comb. Cl2 | Value | Raw | Finished
1 | Present | 139842 | 391157 | 1160000 | 155612 | 123746 | 35000 | 556351300 | 4537.4 | 42507.3 | 37220.5 | 389.3 | 932.1 | 331.8 | 691.5 | 224.7 | 1.05 | 0.16 | inches | 0.75 | 0 | 26.3963 | 9.875 | 0 | 21.725 | 2.25 | 12 | 0 | 12 | Turbidity | 2.77 | 0.028
| Previous | 138682 | 391157 |  | 155577 | 123746 |  | 555238200 | 4523.2 | 42507.3 | 37220.5 | 389.1 | 932.1 | 331.8 | 691.5 | 224.5 |  |  | Lbs. | 26.3963 | 0 |  | 21.725 | 0 |  | 0.5625 |  |  |  | Temp. | 11.8 | 10.6
| Total | 1160000 | 0 |  | 35000 | 0 |  | 1113100 | 14.2 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.2 |  |  | mg/L | 2.7285 | 0 |  | 2.2456 | 0 |  | 0.058143 | 1.2404 | 0 |  | pH | 7.31 | 7.67
2 | Present | 140860 | 391157 | 1018000 | 155612 | 123746 | 0 | 557318500 | 4550.1 | 42507.3 | 37220.5 | 389.3 | 932.1 | 331.8 | 691.5 | 224.7 | 1.04 | 0.04 | inches | 0.625 | 0 | 21.9969 | 8.75 | 0 | 19.25 | 2.125 | 11 | 0 | 11 | Turbidity | 2.44 | 0.033
| Total | 1018000 | 0 |  | 0 | 0 |  | 967200 | 12.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 21.9969 | 0 |  | 19.25 | 0 |  | 0.53125 |  |  |  | Temp. | 10.2 | 11
[19 empty] | mg/L | 2.5909 | 0 |  | 2.2673 | 0 |  | 0.062573 | 1.2956 | 0 |  | pH | 7.39 | 7.62
3 | Present | 141860 | 391157 | 1000000 | 155647 | 123746 | 35000 | 558360000 | 4562.2 | 42507.3 | 37220.5 | 389.4 | 932.1 | 331.9 | 691.5 | 224.8 | 1.04 | 0.08 | inches | 0.4375 | 0 | 15.3978 | 8.375 | 0 | 18.425 | 2.25 | 10 | 0 | 10 | Turbidity | 2.28 | 0.027
| Total | 1000000 | 0 |  | 35000 | 0 |  | 1041500 | 12.1 | 0 | 0 | 0.1 | 0 | 0.1 | 0 | 0.1 |  |  | Lbs. | 15.3978 | 0 |  | 18.425 | 0 |  | 0.5625 |  |  |  | Temp. | 8.8 | 8.5
[19 empty] | mg/L | 1.8463 | 0 |  | 2.2092 | 0 |  | 0.067446 | 1.199 | 0 |  | pH | 7.36 | 7.66
4 | Present | 141860 | 392401 | 1244000 | 155647 | 123781 | 35000 | 559385700 | 4562.2 | 42522.8 | 37236 | 389.4 | 932.4 | 331.9 | 691.7 | 224.8 | 1.01 | 0.15 | inches | 0 | 4 | 21 | 0 | 5.375 | 11.825 | 0.875 | 0 | 15 | 15 | Turbidity | 2.12 | 0.028
| Total | 0 | 1244000 |  | 0 | 35000 |  | 1025700 | 0 | 15.5 | 15.5 | 0 | 0.3 | 0 | 0.2 | 0 |  |  | Lbs. | 0 | 21 |  | 0 | 11.825 |  | 0.21875 |  |  |  | Temp. | 8.9 | 8.8
[19 empty] | mg/L | 0 | 2.0241 |  | 0 | 1.1398 |  | 0.021084 | 0 | 1.4458 |  | pH | 7.48 | 7.67
5 | Present | 142729 | 392401 | 869000 | 155647 | 123781 | 0 | 560403500 | 4572.9 | 42522.8 | 37236 | 389.4 | 932.4 | 331.9 | 691.7 | 224.8 | 1.1 | 0.22 | inches | 0.75 | 0 | 26.3963 | 7.0625 | 0 | 15.5375 | 0 | 9 | 0 | 9 | Turbidity | 1.85 | 0.028
| Total | 869000 | 0 |  | 0 | 0 |  | 1017800 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 26.3963 | 0 |  | 15.5375 | 0 |  | 0 |  |  |  | Temp. | 9.6 | 9
[19 empty] | mg/L | 3.6421 | 0 |  | 2.1439 | 0 |  | 0 | 1.2418 | 0 |  | pH | 7.44 | 7.75
6 | Present | 143806 | 392401 | 1077000 | 155682 | 123781 | 35000 | 561450200 | 4586 | 42522.8 | 37236 | 389.6 | 932.4 | 332 | 691.7 | 224.8 | 1.15 | 0.02 | inches | 0.875 | 0 | 30.7956 | 9.25 | 0 | 20.35 | 2.5 | 11 | 0 | 11 | Turbidity | 3.28 | 0.032
| Total | 1077000 | 0 |  | 35000 | 0 |  | 1046700 | 13.1 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 30.7956 | 0 |  | 20.35 | 0 |  | 0.625 |  |  |  | Temp. | 9.9 | 9.6
[19 empty] | mg/L | 3.4285 | 0 |  | 2.2656 | 0 |  | 0.069582 | 1.2246 | 0 |  | pH | 7.5 | 7.58
7 | Present | 144794 | 392401 | 988000 | 155718 | 123781 | 36000 | 562315200 | 4598.1 | 42522.8 | 37236 | 389.8 | 932.4 | 332.1 | 691.7 | 224.8 | 1.07 | 0.1 | inches | 0.5 | 0 | 17.5975 | 7.875 | 0 | 17.325 | 0.75 | 9 | 0 | 9 | Turbidity | 3.3 | 0.029
| Total | 988000 | 0 |  | 36000 | 0 |  | 865000 | 12.1 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 17.5975 | 0 |  | 17.325 | 0 |  | 0.1875 |  |  |  | Temp. | 11.3 | 9.9
[19 empty] | mg/L | 2.1356 | 0 |  | 2.1026 | 0 |  | 0.022755 | 1.0922 | 0 |  | pH | 7.44 | 7.66
8 | Present | 146067 | 392401 | 1273000 | 155753 | 123781 | 35000 | 563590300 | 4613.6 | 42522.8 | 37236 | 389.96 | 932.4 | 332.2 | 691.7 | 225 | 1 | 0 | inches | 0.875 | 0 | 30.7956 | 10.5 | 0 | 23.1 | 0 | 13 | 0 | 13 | Turbidity | 2.35 | 0.035
| Total | 1273000 | 0 |  | 35000 | 0 |  | 1275100 | 15.5 | 0 | 0 | 0.16 | 0 | 0.1 | 0 | 0.2 |  |  | Lbs. | 30.7956 | 0 |  | 23.1 | 0 |  | 0 |  |  |  | Temp. | 11.4 | 9.1
[19 empty] | mg/L | 2.9006 | 0 |  | 2.1758 | 0 |  | 0 | 1.2245 | 0 |  | pH | 7.38 | 7.6
9 | Present | 147394 | 392401 | 1327000 | 155788 | 123781 | 35000 | 564823700 | 4629.8 | 42522.8 | 37236 | 390.1 | 932.4 | 332.3 | 691.7 | 225.2 | 1.05 | 0 | inches | 0.5 | 0 | 17.5975 | 11 | 0 | 24.2 | 0 | 13 | 0 | 13 | Turbidity | 2.04 | 0.033
| Total | 1327000 | 0 |  | 35000 | 0 |  | 1233400 | 16.2 | 0 | 0 | 0.14 | 0 | 0.1 | 0 | 0.2 |  |  | Lbs. | 17.5975 | 0 |  | 24.2 | 0 |  | 0 |  |  |  | Temp. | 9.4 | 9
[19 empty] | mg/L | 1.5901 | 0 |  | 2.1866 | 0 |  | 0 | 1.1746 | 0 |  | pH | 7.54 | 7.75
10 | Present | 147394 | 393567 | 1166000 | 155788 | 123816 | 35000 | 565961900 | 4629.8 | 42537.3 | 37250.5 | 390.1 | 932.6 | 332.3 | 691.8 | 225.2 | 1.02 | 0 | inches | 0 | 4 | 21 | 0 | 4.625 | 10.175 | 0 | 0 | 13 | 13 | Turbidity | 3.42 | 0.037
| Total | 0 | 1166000 |  | 0 | 35000 |  | 1138200 | 0 | 14.5 | 14.5 | 0 | 0.2 | 0 | 0.1 | 0 |  |  | Lbs. | 0 | 21 |  | 0 | 10.175 |  | 0 |  |  |  | Temp. | 8.9 | 7.9
[19 empty] | mg/L | 0 | 2.1595 |  | 0 | 1.0463 |  | 0 | 0 | 1.3368 |  | pH | 7.42 | 7.73
11 | Present | 147394 | 394555 | 988000 | 155788 | 123852 | 36000 | 566833700 | 4629.8 | 42549.5 | 37262.7 | 390.1 | 932.9 | 332.3 | 692.1 | 225.2 | 1.02 | 0 | inches | 0 | 3.125 | 16.4062 | 0 | 7.25 | 15.95 | 0 | 0 | 10 | 10 | Turbidity | 1.58 | 0.038
| Total | 0 | 988000 |  | 0 | 36000 |  | 871800 | 0 | 12.2 | 12.2 | 0 | 0.3 | 0 | 0.3 | 0 |  |  | Lbs. | 0 | 16.4062 |  | 0 | 15.95 |  | 0 |  |  |  | Temp. | 8.4 | 7.8
[19 empty] | mg/L | 0 | 1.9911 |  | 0 | 1.9357 |  | 0 | 0 | 1.2136 |  | pH | 7.45 | 7.65
12 | Present | 147394 | 395423 | 868000 | 155788 | 123852 | 0 | 567864500 | 4629.8 | 42560.3 | 37273.5 | 390.1 | 932.9 | 332.3 | 692.1 | 225.2 | 1.05 | 0.01 | inches | 0 | 2.875 | 15.0938 | 0 | 3.625 | 7.975 | 0.875 | 0 | 9 | 9 | Turbidity | 1.63 | 0.039
| Total | 0 | 868000 |  | 0 | 0 |  | 1030800 | 0 | 10.8 | 10.8 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 0 | 15.0938 |  | 0 | 7.975 |  | 0.21875 |  |  |  | Temp. | 10.1 | 8.9
[19 empty] | mg/L | 0 | 2.085 |  | 0 | 1.1017 |  | 0.030218 | 0 | 1.2432 |  | pH | 7.5 | 7.69
13 | Present | 147394 | 396378 | 955000 | 155788 | 123887 | 35000 | 568856700 | 4629.8 | 42572.2 | 37285.4 | 390.1 | 933.2 | 332.3 | 692.3 | 225.2 | 1.02 | 0.05 | inches | 0 | 3 | 15.75 | 0 | 4 | 8.8 | 1.125 | 0 | 10 | 10 | Turbidity | 1.58 | 0.038
| Total | 0 | 955000 |  | 0 | 35000 |  | 992200 | 0 | 11.9 | 11.9 | 0 | 0.3 | 0 | 0.2 | 0 |  |  | Lbs. | 0 | 15.75 |  | 0 | 8.8 |  | 0.28125 |  |  |  | Temp. | 9.3 | 8.5
[19 empty] | mg/L | 0 | 1.9775 |  | 0 | 1.1049 |  | 0.035312 | 0 | 1.2555 |  | pH | 7.56 | 7.72
14 | Present | 147394 | 397358 | 980000 | 155788 | 123922 | 35000 | 569916300 | 4629.8 | 42584.5 | 37297.7 | 390.1 | 933.5 | 332.3 | 692.5 | 225.2 | 1.05 | 0.21 | inches | 0 | 3.375 | 17.7188 | 0 | 4.125 | 9.075 | 1.375 | 0 | 10 | 10 | Turbidity | 1.27 | 0.038
| Total | 0 | 980000 |  | 0 | 35000 |  | 1059600 | 0 | 12.3 | 12.3 | 0 | 0.3 | 0 | 0.2 | 0 |  |  | Lbs. | 0 | 17.7188 |  | 0 | 9.075 |  | 0.34375 |  |  |  | Temp. | 9.9 | 8.9
[19 empty] | mg/L | 0 | 2.1679 |  | 0 | 1.1103 |  | 0.042058 | 0 | 1.2235 |  | pH | 7.64 | 7.74
15 | Present | 147394 | 398480 | 1122000 | 155788 | 123939 | 17000 | 570911000 | 4629.8 | 42598.6 | 37311.8 | 390.1 | 933.6 | 332.3 | 692.6 | 225.2 | 1.03 | 0.59 | inches | 0 | 5.125 | 26.9062 | 0 | 4.5 | 9.9 | 1.25 | 0 | 12 | 12 | Turbidity | 1.23 | 0.038
| Total | 0 | 1122000 |  | 0 | 17000 |  | 994700 | 0 | 14.1 | 14.1 | 0 | 0.1 | 0 | 0.1 | 0 |  |  | Lbs. | 0 | 26.9062 |  | 0 | 9.9 |  | 0.3125 |  |  |  | Temp. | 9.1 | 8.7
[19 empty] | mg/L | 0 | 2.8754 |  | 0 | 1.058 |  | 0.033396 | 0 | 1.2824 |  | pH | 7.62 | 7.72
16 | Present | 147394 | 399421 | 941000 | 155788 | 124044 | 105000 | 571955400 | 4629.8 | 42609.8 | 37322.4 | 390.1 | 934.4 | 332.3 | 693.2 | 225.2 | 1.01 | 0.04 | inches | 0 | 6.875 | 36.0938 | 0 | 3.625 | 7.975 | 1.125 | 0 | 10 | 10 | Turbidity | 3.53 | 0.04
| Total | 0 | 941000 |  | 0 | 105000 |  | 1044400 | 0 | 11.2 | 10.6 | 0 | 0.8 | 0 | 0.6 | 0 |  |  | Lbs. | 0 | 36.0938 |  | 0 | 7.975 |  | 0.28125 |  |  |  | Temp. | 8.9 | 8
[19 empty] | mg/L | 0 | 4.5991 |  | 0 | 1.0162 |  | 0.035837 | 0 | 1.2742 |  | pH | 7.58 | 7.79
17 | Present | 147394 | 400588 | 1167000 | 155788 | 124079 | 35000 | 572973500 | 4629.8 | 42624.4 | 37336.9 | 390.1 | 934.7 | 332.3 | 693.4 | 225.2 | 1.03 | 0 | inches | 0 | 4.375 | 22.9688 | 0 | 5.5 | 12.1 | 1.25 | 0 | 12 | 12 | Turbidity | 2.63 | 0.056
| Total | 0 | 1167000 |  | 0 | 35000 |  | 1018100 | 0 | 14.6 | 14.5 | 0 | 0.3 | 0 | 0.2 | 0 |  |  | Lbs. | 0 | 22.9688 |  | 0 | 12.1 |  | 0.3125 |  |  |  | Temp. | 9.4 | 8.8
[19 empty] | mg/L | 0 | 2.3599 |  | 0 | 1.2432 |  | 0.032108 | 0 | 1.2329 |  | pH | 7.53 | 7.77
18 | Present | 147394 | 401851 | 1263000 | 155788 | 124114 | 35000 | 574042600 | 4629.8 | 42640.3 | 37352.8 | 390.1 | 935 | 332.3 | 693.6 | 225.2 | 1.03 | 0 | inches | 0 | 4.875 | 25.5938 | 0 | 5.25 | 11.55 | 1 | 0 | 14 | 14 | Turbidity | 2.25 | 0.042
| Total | 0 | 1263000 |  | 0 | 35000 |  | 1069100 | 0 | 15.9 | 15.9 | 0 | 0.3 | 0 | 0.2 | 0 |  |  | Lbs. | 0 | 25.5938 |  | 0 | 11.55 |  | 0.25 |  |  |  | Temp. | 7.9 | 7.6
[19 empty] | mg/L | 0 | 2.4298 |  | 0 | 1.0965 |  | 0.023734 | 0 | 1.3291 |  | pH | 7.43 | 7.61
19 | Present | 147394 | 402640 | 789000 | 155788 | 124114 | 0 | 575111900 | 4629.8 | 42650.7 | 37363.2 | 390.1 | 935 | 332.3 | 693.6 | 225.2 | 0.99 | 0 | inches | 0 | 3.375 | 17.7188 | 0 | 3.5 | 7.7 | 0.625 | 0 | 9 | 9 | Turbidity | 1.93 | 0.045
| Total | 0 | 789000 |  | 0 | 0 |  | 1069300 | 0 | 10.4 | 10.4 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 0 | 17.7188 |  | 0 | 7.7 |  | 0.15625 |  |  |  | Temp. | 8.3 | 8
[19 empty] | mg/L | 0 | 2.6927 |  | 0 | 1.1702 |  | 0.023745 | 0 | 1.3677 |  | pH | 7.45 | 7.66
20 | Present | 147394 | 403737 | 1097000 | 155788 | 124184 | 70000 | 576171400 | 4629.8 | 42664.4 | 37376.9 | 390.1 | 935.6 | 332.3 | 694 | 225.2 | 1.07 | 0 | inches | 0 | 3.1875 | 16.7344 | 0 | 4.625 | 10.175 | 0.75 | 0 | 12 | 12 | Turbidity | 1.8 | 0.037
| Total | 0 | 1097000 |  | 0 | 70000 |  | 1059500 | 0 | 13.7 | 13.7 | 0 | 0.6 | 0 | 0.4 | 0 |  |  | Lbs. | 0 | 16.7344 |  | 0 | 10.175 |  | 0.1875 |  |  |  | Temp. | 9.7 | 8.7
[19 empty] | mg/L | 0 | 1.8291 |  | 0 | 1.1121 |  | 0.020494 | 0 | 1.3116 |  | pH | 7.47 | 7.62
21 | Present | 147394 | 404902 | 1165000 | 155788 | 124219 | 35000 | 577171200 | 4629.8 | 42678.8 | 37391.4 | 390.1 | 935.8 | 332.3 | 694.2 | 225.2 | 1.05 | 0 | inches | 0 | 3.625 | 19.0312 | 0 | 5 | 11 | 0.875 | 0 | 13 | 13 | Turbidity | 1.73 | 0.04
| Total | 0 | 1165000 |  | 0 | 35000 |  | 999800 | 0 | 14.4 | 14.5 | 0 | 0.2 | 0 | 0.2 | 0 |  |  | Lbs. | 0 | 19.0312 |  | 0 | 11 |  | 0.21875 |  |  |  | Temp. | 9.8 | 8.4
[19 empty] | mg/L | 0 | 1.9587 |  | 0 | 1.1321 |  | 0.022514 | 0 | 1.338 |  | pH | 7.6 | 7.75
22 | Present | 147394 | 405768 | 866000 | 155788 | 124219 | 0 | 578172000 | 4629.8 | 42689.7 | 37402.3 | 390.1 | 935.8 | 332.3 | 694.2 | 225.2 | 1.05 | 0 | inches | 0 | 3 | 15.75 | 0 | 4 | 8.8 | 0.5625 | 0 | 10 | 10 | Turbidity | 1.6 | 0.037
| Total | 0 | 866000 |  | 0 | 0 |  | 1000800 | 0 | 10.9 | 10.9 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 0 | 15.75 |  | 0 | 8.8 |  | 0.14062 |  |  |  | Temp. | 9.9 | 8.3
[19 empty] | mg/L | 0 | 2.1807 |  | 0 | 1.2184 |  | 0.019471 | 0 | 1.3846 |  | pH | 7.54 | 7.71
23 | Present | 147394 | 406765 | 997000 | 155788 | 124254 | 35000 | 579163500 | 4629.8 | 42702.1 | 37414.7 | 390.1 | 936.1 | 332.3 | 694.4 | 225.2 | 1.02 | 0.25 | inches | 0 | 4 | 21 | 0 | 4.25 | 9.35 | 0.75 | 0 | 11 | 11 | Turbidity | 1.54 | 0.037
| Total | 0 | 997000 |  | 0 | 35000 |  | 991500 | 0 | 12.4 | 12.4 | 0 | 0.3 | 0 | 0.2 | 0 |  |  | Lbs. | 0 | 21 |  | 0 | 9.35 |  | 0.1875 |  |  |  | Temp. | 10.6 | 8.7
[19 empty] | mg/L | 0 | 2.5256 |  | 0 | 1.1245 |  | 0.02255 | 0 | 1.3229 |  | pH | 7.33 | 7.53
24 | Present | 147394 | 407962 | 1197000 | 155788 | 124289 | 35000 | 580188700 | 4629.8 | 42717.1 | 37429.7 | 390.1 | 936.4 | 332.3 | 694.6 | 225.2 | 1.05 | 0 | inches | 0 | 5.375 | 28.2188 | 0 | 5.375 | 11.825 | 0.875 | 0 | 13 | 13 | Turbidity | 1.66 | 0.037
| Total | 0 | 1197000 |  | 0 | 35000 |  | 1025200 | 0 | 15 | 15 | 0 | 0.3 | 0 | 0.2 | 0 |  |  | Lbs. | 0 | 28.2188 |  | 0 | 11.825 |  | 0.21875 |  |  |  | Temp. | 8.7 | 8.2
[19 empty] | mg/L | 0 | 2.8267 |  | 0 | 1.1845 |  | 0.021912 | 0 | 1.3022 |  | pH | 7.36 | 7.63
25 | Present | 147394 | 408659 | 697000 | 155788 | 124289 | 0 | 581195500 | 4629.8 | 42725.9 | 37438.4 | 390.1 | 936.4 | 332.3 | 694.6 | 225.2 | 1.08 | 0 | inches | 0 | 2.5 | 13.125 | 0 | 3.5 | 7.7 | 0.5 | 0 | 8 | 8 | Turbidity | 1.86 | 0.04
| Total | 0 | 697000 |  | 0 | 0 |  | 1006800 | 0 | 8.8 | 8.7 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 0 | 13.125 |  | 0 | 7.7 |  | 0.125 |  |  |  | Temp. | 8 | 8.4
[19 empty] | mg/L | 0 | 2.2579 |  | 0 | 1.3246 |  | 0.021504 | 0 | 1.3762 |  | pH | 7.33 | 7.66
26 | Present | 147394 | 409745 | 1086000 | 155788 | 124324 | 35000 | 582076100 | 4629.8 | 42739.3 | 37451.9 | 390.1 | 936.7 | 332.3 | 694.8 | 225.2 | 1.03 | 0 | inches | 0 | 4.25 | 22.3125 | 0 | 4.625 | 10.175 | 0.75 | 0 | 12 | 12 | Turbidity | 1.41 | 0.051
| Total | 0 | 1086000 |  | 0 | 35000 |  | 880600 | 0 | 13.4 | 13.5 | 0 | 0.3 | 0 | 0.2 | 0 |  |  | Lbs. | 0 | 22.3125 |  | 0 | 10.175 |  | 0.1875 |  |  |  | Temp. | 11.2 | 9.3
[19 empty] | mg/L | 0 | 2.4635 |  | 0 | 1.1234 |  | 0.020702 | 0 | 1.3249 |  | pH | 7.41 | 7.73
27 | Present | 147394 | 410654 | 909000 | 155788 | 124359 | 35000 | 583071800 | 4629.8 | 42750.7 | 37463.3 | 390.1 | 937 | 332.3 | 695 | 225.2 | 1.06 | 0 | inches | 0 | 3.625 | 19.0312 | 0 | 3.75 | 8.25 | 0.625 | 0 | 10 | 10 | Turbidity | 1.43 | 0.039
| Total | 0 | 909000 |  | 0 | 35000 |  | 995700 | 0 | 11.4 | 11.4 | 0 | 0.3 | 0 | 0.2 | 0 |  |  | Lbs. | 0 | 19.0312 |  | 0 | 8.25 |  | 0.15625 |  |  |  | Temp. | 7.5 | 9.9
[19 empty] | mg/L | 0 | 2.5104 |  | 0 | 1.0882 |  | 0.020611 | 0 | 1.3191 |  | pH | 7.52 | 7.62
28 | Present | 147394 | 411363 | 709000 | 155788 | 124359 | 0 | 583956800 | 4629.8 | 42759.8 | 37472.4 | 390.1 | 937 | 332.3 | 695 | 225.2 | 1.01 | 0.25 | inches | 0 | 2.5 | 13.125 | 0 | 2.875 | 6.325 | 0.5 | 0 | 8 | 8 | Turbidity | 1.14 | 0.045
| Total | 0 | 709000 |  | 0 | 0 |  | 885000 | 0 | 9.1 | 9.1 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 0 | 13.125 |  | 0 | 6.325 |  | 0.125 |  |  |  | Temp. | 8.8 | 8.7
[19 empty] | mg/L | 0 | 2.2197 |  | 0 | 1.0697 |  | 0.02114 | 0 | 1.3529 |  | pH | 7.54 | 7.69
29 | Present | 147394 | 412469 | 1106000 | 155788 | 124395 | 36000 | 584960500 | 4629.8 | 42773.7 | 37486.3 | 390.1 | 937.2 | 332.3 | 695.2 | 225.2 | 1 | 0.33 | inches | 0 | 5 | 26.25 | 0 | 4.6875 | 10.3125 | 0.75 | 0 | 12 | 12 | Turbidity | 1.16 | 0.049
| Total | 0 | 1106000 |  | 0 | 36000 |  | 1003700 | 0 | 13.9 | 13.9 | 0 | 0.2 | 0 | 0.2 | 0 |  |  | Lbs. | 0 | 26.25 |  | 0 | 10.3125 |  | 0.1875 |  |  |  | Temp. | 10.7 | 10
[19 empty] | mg/L | 0 | 2.8458 |  | 0 | 1.118 |  | 0.020327 | 0 | 1.3009 |  | pH | 7.57 | 7.78
| Total | 8712000 | 21312000 | 30024000 | 211000 | 649000 | 860000 | 29722300 | 106.6 | 266.4 | 265.8 | 1 | 5.1 | 0.5 | 3.7 | 0.7 | N/A | 2.5 | Total Lbs. | 186.9734 | 417.7031 | 617.8016 | 159.9125 | 200.6125 | 366.85 | 6.4531 | 76 | 213 | 321 | Avg Turb. | 2.0596 | 0.037536
| Average | 300413.7931 | 734896.5517 | 1035310.3448 | 7275.8621 | 22379.3103 | 29655.1724 | 1024906.8966 | 3.6759 | 9.1862 | 9.1655 | 0.034483 | 0.17586 | 0.017241 | 0.12759 | 0.024138 | 1.0407 | 0.086207 | Avg Lbs. | 6.6776 | 14.918 | 22.0643 | 5.7112 | 7.1647 | 13.1018 | 0.23047 | 2.7143 | 7.6071 | 11.4643 | Avg. Temp. | 9.5571 | 8.875
| High | 1327000 | 1263000 | 1327000 | 36000 | 105000 | 105000 | 1275100 | 16.2 | 15.9 | 15.9 | 0.2 | 0.8 | 0.1 | 0.6 | 0.2 | 1.15 | 0.59 | High Lbs. | 30.7956 | 36.0938 | 36.0938 | 24.2 | 15.95 | 24.2 | 0.625 | 13 | 15 | 15 | Avg pH | 7.4696 | 7.6811
| Low | 0 | 0 | 697000 | 0 | 0 | 0 | 865000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99 | 0 | Low Lbs. | 0 | 0 | 13.125 | 0 | 0 | 6.325 | 0 | 0 | 0 | 8
[19 empty] | Avg mg/L | 0.74509 | 1.7414 |  | 0.62845 | 0.83745 |  | 0.026717 | 0.34617 | 0.93519 |  | High Turb. | 3.53 | 0.056
[19 empty] | High mg/L | 3.6421 | 4.5991 |  | 2.2673 | 1.9357 |  | 0.069582 | 1.2956 | 1.4458 |  | High Temp. | 11.8 | 11
[19 empty] | Low mg/L | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 |  | High pH | 7.64 | 7.79
*Averages, Highs and Lows represent only days the plant was in operation
[30 empty] | Low Turb. | 1.23 | 0.027
[30 empty] | Low Temp. | 7.5 | 7.6
[30 empty] | Low pH | 7.31 | 7.53

## FebTotals
February, 2020
Combined Plant Daily Totals
Day | Gallons |  |  |  | Plant Hours | Rain Inches | Chemical Usage |  |  |  |  | Finished Water |  |  | Residual Chlorine
| Influent | Backwash | Flush | Totalizer |  |  | Value | ACH | SodaAsh | Polymer | NaOCl | Turbidity | pH | Temp
1 | 1160000 | 35000 | 30000 | 1113100 | 14.2 | 0.16 | Lbs. | 26.3963 | 21.725 | 0.5625 | 12 | 0.028 | 7.67 | 10.6 | 1.05
[7 empty] | mg/L | 2.7285 | 2.2456 | 0.058143 | 1.2404
2 | 1018000 | 0 | 0 | 967200 | 12.7 | 0.04 | Lbs. | 21.9969 | 19.25 | 0.53125 | 11 | 0.033 | 7.62 | 11 | 1.04
[7 empty] | mg/L | 2.5909 | 2.2673 | 0.062573 | 1.2956
3 | 1000000 | 35000 | 15000 | 1041500 | 12.1 | 0.08 | Lbs. | 15.3978 | 18.425 | 0.5625 | 10 | 0.027 | 7.66 | 8.5 | 1.04
[7 empty] | mg/L | 1.8463 | 2.2092 | 0.067446 | 1.199
4 | 1244000 | 35000 | 0 | 1025700 | 15.5 | 0.15 | Lbs. | 21 | 11.825 | 0.21875 | 15 | 0.028 | 7.67 | 8.8 | 1.01
[7 empty] | mg/L | 1.0121 | 0.56988 | 0.021084 | 1.4458
5 | 869000 | 0 | 0 | 1017800 | 10.7 | 0.22 | Lbs. | 26.3963 | 15.5375 | 0 | 9 | 0.028 | 7.75 | 9 | 1.1
[7 empty] | mg/L | 3.6421 | 2.1439 | 0 | 1.2418
6 | 1077000 | 35000 | 0 | 1046700 | 13.1 | 0.02 | Lbs. | 30.7956 | 20.35 | 0.625 | 11 | 0.032 | 7.58 | 9.6 | 1.15
[7 empty] | mg/L | 3.4285 | 2.2656 | 0.069582 | 1.2246
7 | 988000 | 36000 | 0 | 865000 | 12.1 | 0.1 | Lbs. | 17.5975 | 17.325 | 0.1875 | 9 | 0.029 | 7.66 | 9.9 | 1.07
[7 empty] | mg/L | 2.1356 | 2.1026 | 0.022755 | 1.0922
8 | 1273000 | 35000 | 30000 | 1275100 | 15.5 | 0 | Lbs. | 30.7956 | 23.1 | 0 | 13 | 0.035 | 7.6 | 9.1 | 1
[7 empty] | mg/L | 2.9006 | 2.1758 | 0 | 1.2245
9 | 1327000 | 35000 | 30000 | 1233400 | 16.2 | 0 | Lbs. | 17.5975 | 24.2 | 0 | 13 | 0.033 | 7.75 | 9 | 1.05
[7 empty] | mg/L | 1.5901 | 2.1866 | 0 | 1.1746
10 | 1166000 | 35000 | 0 | 1138200 | 14.5 | 0 | Lbs. | 21 | 10.175 | 0 | 13 | 0.037 | 7.73 | 7.9 | 1.02
[7 empty] | mg/L | 1.0798 | 0.52317 | 0 | 1.3368
11 | 988000 | 36000 | 0 | 871800 | 12.2 | 0 | Lbs. | 16.4062 | 15.95 | 0 | 10 | 0.038 | 7.65 | 7.8 | 1.02
[7 empty] | mg/L | 0.99553 | 0.96785 | 0 | 1.2136
12 | 868000 | 0 | 0 | 1030800 | 10.8 | 0.01 | Lbs. | 15.0938 | 7.975 | 0.21875 | 9 | 0.039 | 7.69 | 8.9 | 1.05
[7 empty] | mg/L | 1.0425 | 0.55083 | 0.030218 | 1.2432
13 | 955000 | 35000 | 0 | 992200 | 11.9 | 0.05 | Lbs. | 15.75 | 8.8 | 0.28125 | 10 | 0.038 | 7.72 | 8.5 | 1.02
[7 empty] | mg/L | 0.98874 | 0.55244 | 0.035312 | 1.2555
14 | 980000 | 35000 | 0 | 1059600 | 12.3 | 0.21 | Lbs. | 17.7188 | 9.075 | 0.34375 | 10 | 0.038 | 7.74 | 8.9 | 1.05
[7 empty] | mg/L | 1.084 | 0.55517 | 0.042058 | 1.2235
15 | 1122000 | 17000 | 0 | 994700 | 14.1 | 0.59 | Lbs. | 26.9062 | 9.9 | 0.3125 | 12 | 0.038 | 7.72 | 8.7 | 1.03
[7 empty] | mg/L | 1.4377 | 0.52899 | 0.033396 | 1.2824
16 | 941000 | 105000 | 0 | 1044400 | 11.2 | 0.04 | Lbs. | 36.0938 | 7.975 | 0.28125 | 10 | 0.04 | 7.79 | 8 | 1.01
[7 empty] | mg/L | 2.2996 | 0.5081 | 0.035837 | 1.2742
17 | 1167000 | 35000 | 0 | 1018100 | 14.6 | 0 | Lbs. | 22.9688 | 12.1 | 0.3125 | 12 | 0.056 | 7.77 | 8.8 | 1.03
[7 empty] | mg/L | 1.18 | 0.62161 | 0.032108 | 1.2329
18 | 1263000 | 35000 | 0 | 1069100 | 15.9 | 0 | Lbs. | 25.5938 | 11.55 | 0.25 | 14 | 0.042 | 7.61 | 7.6 | 1.03
[7 empty] | mg/L | 1.2149 | 0.54825 | 0.023734 | 1.3291
19 | 789000 | 0 | 0 | 1069300 | 10.4 | 0 | Lbs. | 17.7188 | 7.7 | 0.15625 | 9 | 0.045 | 7.66 | 8 | 0.99
[7 empty] | mg/L | 1.3464 | 0.58508 | 0.023745 | 1.3677
20 | 1097000 | 70000 | 0 | 1059500 | 13.7 | 0 | Lbs. | 16.7344 | 10.175 | 0.1875 | 12 | 0.037 | 7.62 | 8.7 | 1.07
[7 empty] | mg/L | 0.91455 | 0.55607 | 0.020494 | 1.3116
21 | 1165000 | 35000 | 0 | 999800 | 14.4 | 0 | Lbs. | 19.0312 | 11 | 0.21875 | 13 | 0.04 | 7.75 | 8.4 | 1.05
[7 empty] | mg/L | 0.97937 | 0.56607 | 0.022514 | 1.338
22 | 866000 | 0 | 0 | 1000800 | 10.9 | 0 | Lbs. | 15.75 | 8.8 | 0.14062 | 10 | 0.037 | 7.71 | 8.3 | 1.05
[7 empty] | mg/L | 1.0904 | 0.60921 | 0.019471 | 1.3846
23 | 997000 | 35000 | 0 | 991500 | 12.4 | 0.25 | Lbs. | 21 | 9.35 | 0.1875 | 11 | 0.037 | 7.53 | 8.7 | 1.02
[7 empty] | mg/L | 1.2628 | 0.56224 | 0.02255 | 1.3229
24 | 1197000 | 35000 | 0 | 1025200 | 15 | 0 | Lbs. | 28.2188 | 11.825 | 0.21875 | 13 | 0.037 | 7.63 | 8.2 | 1.05
[7 empty] | mg/L | 1.4133 | 0.59226 | 0.021912 | 1.3022
25 | 697000 | 0 | 0 | 1006800 | 8.8 | 0 | Lbs. | 13.125 | 7.7 | 0.125 | 8 | 0.04 | 7.66 | 8.4 | 1.08
[7 empty] | mg/L | 1.1289 | 0.66231 | 0.021504 | 1.3762
26 | 1086000 | 35000 | 0 | 880600 | 13.4 | 0 | Lbs. | 22.3125 | 10.175 | 0.1875 | 12 | 0.051 | 7.73 | 9.3 | 1.03
[7 empty] | mg/L | 1.2317 | 0.56171 | 0.020702 | 1.3249
27 | 909000 | 35000 | 0 | 995700 | 11.4 | 0 | Lbs. | 19.0312 | 8.25 | 0.15625 | 10 | 0.039 | 7.62 | 9.9 | 1.06
[7 empty] | mg/L | 1.2552 | 0.54412 | 0.020611 | 1.3191
28 | 709000 | 0 | 0 | 885000 | 9.1 | 0.25 | Lbs. | 13.125 | 0 | 0.125 | 8 | 0.045 | 7.69 | 8.7 | 1.01
[7 empty] | mg/L | 1.1098 | 2.2197 | 0.02114 | 1.3529
29 | 1106000 | 36000 | 0 | 1003700 | 13.9 | 0.33 | Lbs. | 26.25 | 10.3125 | 0.1875 | 12 | 0.049 | 7.78 | 10 | 1
[7 empty] | mg/L | 1.4229 | 0.559 | 0.020327 | 1.3009
Monthly Totals
| 30024000 | 860000 | 105000 | 29722300 | 373 | 2.5 | Lbs. | 617.8016 | 360.525 | 6.5781 | 321 | N/A | N/A | N/A | N/A
[7 empty] | mg/L | N/A | N/A | N/A | N/A
Daily Averages
| 1035310.3448 | 29655.1724 | 3620.6897 | 1024906.8966 | 12.8621 | 0.086207 | Lbs. | 22.0643 | 12.8759 | 0.23493 | 11.4643 | 0.037793 | 7.6814 | 8.869 | 1.0407
[7 empty] | mg/L | 1.5984 | 1.0876 | 0.026525 | 1.2838
Maximum Daily Totals
| 1327000 | 105000 | 30000 | 1275100 | 16.2 | 0.59 | Lbs. | 36.0938 | 24.2 | 0.625 | 15 | 0.056 | 7.79 | 11 | 1.15
[7 empty] | mg/L | 3.6421 | 2.2673 | 0.069582 | 1.4458
Minimum Daily Totals
| 697000 | 0 | 0 | 865000 | 8.8 | 0 | Lbs. | 13.125 | 0 | 0 | 8 | 0.027 | 7.53 | 7.6 | 0.99
[7 empty] | mg/L | 0.91455 | 0.5081 | 0 | 1.0922

## Mar
March, 2020
Day | Value | Influent | Influent 2 | Combined Inf | Backwash | Backwash 2 | Comb. BW | Totalizer | EP-1 | FE-1 | FE-2 | BWP-1 | BWP-2 | SWP-1 | SWP-2 | BL-1 | Residual | Rain | Value | ACH | ACH-2 | Comb Lbs. | SA | SA-2 | Comb Lbs. | Polymer | Chlorine | Chlorine2 | Comb. Cl2 | Value | Raw | Finished
1 | Present | 147394 | 413500 | 1031000 | 155788 | 124412 | 17000 | 585955800 | 4629.8 | 42786.6 | 37499.1 | 390.1 | 937.4 | 332.3 | 695.3 | 225.2 | 1.01 | 0 | inches | 0 | 4.625 | 24.2812 | 0 | 4 | 8.8 | 0.75 | 0 | 11 | 11 | Turbidity | 1.36 | 0.043
| Previous | 147394 | 412469 |  | 155788 | 124395 |  | 584960500 | 4629.8 | 42773.7 | 37486.3 | 390.1 | 937.2 | 332.3 | 695.2 | 225.2 |  |  | Lbs. | 0 | 24.2812 |  | 0 | 8.8 |  | 0.1875 |  |  |  | Temp. | 8.8 | 9.5
| Total | 0 | 1031000 |  | 0 | 17000 |  | 995300 | 0 | 12.9 | 12.8 | 0 | 0.2 | 0 | 0.1 | 0 |  |  | mg/L | 0 | 2.8239 |  | 0 | 1.0234 |  | 0.021806 | 0 | 1.2793 |  | pH | 7.45 | 7.67
2 | Present | 148397 | 413500 | 1003000 | 155858 | 124412 | 70000 | 586936800 | 4641.5 | 42786.6 | 37499.1 | 390.4 | 937.4 | 332.3 | 695.3 | 225.2 | 1.01 | 0 | inches | 0.5625 | 0 | 19.7972 | 6.875 | 0 | 15.125 | 2.875 | 11 | 0 | 11 | Turbidity | 1.43 | 0.037
| Total | 1003000 | 0 |  | 70000 | 0 |  | 981000 | 11.7 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 |  |  | Lbs. | 19.7972 | 0 |  | 15.125 | 0 |  | 0.71875 |  |  |  | Temp. | 8.5 | 7.8
[19 empty] | mg/L | 2.3667 | 0 |  | 1.8081 | 0 |  | 0.085923 | 1.315 | 0 |  | pH | 7.43 | 7.68
3 | Present | 149311 | 413500 | 914000 | 155858 | 124412 | 0 | 587884200 | 4652.8 | 42786.6 | 37499.1 | 390.4 | 937.4 | 332.3 | 695.3 | 225.3 | 1.07 | 0.01 | inches | 0.5 | 0 | 17.5975 | 7.875 | 0 | 17.325 | 2.875 | 10 | 0 | 10 | Turbidity | 1.48 | 0.029
| Total | 914000 | 0 |  | 0 | 0 |  | 947400 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 17.5975 | 0 |  | 17.325 | 0 |  | 0.71875 |  |  |  | Temp. | 10.2 | 9.4
[19 empty] | mg/L | 2.3085 | 0 |  | 2.2728 | 0 |  | 0.09429 | 1.3119 | 0 |  | pH | 7.32 | 7.61
4 | Present | 150464 | 413500 | 1153000 | 155894 | 124412 | 36000 | 588948700 | 4666.8 | 42786.6 | 37499.1 | 390.6 | 937.4 | 332.4 | 695.3 | 225.5 | 1.01 | 0.01 | inches | 0.625 | 0 | 21.9969 | 9.625 | 0 | 21.175 | 3.5 | 12 | 0 | 12 | Turbidity | 1.57 | 0.028
| Total | 1153000 | 0 |  | 36000 | 0 |  | 1064500 | 14 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0.2 |  |  | Lbs. | 21.9969 | 0 |  | 21.175 | 0 |  | 0.875 |  |  |  | Temp. | 10.7 | 10.6
[19 empty] | mg/L | 2.2875 | 0 |  | 2.2021 | 0 |  | 0.090994 | 1.2479 | 0 |  | pH | 7.43 | 7.55
5 | Present | 151372 | 413500 | 908000 | 155929 | 124412 | 35000 | 589903800 | 4677.9 | 42786.6 | 37499.1 | 390.7 | 937.4 | 332.5 | 695.3 | 225.5 | 1.05 | 0 | inches | 0.5 | 0 | 17.5975 | 7.75 | 0 | 17.05 | 2.875 | 10 | 0 | 10 | Turbidity | 1.62 | 0.029
| Total | 908000 | 0 |  | 35000 | 0 |  | 955100 | 11.1 | 0 | 0 | 0.1 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 17.5975 | 0 |  | 17.05 | 0 |  | 0.71875 |  |  |  | Temp. | 10.6 | 8.6
[19 empty] | mg/L | 2.3238 | 0 |  | 2.2515 | 0 |  | 0.094913 | 1.3205 | 0 |  | pH | 7.43 | 7.66
6 | Present | 152360 | 413500 | 988000 | 155929 | 124412 | 0 | 590960700 | 4690.2 | 42786.6 | 37499.1 | 390.8 | 937.4 | 332.6 | 695.3 | 225.6 | 1.06 | 0.42 | inches | 0.5 | 0 | 17.5975 | 8.5 | 0 | 18.7 | 2 | 11 | 0 | 11 | Turbidity | 1.01 | 0.039
| Total | 988000 | 0 |  | 0 | 0 |  | 1056900 | 12.3 | 0 | 0 | 0.1 | 0 | 0.1 | 0 | 0.1 |  |  | Lbs. | 17.5975 | 0 |  | 18.7 | 0 |  | 0.5 |  |  |  | Temp. | 10.6 | 10.5
[19 empty] | mg/L | 2.1356 | 0 |  | 2.2694 | 0 |  | 0.06068 | 1.335 | 0 |  | pH | 7.65 | 7.83
7 | Present | 153295 | 413500 | 935000 | 155964 | 124412 | 35000 | 591833300 | 4701.7 | 42786.6 | 37499.1 | 390.96 | 937.4 | 332.6 | 695.3 | 225.6 | 1 | 0.19 | inches | 0.5 | 0 | 17.5975 | 7.875 | 0 | 17.325 | 2 | 10 | 0 | 10 | Turbidity | 1.35 | 0.043
| Total | 935000 | 0 |  | 35000 | 0 |  | 872600 | 11.5 | 0 | 0 | 0.16 | 0 | 0 | 0 | 0 |  |  | Lbs. | 17.5975 | 0 |  | 17.325 | 0 |  | 0.5 |  |  |  | Temp. | 10.6 | 8.9
[19 empty] | mg/L | 2.2567 | 0 |  | 2.2218 | 0 |  | 0.06412 | 1.2824 | 0 |  | pH | 7.47 | 7.83
8 | Present | 154173 | 413500 | 878000 | 155999 | 124412 | 35000 | 592732900 | 4712.3 | 42786.6 | 37499.1 | 391.1 | 937.4 | 332.9 | 695.3 | 225.7 | 1.02 | 0.01 | inches | 0.5 | 0 | 17.5975 | 7.125 | 0 | 15.675 | 2 | 9 | 0 | 9 | Turbidity | 1.32 | 0.037
| Total | 878000 | 0 |  | 35000 | 0 |  | 899600 | 10.6 | 0 | 0 | 0.14 | 0 | 0.3 | 0 | 0.1 |  |  | Lbs. | 17.5975 | 0 |  | 15.675 | 0 |  | 0.5 |  |  |  | Temp. | 8.1 | 7.9
[19 empty] | mg/L | 2.4032 | 0 |  | 2.1407 | 0 |  | 0.068283 | 1.2291 | 0 |  | pH | 7.5 | 7.78
9 | Present | 155440 | 413500 | 1267000 | 156035 | 124412 | 36000 | 593747400 | 4727.6 | 42786.6 | 37499.1 | 391.2 | 937.4 | 332.9 | 695.3 | 225.8 | 0.98 | 0 | inches | 0.625 | 0 | 21.9969 | 10.625 | 0 | 23.375 | 4 | 13 | 0 | 13 | Turbidity | 1.69 | 0.035
| Total | 1267000 | 0 |  | 36000 | 0 |  | 1014500 | 15.3 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 21.9969 | 0 |  | 23.375 | 0 |  | 1 |  |  |  | Temp. | 8.8 | 7.7
[19 empty] | mg/L | 2.0817 | 0 |  | 2.2121 | 0 |  | 0.094636 | 1.2303 | 0 |  | pH | 7.49 | 7.76
10 | Present | 156305 | 413500 | 865000 | 156035 | 124412 | 0 | 594738600 | 4738.3 | 42786.6 | 37499.1 | 391.2 | 937.4 | 332.9 | 695.3 | 225.8 | 0.87 | 0 | inches | 0.4375 | 0 | 15.3978 | 6.375 | 0 | 14.025 | 2.875 | 12 | 0 | 12 | Turbidity | 1.23 | 0.067
| Total | 865000 | 0 |  | 0 | 0 |  | 991200 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 15.3978 | 0 |  | 14.025 | 0 |  | 0.71875 |  |  |  | Temp. | 8 | 8.6
[19 empty] | mg/L | 2.1344 | 0 |  | 1.9441 | 0 |  | 0.099631 | 1.6634 | 0 |  | pH | 7.6 | 7.87
11 | Present | 157273 | 413500 | 968000 | 156070 | 124412 | 35000 | 595673200 | 4750 | 42786.6 | 37499.1 | 391.4 | 937.4 | 332.9 | 695.3 | 225.8 | 1.01 | 0 | inches | 0.375 | 0 | 13.1981 | 7 | 0 | 15.4 | 3 | 10 | 0 | 10 | Turbidity | 1.29 | 0.037
| Total | 968000 | 0 |  | 35000 | 0 |  | 934600 | 11.7 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 |  |  | Lbs. | 13.1981 | 0 |  | 15.4 | 0 |  | 0.75 |  |  |  | Temp. | 9 | 9.6
[19 empty] | mg/L | 1.6348 | 0 |  | 1.9076 | 0 |  | 0.092901 | 1.2387 | 0 |  | pH | 7.65 | 7.86
12 | Present | 158166 | 413500 | 893000 | 156070 | 124412 | 0 | 596668900 | 4761.2 | 42786.6 | 37499.1 | 391.4 | 937.4 | 332.9 | 695.3 | 225.8 | 1.03 | 0 | inches | 0.4375 | 0 | 15.3978 | 6.625 | 0 | 14.575 | 1.625 | 9 | 0 | 9 | Turbidity | 1.26 | 0.043
| Total | 893000 | 0 |  | 0 | 0 |  | 995700 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 15.3978 | 0 |  | 14.575 | 0 |  | 0.40625 |  |  |  | Temp. | 8.8 | 10.2
[19 empty] | mg/L | 2.0675 | 0 |  | 1.957 | 0 |  | 0.054548 | 1.2084 | 0 |  | pH | 7.63 | 7.82
13 | Present | 159227 | 413500 | 1061000 | 156105 | 124412 | 35000 | 597710000 | 4774.2 | 42786.6 | 37499.1 | 391.6 | 937.4 | 332.9 | 695.3 | 225.9 | 1.11 | 0.3 | inches | 0.4375 | 0 | 15.3978 | 7.625 | 0 | 16.775 | 2.125 | 11 | 0 | 11 | Turbidity | 0.98 | 0.035
| Total | 1061000 | 0 |  | 35000 | 0 |  | 1041100 | 13 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 15.3978 | 0 |  | 16.775 | 0 |  | 0.53125 |  |  |  | Temp. | 8 | 9
[19 empty] | mg/L | 1.7401 | 0 |  | 1.8958 | 0 |  | 0.060037 | 1.2431 | 0 |  | pH | 7.69 | 7.99
14 | Present | 160147 | 413500 | 920000 | 156140 | 124412 | 35000 | 598590200 | 4785.3 | 42786.6 | 37499.1 | 391.7 | 937.4 | 332.9 | 695.3 | 226 | 1.12 | 0.28 | inches | 0.375 | 0 | 13.1981 | 6.625 | 0 | 14.575 | 1.625 | 9 | 0 | 9 | Turbidity | 1.09 | 0.037
| Total | 920000 | 0 |  | 35000 | 0 |  | 880200 | 11.1 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 13.1981 | 0 |  | 14.575 | 0 |  | 0.40625 |  |  |  | Temp. | 8.2 | 8.7
[19 empty] | mg/L | 1.7201 | 0 |  | 1.8996 | 0 |  | 0.052947 | 1.173 | 0 |  | pH | 7.68 | 7.9
15 | Present | 161112 | 413500 | 965000 | 156140 | 124412 | 0 | 599527300 | 4797.3 | 42786.6 | 37499.1 | 391.7 | 937.4 | 332.9 | 695.3 | 226.1 | 1.01 | 0 | inches | 0.4375 | 0 | 15.3978 | 7 | 0 | 15.4 | 1.5 | 9 | 0 | 9 | Turbidity | 1.49 | 0.04
| Total | 965000 | 0 |  | 0 | 0 |  | 937100 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 15.3978 | 0 |  | 15.4 | 0 |  | 0.375 |  |  |  | Temp. | 8.1 | 9.4
[19 empty] | mg/L | 1.9132 | 0 |  | 1.9135 | 0 |  | 0.046595 | 1.1183 | 0 |  | pH | 7.66 | 7.91
16 | Present | 162241 | 413500 | 1129000 | 156175 | 124412 | 35000 | 600525800 | 4811.1 | 42786.6 | 37499.1 | 391.9 | 937.4 | 333 | 695.3 | 226.1 | 0.99 | 0 | inches | 0.5 | 0 | 17.5975 | 8.5 | 0 | 18.7 | 1.5 | 11 | 0 | 11 | Turbidity | 1.47 | 0.037
| Total | 1129000 | 0 |  | 35000 | 0 |  | 998500 | 13.8 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 17.5975 | 0 |  | 18.7 | 0 |  | 0.375 |  |  |  | Temp. | 8.2 | 7.1
[19 empty] | mg/L | 1.8689 | 0 |  | 1.986 | 0 |  | 0.039826 | 1.1682 | 0 |  | pH | 7.57 | 7.92
17 | Present | 163151 | 413500 | 910000 | 156211 | 124412 | 36000 | 601523900 | 4822.2 | 42786.6 | 37499.1 | 392.1 | 937.4 | 333.1 | 695.3 | 226.1 | 1.09 | 0 | inches | 0.375 | 0 | 13.1981 | 6.5 | 0 | 14.3 | 1 | 8 | 0 | 8 | Turbidity | 1.41 | 0.036
| Total | 910000 | 0 |  | 36000 | 0 |  | 998100 | 11.1 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 13.1981 | 0 |  | 14.3 | 0 |  | 0.25 |  |  |  | Temp. | 8 | 8.5
[19 empty] | mg/L | 1.739 | 0 |  | 1.8842 | 0 |  | 0.032941 | 1.0541 | 0 |  | pH | 7.7 | 7.81
18 | Present | 163977 | 413500 | 826000 | 156211 | 124412 | 0 | 602449600 | 4832.5 | 42786.6 | 37499.1 | 392.1 | 937.4 | 333.1 | 695.3 | 226.2 | 1.13 | 0 | inches | 0.375 | 0 | 13.1981 | 6.25 | 0 | 13.75 | 0.875 | 8 | 0 | 8 | Turbidity | 1.38 | 0.044
| Total | 826000 | 0 |  | 0 | 0 |  | 925700 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 13.1981 | 0 |  | 13.75 | 0 |  | 0.21875 |  |  |  | Temp. | 10.2 | 9.7
[19 empty] | mg/L | 1.9159 | 0 |  | 1.996 | 0 |  | 0.031754 | 1.1613 | 0 |  | pH | 7.57 | 7.67
19 | Present | 164865 | 413500 | 888000 | 156246 | 124412 | 35000 | 603383200 | 4843.2 | 42786.6 | 37499.1 | 392.3 | 937.4 | 333.2 | 695.3 | 226.3 | 1.05 | 0 | inches | 0.375 | 0 | 13.1981 | 6.25 | 0 | 13.75 | 0.625 | 8 | 0 | 8 | Turbidity | 1.33 | 0.039
| Total | 888000 | 0 |  | 35000 | 0 |  | 933600 | 10.7 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0.1 |  |  | Lbs. | 13.1981 | 0 |  | 13.75 | 0 |  | 0.15625 |  |  |  | Temp. | 9.8 | 7.7
[19 empty] | mg/L | 1.7821 | 0 |  | 1.8566 | 0 |  | 0.021098 | 1.0802 | 0 |  | pH | 7.47 | 7.79
20 | Present | 166116 | 413500 | 1251000 | 156246 | 124412 | 0 | 604537800 | 4858.8 | 42786.6 | 37499.1 | 392.3 | 937.4 | 333.2 | 695.3 | 226.3 | 0.98 | 0 | inches | 0.625 | 0 | 21.9969 | 9.25 | 0 | 20.35 | 1 | 12 | 0 | 12 | Turbidity | 1.34 | 0.048
| Total | 1251000 | 0 |  | 0 | 0 |  | 1154600 | 15.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 21.9969 | 0 |  | 20.35 | 0 |  | 0.25 |  |  |  | Temp. | 10.8 | 8.9
[19 empty] | mg/L | 2.1083 | 0 |  | 1.9505 | 0 |  | 0.023962 | 1.1502 | 0 |  | pH | 7.49 | 7.82
21 | Present | 167173 | 413500 | 1057000 | 156281 | 124412 | 35000 | 605566500 | 4871.7 | 42786.6 | 37499.1 | 392.5 | 937.4 | 333.3 | 695.3 | 226.3 | 0.98 | 0 | inches | 0.4375 | 0 | 15.3978 | 7.75 | 0 | 17.05 | 0.25 | 10 | 0 | 10 | Turbidity | 1.27 | 0.04
| Total | 1057000 | 0 |  | 35000 | 0 |  | 1028700 | 12.9 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 15.3978 | 0 |  | 17.05 | 0 |  | 0.0625 |  |  |  | Temp. | 10.2 | 9.1
[19 empty] | mg/L | 1.7467 | 0 |  | 1.9341 | 0 |  | 0.0070899 | 1.1344 | 0 |  | pH | 7.44 | 7.77
22 | Present | 168202 | 413500 | 1029000 | 156281 | 124412 | 0 | 606499700 | 4884.6 | 42786.6 | 37499.1 | 392.5 | 937.4 | 333.3 | 695.3 | 226.3 | 0.99 | 0.01 | inches | 0.4375 | 0 | 15.3978 | 7.75 | 0 | 17.05 | 0 | 9 | 0 | 9 | Turbidity | 1.2 | 0.038
| Total | 1029000 | 0 |  | 0 | 0 |  | 933200 | 12.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 15.3978 | 0 |  | 17.05 | 0 |  | 0 |  |  |  | Temp. | 10.5 | 9.4
[19 empty] | mg/L | 1.7942 | 0 |  | 1.9867 | 0 |  | 0 | 1.0487 | 0 |  | pH | 7.57 | 7.8
23 | Present | 168855 | 413758 | 911000 | 156316 | 124447 | 70000 | 607433200 | 4892.4 | 42789.8 | 37502.3 | 392.6 | 937.7 | 333.3 | 695.5 | 226.4 | 1.01 | 0.19 | inches | 0.375 | 1 | 18.4481 | 3.75 | 1 | 10.45 | 0 | 7 | 3 | 10 | Turbidity | 1.26 | 0.036
| Total | 653000 | 258000 |  | 35000 | 35000 |  | 933500 | 7.8 | 3.2 | 3.2 | 0.1 | 0.3 | 0 | 0.2 | 0.1 |  |  | Lbs. | 13.1981 | 5.25 |  | 8.25 | 2.2 |  | 0 |  |  |  | Temp. | 9.9 | 9.2
[19 empty] | mg/L | 2.4234 | 2.4399 |  | 1.5149 | 1.0224 |  | 0 | 1.2853 | 1.3942 |  | pH | 7.41 | 7.64
24 | Present | 169757 | 413758 | 902000 | 156316 | 124447 | 0 | 608411600 | 4903.6 | 42789.8 | 37502.3 | 392.6 | 937.7 | 333.3 | 695.5 | 226.4 | 1.06 | 0.21 | inches | 0.5 | 0 | 17.5975 | 6.5 | 0 | 14.3 | 3.125 | 9 | 0 | 9 | Turbidity | 1.6 | 0.034
| Total | 902000 | 0 |  | 0 | 0 |  | 978400 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 17.5975 | 0 |  | 14.3 | 0 |  | 0.78125 |  |  |  | Temp. | 11 | 9.8
[19 empty] | mg/L | 2.3393 | 0 |  | 1.9009 | 0 |  | 0.10385 | 1.1964 | 0 |  | pH | 7.54 | 7.7
25 | Present | 170098 | 414542 | 1125000 | 156351 | 124465 | 53000 | 609502600 | 4907.3 | 42799.8 | 37512.4 | 392.7 | 937.8 | 333.4 | 695.6 | 226.5 | 1.01 | 0.03 | inches | 0.125 | 4.25 | 26.7119 | 2.5 | 3.25 | 12.65 | 1.5 | 3 | 8 | 11 | Turbidity | 1.76 | 0.032
| Total | 341000 | 784000 |  | 35000 | 18000 |  | 1091000 | 3.7 | 10 | 10.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |  |  | Lbs. | 4.3994 | 22.3125 |  | 5.5 | 7.15 |  | 0.375 |  |  |  | Temp. | 10.6 | 10.5
[19 empty] | mg/L | 1.5469 | 3.4124 |  | 1.9339 | 1.0935 |  | 0.13186 | 1.0549 | 1.2235 |  | pH | 7.55 | 7.76
26 | Present | 170098 | 415623 | 1081000 | 156351 | 124500 | 35000 | 610287600 | 4907.3 | 42813.7 | 37526.2 | 392.7 | 938.1 | 333.4 | 695.8 | 226.5 | 1.1 | 0 | inches | 0 | 5.375 | 28.2188 | 0 | 4.5 | 9.9 | 0.5 | 0 | 10 | 10 | Turbidity | 1.88 | 0.038
| Total | 0 | 1081000 |  | 0 | 35000 |  | 785000 | 0 | 13.9 | 13.8 | 0 | 0.3 | 0 | 0.2 | 0 |  |  | Lbs. | 0 | 28.2188 |  | 0 | 9.9 |  | 0.125 |  |  |  | Temp. | 10.9 | 11.1
[19 empty] | mg/L | 0 | 3.13 |  | 0 | 1.0981 |  | 0.013865 | 0 | 1.1092 |  | pH | 7.62 | 7.88
27 | Present | 170098 | 416419 | 796000 | 156351 | 124535 | 35000 | 611031500 | 4907.3 | 42823.5 | 37536 | 392.7 | 938.3 | 333.4 | 696 | 226.5 | 1.08 | 0.06 | inches | 0 | 4 | 21 | 0 | 3.375 | 7.425 | 0.375 | 0 | 7 | 7 | Turbidity | 1.34 | 0.04
| Total | 0 | 796000 |  | 0 | 35000 |  | 743900 | 0 | 9.8 | 9.8 | 0 | 0.2 | 0 | 0.2 | 0 |  |  | Lbs. | 0 | 21 |  | 0 | 7.425 |  | 0.09375 |  |  |  | Temp. | 10.4 | 9.4
[19 empty] | mg/L | 0 | 3.1633 |  | 0 | 1.1185 |  | 0.014122 | 0 | 1.0544 |  | pH | 7.58 | 7.67
28 | Present | 170098 | 417461 | 1042000 | 156351 | 124535 | 0 | 612335900 | 4907.3 | 42836.7 | 37549.2 | 392.7 | 938.3 | 333.4 | 696 | 226.5 | 1.05 | 0.34 | inches | 0 | 5.5 | 28.875 | 0 | 4.625 | 10.175 | 0.75 | 0 | 10 | 10 | Turbidity | 1.36 | 0.077
| Total | 0 | 1042000 |  | 0 | 0 |  | 1304400 | 0 | 13.2 | 13.2 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 0 | 28.875 |  | 0 | 10.175 |  | 0.1875 |  |  |  | Temp. | 10 | 9.9
[19 empty] | mg/L | 0 | 3.3227 |  | 0 | 1.1708 |  | 0.021576 | 0 | 1.1507 |  | pH | 7.67 | 7.8
29 | Present | 170098 | 418426 | 965000 | 156351 | 124570 | 35000 | 613218600 | 4907.3 | 42849 | 37561.5 | 392.7 | 938.6 | 333.4 | 696.2 | 226.5 | 1.08 | 0.45 | inches | 0 | 6.125 | 32.1562 | 0 | 3.75 | 8.25 | 0.5 | 0 | 8 | 8 | Turbidity | 2.7 | 0.036
| Total | 0 | 965000 |  | 0 | 35000 |  | 882700 | 0 | 12.3 | 12.3 | 0 | 0.3 | 0 | 0.2 | 0 |  |  | Lbs. | 0 | 32.1562 |  | 0 | 8.25 |  | 0.125 |  |  |  | Temp. | 9.6 | 9.3
[19 empty] | mg/L | 0 | 3.9955 |  | 0 | 1.0251 |  | 0.015532 | 0 | 0.99402 |  | pH | 7.64 | 7.75
30 | Present | 171035 | 418426 | 937000 | 156386 | 124570 | 35000 | 614293800 | 4921.2 | 42849 | 37561.5 | 392.9 | 939.6 | 333.5 | 696.2 | 226.7 | 1.03 | 0.46 | inches | 0.875 | 0 | 30.7956 | 5.25 | 0 | 11.55 | 1.875 | 12 | 0 | 12 | Turbidity | 3.35 | 0.045
| Total | 937000 | 0 |  | 35000 | 0 |  | 1075200 | 13.9 | 0 | 0 | 0.2 | 1 | 0.1 | 0 | 0.2 |  |  | Lbs. | 30.7956 | 0 |  | 11.55 | 0 |  | 0.46875 |  |  |  | Temp. | 9.8 | 9.3
[19 empty] | mg/L | 3.9408 | 0 |  | 1.478 | 0 |  | 0.059984 | 1.5356 | 0 |  | pH | 7.5 | 7.72
31 | Present | 171985 | 418426 | 950000 | 156422 | 124570 | 36000 | 615243800 | 4930.1 | 42849 | 37561.5 | 393.1 | 939.6 | 333.6 | 696.2 | 226.7 | 1 | 0.4 | inches | 0.875 | 0 | 30.7956 | 6 | 0 | 13.2 | 2 | 0 | 11 | 11 | Turbidity | 6.72 | 0.048
| Total | 950000 | 0 |  | 36000 | 0 |  | 950000 | 8.9 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 30.7956 | 0 |  | 13.2 | 0 |  | 0.5 |  |  |  | Temp. | 11.8 | 12.2
[19 empty] | mg/L | 3.8869 | 0 |  | 1.666 | 0 |  | 0.063107 | 0 | 1.3884 |  | pH | 7.38 | 7.7
| Total | 24591000 | 5957000 | 30548000 | 634000 | 175000 | 809000 | 30283300 | 300.3 | 75.3 | 75.2 | 3 | 2.4 | 1.3 | 1 | 1.5 | N/A | 3.37 | Total Lbs. | 446.5366 | 162.0938 | 608.6303 | 404.25 | 53.9 | 458.15 | 12.875 | 243 | 68 | 311 | Avg Turb. | 1.5545 | 0.038774
| Average | 793258.0645 | 192161.2903 | 985419.3548 | 20451.6129 | 5645.1613 | 26096.7742 | 976880.6452 | 9.6871 | 2.429 | 2.4258 | 0.096774 | 0.077419 | 0.041935 | 0.032258 | 0.048387 | 1.0319 | 0.10871 | Avg Lbs. | 14.4044 | 5.2288 | 19.6332 | 13.0403 | 1.7387 | 14.779 | 0.41532 | 7.8387 | 2.1935 | 10.0323 | Avg. Temp. | 9.3194 | 8.9742
| High | 1267000 | 1081000 | 1902000 | 70000 | 35000 | 70000 | 1304400 | 15.6 | 13.9 | 13.8 | 0.3 | 1 | 0.3 | 0.2 | 0.2 | 1.13 | 0.46 | High Lbs. | 30.7956 | 32.1562 | 32.1562 | 23.375 | 10.175 | 23.375 | 1 | 13 | 11 | 13 | Avg pH | 7.2994 | 7.5226
| Low | 0 | 0 | 796000 | 0 | 0 | 0 | 743900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87 | 0 | Low Lbs. | 0 | 0 | 13.1981 | 0 | 0 | 7.425 | 0 | 0 | 0 | 7
[19 empty] | Avg mg/L | 1.8215 | 0.71896 |  | 1.6446 | 0.24361 |  | 0.053641 | 0.9931 | 0.30948 |  | High Turb. | 6.72 | 0.077
[19 empty] | High mg/L | 3.9408 | 3.9955 |  | 2.2728 | 1.1708 |  | 0.13186 | 1.6634 | 1.3942 |  | High Temp. | 11.8 | 12.2
[19 empty] | Low mg/L | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 |  | High pH | 7.7 | 7.99
*Averages, Highs and Lows represent only days the plant was in operation
[30 empty] | Low Turb. | 0.98 | 0.028
[30 empty] | Low Temp. | 8 | 7.1
[30 empty] | Low pH | 7.32 | 7.55

## MarTotals
March, 2020
Combined Plant Daily Totals
Day | Gallons |  |  |  | Plant Hours | Rain Inches | Chemical Usage |  |  |  |  | Finished Water |  |  | Residual Chlorine
| Influent | Backwash | Flush | Totalizer |  |  | Value | ACH | SodaAsh | Polymer | NaOCl | Turbidity | pH | Temp
1 | 1031000 | 17000 | 0 | 995300 | 12.9 | 0 | Lbs. | 24.2812 | 8.8 | 0.1875 | 11 | 0.043 | 7.67 | 9.5 | 1.01
[7 empty] | mg/L | 1.4119 | 0.51171 | 0.021806 | 0.63964
2 | 1003000 | 70000 | 0 | 981000 | 11.7 | 0 | Lbs. | 19.7972 | 15.125 | 0.71875 | 11 | 0.037 | 7.68 | 7.8 | 1.01
[7 empty] | mg/L | 2.3667 | 1.8081 | 0.085923 | 1.315
3 | 914000 | 0 | 15000 | 947400 | 11.3 | 0.01 | Lbs. | 17.5975 | 17.325 | 0.71875 | 10 | 0.029 | 7.61 | 9.4 | 1.07
[7 empty] | mg/L | 2.3085 | 2.2728 | 0.09429 | 1.3119
4 | 1153000 | 36000 | 30000 | 1064500 | 14 | 0.01 | Lbs. | 21.9969 | 21.175 | 0.875 | 12 | 0.028 | 7.55 | 10.6 | 1.01
[7 empty] | mg/L | 2.2875 | 2.2021 | 0.090994 | 1.2479
5 | 908000 | 35000 | 0 | 955100 | 11.1 | 0 | Lbs. | 17.5975 | 17.05 | 0.71875 | 10 | 0.029 | 7.66 | 8.6 | 1.05
[7 empty] | mg/L | 2.3238 | 2.2515 | 0.094913 | 1.3205
6 | 988000 | 0 | 15000 | 1056900 | 12.3 | 0.42 | Lbs. | 17.5975 | 18.7 | 0.5 | 11 | 0.039 | 7.83 | 10.5 | 1.06
[7 empty] | mg/L | 2.1356 | 2.2694 | 0.06068 | 1.335
7 | 935000 | 35000 | 0 | 872600 | 11.5 | 0.19 | Lbs. | 17.5975 | 17.325 | 0.5 | 10 | 0.043 | 7.83 | 8.9 | 1
[7 empty] | mg/L | 2.2567 | 2.2218 | 0.06412 | 1.2824
8 | 878000 | 35000 | 15000 | 899600 | 10.6 | 0.01 | Lbs. | 17.5975 | 15.675 | 0.5 | 9 | 0.037 | 7.78 | 7.9 | 1.02
[7 empty] | mg/L | 2.4032 | 2.1407 | 0.068283 | 1.2291
9 | 1267000 | 36000 | 15000 | 1014500 | 15.3 | 0 | Lbs. | 21.9969 | 23.375 | 1 | 13 | 0.035 | 7.76 | 7.7 | 0.98
[7 empty] | mg/L | 2.0817 | 2.2121 | 0.094636 | 1.2303
10 | 865000 | 0 | 0 | 991200 | 10.7 | 0 | Lbs. | 15.3978 | 14.025 | 0.71875 | 12 | 0.067 | 7.87 | 8.6 | 0.87
[7 empty] | mg/L | 2.1344 | 1.9441 | 0.099631 | 1.6634
11 | 968000 | 35000 | 0 | 934600 | 11.7 | 0 | Lbs. | 13.1981 | 15.4 | 0.75 | 10 | 0.037 | 7.86 | 9.6 | 1.01
[7 empty] | mg/L | 1.6348 | 1.9076 | 0.092901 | 1.2387
12 | 893000 | 0 | 0 | 995700 | 11.2 | 0 | Lbs. | 15.3978 | 14.575 | 0.40625 | 9 | 0.043 | 7.82 | 10.2 | 1.03
[7 empty] | mg/L | 2.0675 | 1.957 | 0.054548 | 1.2084
13 | 1061000 | 35000 | 15000 | 1041100 | 13 | 0.3 | Lbs. | 15.3978 | 16.775 | 0.53125 | 11 | 0.035 | 7.99 | 9 | 1.11
[7 empty] | mg/L | 1.7401 | 1.8958 | 0.060037 | 1.2431
14 | 920000 | 35000 | 15000 | 880200 | 11.1 | 0.28 | Lbs. | 13.1981 | 14.575 | 0.40625 | 9 | 0.037 | 7.9 | 8.7 | 1.12
[7 empty] | mg/L | 1.7201 | 1.8996 | 0.052947 | 1.173
15 | 965000 | 0 | 15000 | 937100 | 12 | 0 | Lbs. | 15.3978 | 15.4 | 0.375 | 9 | 0.04 | 7.91 | 9.4 | 1.01
[7 empty] | mg/L | 1.9132 | 1.9135 | 0.046595 | 1.1183
16 | 1129000 | 35000 | 0 | 998500 | 13.8 | 0 | Lbs. | 17.5975 | 18.7 | 0.375 | 11 | 0.037 | 7.92 | 7.1 | 0.99
[7 empty] | mg/L | 1.8689 | 1.986 | 0.039826 | 1.1682
17 | 910000 | 36000 | 0 | 998100 | 11.1 | 0 | Lbs. | 13.1981 | 14.3 | 0.25 | 8 | 0.036 | 7.81 | 8.5 | 1.09
[7 empty] | mg/L | 1.739 | 1.8842 | 0.032941 | 1.0541
18 | 826000 | 0 | 15000 | 925700 | 10.3 | 0 | Lbs. | 13.1981 | 13.75 | 0.21875 | 8 | 0.044 | 7.67 | 9.7 | 1.13
[7 empty] | mg/L | 1.9159 | 1.996 | 0.031754 | 1.1613
19 | 888000 | 35000 | 15000 | 933600 | 10.7 | 0 | Lbs. | 13.1981 | 13.75 | 0.15625 | 8 | 0.039 | 7.79 | 7.7 | 1.05
[7 empty] | mg/L | 1.7821 | 1.8566 | 0.021098 | 1.0802
20 | 1251000 | 0 | 0 | 1154600 | 15.6 | 0 | Lbs. | 21.9969 | 20.35 | 0.25 | 12 | 0.048 | 7.82 | 8.9 | 0.98
[7 empty] | mg/L | 2.1083 | 1.9505 | 0.023962 | 1.1502
21 | 1057000 | 35000 | 0 | 1028700 | 12.9 | 0 | Lbs. | 15.3978 | 17.05 | 0.0625 | 10 | 0.04 | 7.77 | 9.1 | 0.98
[7 empty] | mg/L | 1.7467 | 1.9341 | 0.0070899 | 1.1344
22 | 1029000 | 0 | 0 | 933200 | 12.9 | 0.01 | Lbs. | 15.3978 | 17.05 | 0 | 9 | 0.038 | 7.8 | 9.4 | 0.99
[7 empty] | mg/L | 1.7942 | 1.9867 | 0 | 1.0487
23 | 911000 | 70000 | 15000 | 933500 | 11 | 0.19 | Lbs. | 18.4481 | 10.45 | 0 | 10 | 0.036 | 7.64 | 9.2 | 1.01
[7 empty] | mg/L | 2.4317 | 1.2687 | 0 | 1.3398
24 | 902000 | 0 | 0 | 978400 | 11.2 | 0.21 | Lbs. | 17.5975 | 14.3 | 0.78125 | 9 | 0.034 | 7.7 | 9.8 | 1.06
[7 empty] | mg/L | 2.3393 | 1.9009 | 0.10385 | 1.1964
25 | 1125000 | 53000 | 15000 | 1091000 | 13.7 | 0.03 | Lbs. | 26.7119 | 12.65 | 0.375 | 11 | 0.032 | 7.76 | 10.5 | 1.01
[7 empty] | mg/L | 2.4797 | 1.5137 | 0.13186 | 1.1392
26 | 1081000 | 35000 | 0 | 785000 | 13.9 | 0 | Lbs. | 28.2188 | 9.9 | 0.125 | 10 | 0.038 | 7.88 | 11.1 | 1.1
[7 empty] | mg/L | 1.565 | 0.54905 | 0.013865 | 0.5546
27 | 796000 | 35000 | 0 | 743900 | 9.8 | 0.06 | Lbs. | 21 | 7.425 | 0.09375 | 7 | 0.04 | 7.67 | 9.4 | 1.08
[7 empty] | mg/L | 1.5816 | 0.55923 | 0.014122 | 0.52722
28 | 1042000 | 0 | 0 | 1304400 | 13.2 | 0.34 | Lbs. | 28.875 | 10.175 | 0.1875 | 10 | 0.077 | 7.8 | 9.9 | 1.05
[7 empty] | mg/L | 1.6613 | 0.58542 | 0.021576 | 0.57536
29 | 965000 | 35000 | 0 | 882700 | 12.3 | 0.45 | Lbs. | 32.1562 | 8.25 | 0.125 | 8 | 0.036 | 7.75 | 9.3 | 1.08
[7 empty] | mg/L | 1.9978 | 0.51254 | 0.015532 | 0.49701
30 | 937000 | 35000 | 30000 | 1075200 | 13.9 | 0.46 | Lbs. | 30.7956 | 11.55 | 0.46875 | 12 | 0.045 | 7.72 | 9.3 | 1.03
[7 empty] | mg/L | 3.9408 | 1.478 | 0.059984 | 1.5356
31 | 950000 | 36000 | 0 | 950000 | 8.9 | 0.4 | Lbs. | 30.7956 | 13.2 | 0.5 | 11 | 0.048 | 7.7 | 12.2 | 1
[7 empty] | mg/L | 3.8869 | 1.666 | 0.063107 | 0.69418
Monthly Totals
| 30548000 | 809000 | 225000 | 30283300 | 375.6 | 3.37 | Lbs. | 608.6303 | 458.15 | 12.875 | 311 | N/A | N/A | N/A | N/A
[7 empty] | mg/L | N/A | N/A | N/A | N/A
Daily Averages
| 985419.3548 | 26096.7742 | 7258.0645 | 976880.6452 | 12.1161 | 0.10871 | Lbs. | 19.6332 | 14.779 | 0.41532 | 10.0323 | 0.040226 | 7.7716 | 9.2742 | 1.0319
[7 empty] | mg/L | 2.1169 | 1.7108 | 0.053641 | 1.1101
Maximum Daily Totals
| 1267000 | 70000 | 30000 | 1304400 | 15.6 | 0.46 | Lbs. | 32.1562 | 23.375 | 1 | 13 | 0.077 | 7.99 | 12.2 | 1.13
[7 empty] | mg/L | 3.9408 | 2.2728 | 0.13186 | 1.6634
Minimum Daily Totals
| 796000 | 0 | 0 | 743900 | 8.9 | 0 | Lbs. | 13.1981 | 7.425 | 0 | 7 | 0.028 | 7.55 | 7.1 | 0.87
[7 empty] | mg/L | 1.4119 | 0.51171 | 0 | 0.49701

## Apr
April, 2020
Day | Value | Influent | Influent 2 | Combined Inf | Backwash | Backwash 2 | Comb. BW | Totalizer | EP-1 | FE-1 | FE-2 | BWP-1 | BWP-2 | SWP-1 | SWP-2 | BL-1 | Residual | Rain | Value | ACH | ACH-2 | Comb Lbs. | SA | SA-2 | Comb Lbs. | Polymer | Chlorine | Chlorine2 | Comb. Cl2 | Value | Raw | Finished
1 | Present | 173157 | 418426 | 1172000 | 156457 | 124570 | 35000 | 616104900 | 4944.5 | 42849 | 37561.5 | 393.3 | 939.6 | 333.7 | 696.2 | 226.8 | 1 | 0.11 | inches | 0.75 | 0 | 26.3963 | 8.5 | 0 | 18.7 | 2.5 | 13 | 0 | 13 | Turbidity | 4.38 | 0.048
| Previous | 171985 | 418426 |  | 156422 | 124570 |  | 615243800 | 4930.1 | 42849 | 37561.5 | 393.1 | 939.6 | 333.6 | 696.2 | 226.7 |  |  | Lbs. | 26.3963 | 0 |  | 18.7 | 0 |  | 0.625 |  |  |  | Temp. | 9.5 | 9.6
| Total | 1172000 | 0 |  | 35000 | 0 |  | 861100 | 14.4 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0.1 |  |  | mg/L | 2.7005 | 0 |  | 1.9131 | 0 |  | 0.063942 | 9.0633 | 0 |  | pH | 7.39 | 7.73
2 | Present | 173984 | 418426 | 827000 | 156457 | 124570 | 0 | 617027600 | 4954.5 | 42849 | 37561.5 | 393.3 | 939.6 | 333.7 | 696.2 | 226.8 | 1.03 | 0.02 | inches | 0.375 | 0 | 13.1981 | 6 | 0 | 13.2 | 1.875 | 9 | 0 | 9 | Turbidity | 3.47 | 0.068
| Total | 827000 | 0 |  | 0 | 0 |  | 922700 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 13.1981 | 0 |  | 13.2 | 0 |  | 0.46875 |  |  |  | Temp. | 9.4 | 9.4
[19 empty] | mg/L | 1.9136 | 0 |  | 1.9138 | 0 |  | 0.067963 | 1.3049 | 0 |  | pH | 7.4 | 7.58
3 | Present | 175084 | 418426 | 1100000 | 156492 | 124570 | 35000 | 618132900 | 4968 | 42849 | 37561.5 | 393.4 | 939.6 | 333.7 | 696.2 | 226.96 | 1.11 | 0.01 | inches | 0.4375 | 0 | 15.3978 | 8 | 0 | 17.6 | 2.625 | 13 | 0 | 13 | Turbidity | 2.52 | 0.048
| Total | 1100000 | 0 |  | 35000 | 0 |  | 1105300 | 13.5 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0.16 |  |  | Lbs. | 15.3978 | 0 |  | 17.6 | 0 |  | 0.65625 |  |  |  | Temp. | 9.1 | 8.6
[19 empty] | mg/L | 1.6784 | 0 |  | 1.9185 | 0 |  | 0.071534 | 1.417 | 0 |  | pH | 7.59 | 7.81
4 | Present | 176349 | 418426 | 1265000 | 156527 | 124570 | 35000 | 619199500 | 4983.5 | 42849 | 37561.5 | 393.6 | 939.6 | 333.8 | 696.2 | 227 | 1.03 | 0.08 | inches | 0.6875 | 0 | 24.1966 | 9.25 | 0 | 20.35 | 2.75 | 14 | 0 | 14 | Turbidity | 2.24 | 0.048
| Total | 1265000 | 0 |  | 35000 | 0 |  | 1066600 | 15.5 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0.04 |  |  | Lbs. | 24.1966 | 0 |  | 20.35 | 0 |  | 0.6875 |  |  |  | Temp. | 9.9 | 8.9
[19 empty] | mg/L | 2.2935 | 0 |  | 1.9289 | 0 |  | 0.065165 | 1.327 | 0 |  | pH | 7.46 | 7.68
5 | Present | 177068 | 418426 | 719000 | 156527 | 124570 | 0 | 619966400 | 4992.5 | 42849 | 37561.5 | 393.6 | 939.6 | 333.8 | 696.2 | 227 | 1.06 | 0 | inches | 0.375 | 0 | 13.1981 | 5.375 | 0 | 11.825 | 1.5 | 8 | 0 | 8 | Turbidity | 2.08 | 0.046
| Total | 719000 | 0 |  | 0 | 0 |  | 766900 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 13.1981 | 0 |  | 11.825 | 0 |  | 0.375 |  |  |  | Temp. | 11.4 | 9.3
[19 empty] | mg/L | 2.201 | 0 |  | 1.972 | 0 |  | 0.062537 | 1.3341 | 0 |  | pH | 7.55 | 7.75
6 | Present | 178136 | 418426 | 1068000 | 156562 | 124570 | 35000 | 620948300 | 5005.4 | 42849 | 37561.5 | 393.7 | 939.6 | 333.8 | 696.2 | 227.1 | 1.04 | 0 | inches | 0.625 | 0 | 21.9969 | 7.75 | 0 | 17.05 | 2.25 | 11 | 0 | 11 | Turbidity | 2.05 | 0.048
| Total | 1068000 | 0 |  | 35000 | 0 |  | 981900 | 12.9 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 21.9969 | 0 |  | 17.05 | 0 |  | 0.5625 |  |  |  | Temp. | 11.1 | 9.5
[19 empty] | mg/L | 2.4696 | 0 |  | 1.9142 | 0 |  | 0.063152 | 1.235 | 0 |  | pH | 7.45 | 7.69
7 | Present | 178894 | 418426 | 758000 | 156562 | 124570 | 0 | 621978800 | 5014.8 | 42849 | 37561.5 | 393.7 | 939.6 | 333.8 | 696.2 | 227.1 | 1.07 | 0 | inches | 0.375 | 0 | 13.1981 | 5.25 | 0 | 11.55 | 1.75 | 9 | 0 | 9 | Turbidity | 1.13 | 0.048
| Total | 758000 | 0 |  | 0 | 0 |  | 1030500 | 9.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 13.1981 | 0 |  | 11.55 | 0 |  | 0.4375 |  |  |  | Temp. | 12 | 12.3
[19 empty] | mg/L | 2.0877 | 0 |  | 1.827 | 0 |  | 0.069206 | 1.4237 | 0 |  | pH | 7.5 | 7.69
8 | Present | 180017 | 418426 | 1123000 | 156597 | 124570 | 35000 | 623042600 | 5028.6 | 42849 | 37561.5 | 393.9 | 939.6 | 333.9 | 696.2 | 227.1 | 1.04 | 0 | inches | 0.625 | 0 | 21.9969 | 8.5 | 0 | 18.7 | 2.5 | 13 | 0 | 13 | Turbidity | 1.69 | 0.052
| Total | 1123000 | 0 |  | 35000 | 0 |  | 1063800 | 13.8 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 21.9969 | 0 |  | 18.7 | 0 |  | 0.625 |  |  |  | Temp. | 10.1 | 10.8
[19 empty] | mg/L | 2.3486 | 0 |  | 1.9966 | 0 |  | 0.066732 | 1.388 | 0 |  | pH | 7.54 | 7.73
9 | Present | 181039 | 418426 | 1022000 | 156632 | 124570 | 35000 | 624047300 | 5041.1 | 42849 | 37561.5 | 394.1 | 939.6 | 334 | 696.2 | 227.1 | 1.08 | 0 | inches | 0.5 | 0 | 17.5975 | 7.5 | 0 | 16.5 | 2.375 | 12 | 0 | 12 | Turbidity | 1.63 | 0.047
| Total | 1022000 | 0 |  | 35000 | 0 |  | 1004700 | 12.5 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 17.5975 | 0 |  | 16.5 | 0 |  | 0.59375 |  |  |  | Temp. | 11.1 | 12
[19 empty] | mg/L | 2.0646 | 0 |  | 1.9358 | 0 |  | 0.069661 | 1.4079 | 0 |  | pH | 7.64 | 7.7
10 | Present | 182178 | 418426 | 1139000 | 156668 | 124570 | 36000 | 625130400 | 5055 | 42849 | 37561.5 | 394.2 | 939.6 | 334.1 | 696.2 | 227.2 | 1.02 | 0 | inches | 0.625 | 0 | 21.9969 | 8.375 | 0 | 18.425 | 2.5 | 13 | 0 | 13 | Turbidity | 1.36 | 0.047
| Total | 1139000 | 0 |  | 36000 | 0 |  | 1083100 | 13.9 | 0 | 0 | 0.1 | 0 | 0.1 | 0 | 0.1 |  |  | Lbs. | 21.9969 | 0 |  | 18.425 | 0 |  | 0.625 |  |  |  | Temp. | 10.3 | 12.9
[19 empty] | mg/L | 2.3156 | 0 |  | 1.9396 | 0 |  | 0.065795 | 1.3685 | 0 |  | pH | 7.55 | 7.61
11 | Present | 183287 | 418426 | 1109000 | 156668 | 124570 | 0 | 626129500 | 5068.7 | 42849 | 37561.5 | 394.2 | 939.6 | 334.1 | 696.2 | 227.3 | 1 | 0 | inches | 0.5 | 0 | 17.5975 | 8.25 | 0 | 18.15 | 0 | 13 | 0 | 13 | Turbidity | 1.35 | 0.048
| Total | 1109000 | 0 |  | 0 | 0 |  | 999100 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 17.5975 | 0 |  | 18.15 | 0 |  | 0 |  |  |  | Temp. | 10.7 | 11.8
[19 empty] | mg/L | 1.9026 | 0 |  | 1.9624 | 0 |  | 0 | 1.4055 | 0 |  | pH | 7.53 | 7.72
12 | Present | 184162 | 418426 | 875000 | 156703 | 124570 | 35000 | 627213700 | 5079.6 | 42849 | 37561.5 | 394.2 | 939.6 | 334.2 | 696.2 | 227.3 | 1.05 | 0 | inches | 0.375 | 0 | 13.1981 | 6.375 | 0 | 14.025 | 0 | 10 | 0 | 10 | Turbidity | 1.3 | 0.047
| Total | 875000 | 0 |  | 35000 | 0 |  | 1084200 | 10.9 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 13.1981 | 0 |  | 14.025 | 0 |  | 0 |  |  |  | Temp. | 10.6 | 11.2
[19 empty] | mg/L | 1.8086 | 0 |  | 1.9219 | 0 |  | 0 | 1.3703 | 0 |  | pH | 7.66 | 7.73
13 | Present | 184617 | 419076 | 1105000 | 156703 | 124605 | 35000 | 628289700 | 5085.2 | 42857.1 | 37569.6 | 394.4 | 939.9 | 334.2 | 696.4 | 227.3 | 0.99 | 0 | inches | 0.1875 | 2.125 | 17.7553 | 3.1875 | 2.75 | 13.0625 | 0 | 5 | 6 | 11 | Turbidity | 1.28 | 0.048
| Total | 455000 | 650000 |  | 0 | 35000 |  | 1076000 | 5.6 | 8.1 | 8.1 | 0.2 | 0.3 | 0 | 0.2 | 0 |  |  | Lbs. | 6.5991 | 11.1562 |  | 7.0125 | 6.05 |  | 0 |  |  |  | Temp. | 9.4 | 10.2
[19 empty] | mg/L | 1.739 | 2.058 |  | 1.848 | 1.116 |  | 0 | 1.3176 | 1.1068 |  | pH | 7.45 | 7.85
14 | Present | 185813 | 419076 | 1196000 | 156738 | 124605 | 35000 | 629449100 | 5099.9 | 42857.1 | 37569.6 | 394.6 | 939.9 | 334.3 | 696.4 | 227.3 | 0.99 | 0 | inches | 0.5625 | 0 | 19.7972 | 9 | 0 | 19.8 | 1.125 | 14 | 0 | 14 | Turbidity | 1.32 | 0.047
| Total | 1196000 | 0 |  | 35000 | 0 |  | 1159400 | 14.7 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 19.7972 | 0 |  | 19.8 | 0 |  | 0.28125 |  |  |  | Temp. | 10.1 | 10.5
[19 empty] | mg/L | 1.9848 | 0 |  | 1.985 | 0 |  | 0.028197 | 1.4036 | 0 |  | pH | 7.38 | 7.74
15 | Present | 186981 | 419076 | 1168000 | 156738 | 124605 | 0 | 630485600 | 5114.4 | 42857.1 | 37569.6 | 394.6 | 939.9 | 334.3 | 696.4 | 227.4 | 1.06 | 0 | inches | 0.5625 | 0 | 19.7972 | 8.75 | 0 | 19.25 | 1.375 | 14 | 0 | 14 | Turbidity | 1.35 | 0.038
| Total | 1168000 | 0 |  | 0 | 0 |  | 1036500 | 14.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 19.7972 | 0 |  | 19.25 | 0 |  | 0.34375 |  |  |  | Temp. | 11.7 | 11.2
[19 empty] | mg/L | 2.0323 | 0 |  | 1.9762 | 0 |  | 0.035289 | 1.4372 | 0 |  | pH | 7.4 | 7.73
16 | Present | 188170 | 419076 | 1189000 | 156773 | 124605 | 35000 | 631617500 | 5128.8 | 42857.1 | 37569.6 | 394.7 | 939.9 | 334.3 | 696.4 | 227.4 | 1.04 | 0 | inches | 0.5625 | 0 | 19.7972 | 8.625 | 0 | 18.975 | 1.5 | 14 | 0 | 14 | Turbidity | 1.34 | 0.035
| Total | 1189000 | 0 |  | 35000 | 0 |  | 1131900 | 14.4 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 |  |  | Lbs. | 19.7972 | 0 |  | 18.975 | 0 |  | 0.375 |  |  |  | Temp. | 11 | 10.6
[19 empty] | mg/L | 1.9964 | 0 |  | 1.9135 | 0 |  | 0.037817 | 1.4118 | 0 |  | pH | 7.36 | 7.7
17 | Present | 189352 | 419047 | 1153000 | 156808 | 124605 | 35000 | 632845200 | 5143.4 | 42857.1 | 37569.6 | 394.9 | 939.9 | 334.4 | 696.4 | 227.6 | 1.1 | 0.04 | inches | 0.625 | 0 | 21.9969 | 8.5 | 0 | 18.7 | 1.875 | 13 | 0 | 13 | Turbidity | 0.94 | 0.031
| Total | 1182000 | -29000 |  | 35000 | 0 |  | 1227700 | 14.6 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0.2 |  |  | Lbs. | 21.9969 | 0 |  | 18.7 | 0 |  | 0.46875 |  |  |  | Temp. | 10 | 11.7
[19 empty] | mg/L | 2.2314 | 0 |  | 1.897 | 0 |  | 0.047551 | 1.3187 | 0 |  | pH | 7.47 | 7.54
18 | Present | 190276 | 419076 | 953000 | 156808 | 124605 | 0 | 633923100 | 5154.9 | 42857.1 | 37569.6 | 395.1 | 939.9 | 334.4 | 696.4 | 227.6 | 1.01 | 0.05 | inches | 0.4375 | 0 | 15.3978 | 7 | 0 | 15.4 | 1.75 | 11 | 0 | 11 | Turbidity | 0.96 | 0.047
| Total | 924000 | 29000 |  | 0 | 0 |  | 1077900 | 11.5 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 |  |  | Lbs. | 15.3978 | 0 |  | 15.4 | 0 |  | 0.4375 |  |  |  | Temp. | 10.7 | 10.8
[19 empty] | mg/L | 1.9981 | 0 |  | 1.9984 | 0 |  | 0.056773 | 1.4274 | 0 |  | pH | 7.49 | 7.7
19 | Present | 191332 | 419076 | 1056000 | 156843 | 124605 | 35000 | 634808300 | 5167.8 | 42857.1 | 37569.6 | 395.1 | 939.9 | 334.5 | 696.4 | 227.7 | 0.98 | 0 | inches | 0.5 | 0 | 17.5975 | 7.75 | 0 | 17.05 | 1.75 | 12 | 0 | 12 | Turbidity | 0.95 | 0.048
| Total | 1056000 | 0 |  | 35000 | 0 |  | 885200 | 12.9 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.1 |  |  | Lbs. | 17.5975 | 0 |  | 17.05 | 0 |  | 0.4375 |  |  |  | Temp. | 11.1 | 11.5
[19 empty] | mg/L | 1.9981 | 0 |  | 1.936 | 0 |  | 0.049676 | 1.3625 | 0 |  | pH | 7.42 | 7.77
20 | Present | 192367 | 419076 | 1035000 | 156843 | 124605 | 0 | 635957900 | 5180.6 | 42857.1 | 37569.6 | 395.1 | 939.9 | 334.5 | 696.4 | 227.7 | 0.98 | 0 | inches | 0.5 | 0 | 17.5975 | 7.875 | 0 | 17.325 | 2.25 | 13 | 0 | 13 | Turbidity | 1.02 | 0.057
| Total | 1035000 | 0 |  | 0 | 0 |  | 1149600 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 17.5975 | 0 |  | 17.325 | 0 |  | 0.5625 |  |  |  | Temp. | 11.1 | 10.8
[19 empty] | mg/L | 2.0387 | 0 |  | 2.0071 | 0 |  | 0.065165 | 1.506 | 0 |  | pH | 7.42 | 7.74
21 | Present | 193433 | 419076 | 1066000 | 156879 | 124605 | 36000 | 636976300 | 5193.5 | 42857.1 | 37569.6 | 395.2 | 939.9 | 334.5 | 696.4 | 227.7 | 1.03 | 0.12 | inches | 0.625 | 0 | 21.9969 | 7.875 | 0 | 17.325 | 2.5 | 17 | 0 | 17 | Turbidity | 1.1 | 0.036
| Total | 1066000 | 0 |  | 36000 | 0 |  | 1018400 | 12.9 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 |  |  | Lbs. | 21.9969 | 0 |  | 17.325 | 0 |  | 0.625 |  |  |  | Temp. | 12.1 | 11.9
[19 empty] | mg/L | 2.4742 | 0 |  | 1.9487 | 0 |  | 0.0703 | 1.9122 | 0 |  | pH | 7.52 | 7.73
22 | Present | 194560 | 419076 | 1127000 | 156914 | 124605 | 35000 | 637979400 | 5207.4 | 42857.1 | 37569.6 | 395.4 | 939.9 | 334.6 | 696.4 | 227.8 | 1.12 | 0.19 | inches | 0.625 | 0 | 21.9969 | 8.125 | 0 | 17.875 | 2.375 | 11 | 0 | 11 | Turbidity | 1.11 | 0.04
| Total | 1127000 | 0 |  | 35000 | 0 |  | 1003100 | 13.9 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0.1 |  |  | Lbs. | 21.9969 | 0 |  | 17.875 | 0 |  | 0.59375 |  |  |  | Temp. | 11.8 | 12.7
[19 empty] | mg/L | 2.3403 | 0 |  | 1.9018 | 0 |  | 0.06317 | 1.1703 | 0 |  | pH | 7.66 | 7.79
23 | Present | 195450 | 419076 | 890000 | 156914 | 124605 | 0 | 639038600 | 5218.5 | 42857.1 | 37569.6 | 395.4 | 939.9 | 334.6 | 696.4 | 227.8 | 1.13 | 0.03 | inches | 0.75 | 0 | 26.3963 | 6.25 | 0 | 13.75 | 2 | 8 | 0 | 8 | Turbidity | 1.9 | 0.042
| Total | 890000 | 0 |  | 0 | 0 |  | 1059200 | 11.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 26.3963 | 0 |  | 13.75 | 0 |  | 0.5 |  |  |  | Temp. | 11.5 | 12
[19 empty] | mg/L | 3.5562 | 0 |  | 1.8525 | 0 |  | 0.067362 | 1.0778 | 0 |  | pH | 7.58 | 7.74
24 | Present | 196580 | 419076 | 1130000 | 156949 | 124605 | 35000 | 640072300 | 5232.3 | 42857.1 | 37569.6 | 395.6 | 939.9 | 334.7 | 696.4 | 227.8 | 1.05 | 0.09 | inches | 0.625 | 0 | 21.9969 | 8.25 | 0 | 18.15 | 2.75 | 10 | 0 | 10 | Turbidity | 1.11 | 0.036
| Total | 1130000 | 0 |  | 35000 | 0 |  | 1033700 | 13.8 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 21.9969 | 0 |  | 18.15 | 0 |  | 0.6875 |  |  |  | Temp. | 11 | 11.8
[19 empty] | mg/L | 2.3341 | 0 |  | 1.9259 | 0 |  | 0.07295 | 1.0611 | 0 |  | pH | 7.6 | 7.77
25 | Present | 197929 | 419076 | 1349000 | 156984 | 124605 | 35000 | 641187900 | 5248.8 | 42857.1 | 37569.6 | 395.7 | 939.9 | 334.7 | 696.4 | 227.9 | 1.03 | 0.14 | inches | 0.75 | 0 | 26.3963 | 10 | 0 | 22 | 3.125 | 12 | 0 | 12 | Turbidity | 1.05 | 0.036
| Total | 1349000 | 0 |  | 35000 | 0 |  | 1115600 | 16.5 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 26.3963 | 0 |  | 22 | 0 |  | 0.78125 |  |  |  | Temp. | 12 | 13
[19 empty] | mg/L | 2.3462 | 0 |  | 1.9554 | 0 |  | 0.06944 | 1.0666 | 0 |  | pH | 7.58 | 7.81
26 | Present | 198652 | 419076 | 723000 | 156984 | 124605 | 0 | 642193732 | 5257.9 | 42857.1 | 37569.6 | 395.8 | 939.9 | 334.8 | 696.4 | 228 | 1.06 | 0.11 | inches | 0.4375 | 0 | 15.3978 | 5.375 | 0 | 11.825 | 1.5 | 6 | 0 | 6 | Turbidity | 1.11 | 0.038
| Total | 723000 | 0 |  | 0 | 0 |  | 1005832 | 9.1 | 0 | 0 | 0.1 | 0 | 0.1 | 0 | 0.1 |  |  | Lbs. | 15.3978 | 0 |  | 11.825 | 0 |  | 0.375 |  |  |  | Temp. | 11 | 11.6
[19 empty] | mg/L | 2.5536 | 0 |  | 1.9611 | 0 |  | 0.062191 | 0.99505 | 0 |  | pH | 7.7 | 7.83
27 | Present | 199207 | 419842 | 1321000 | 156984 | 124605 | 0 | 643305500 | 5264.6 | 42866.8 | 37579.3 | 395.8 | 939.9 | 334.8 | 696.4 | 228 | 0.97 | 0 | inches | 0.375 | 3.125 | 29.6044 | 4 | 3 | 15.4 | 0.9375 | 5 | 12 | 17 | Turbidity | 1.17 | 0.041
| Total | 555000 | 766000 |  | 0 | 0 |  | 1111768 | 6.7 | 9.7 | 9.7 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 13.1981 | 16.4062 |  | 8.8 | 6.6 |  | 0.23438 |  |  |  | Temp. | 12 | 12
[19 empty] | mg/L | 2.8514 | 2.5681 |  | 1.9012 | 1.0331 |  | 0.050635 | 1.0802 | 1.8784 |  | pH | 7.52 | 7.84
28 | Present | 199207 | 420748 | 906000 | 156984 | 124641 | 36000 | 644280100 | 5264.6 | 42878 | 37590.5 | 395.8 | 940.2 | 334.8 | 696.6 | 228 | 1.07 | 0 | inches | 0 | 4.5 | 23.625 | 0 | 3.625 | 7.975 | 0 | 0 | 11 | 11 | Turbidity | 1.23 | 0.034
| Total | 0 | 906000 |  | 0 | 36000 |  | 974600 | 0 | 11.2 | 11.2 | 0 | 0.3 | 0 | 0.2 | 0 |  |  | Lbs. | 0 | 23.625 |  | 0 | 7.975 |  | 0 |  |  |  | Temp. | 11.8 | 13.4
[19 empty] | mg/L | 0 | 3.1266 |  | 0 | 1.0554 |  | 0 | 0 | 1.4558 |  | pH | 7.6 | 7.73
29 | Present | 199207 | 421595 | 847000 | 156984 | 124641 | 0 | 645217000 | 5264.6 | 42888.7 | 37601.2 | 395.8 | 940.2 | 334.8 | 696.6 | 228 | 1.1 | 0.1 | inches | 0 | 3.75 | 19.6875 | 0 | 3.5 | 7.7 | 0.5 | 0 | 9 | 9 | Turbidity | 1.23 | 0.047
| Total | 0 | 847000 |  | 0 | 0 |  | 936900 | 0 | 10.7 | 10.7 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 0 | 19.6875 |  | 0 | 7.7 |  | 0.125 |  |  |  | Temp. | 12.7 | 12.5
[19 empty] | mg/L | 0 | 2.787 |  | 0 | 1.09 |  | 0.017695 | 0 | 1.2741 |  | pH | 7.47 | 7.71
30 | Present | 200149 | 421815 | 1162000 | 157020 | 124676 | 71000 | 646212500 | 5275.8 | 42891.4 | 37603.9 | 395.9 | 939.5 | 334.8 | 696.8 | 228.1 | 1.09 | 0 | inches | 0.625 | 1 | 27.2469 | 6.125 | 0.75 | 15.125 | 0.25 | 8 | 2 | 10 | Turbidity | 1.49 | 0.046
| Total | 942000 | 220000 |  | 36000 | 35000 |  | 995500 | 11.2 | 2.7 | 2.7 | 0.1 | -0.7 | 0 | 0.2 | 0.1 |  |  | Lbs. | 21.9969 | 5.25 |  | 13.475 | 1.65 |  | 0.0625 |  |  |  | Temp. | 12.6 | 12.5
[19 empty] | mg/L | 2.7999 | 2.8613 |  | 1.7152 | 0.89928 |  | 0.0079554 | 1.0183 | 1.09 |  | pH | 7.49 | 7.76
| Total | 28164000 | 3389000 | 31553000 | 598000 | 106000 | 704000 | 30968700 | 345.7 | 42.4 | 42.4 | 2.8 | -0.1 | 1.2 | 0.6 | 1.4 | N/A | 1.09 | Total Lbs. | 527.925 | 76.125 | 604.05 | 452.7875 | 29.975 | 482.7625 | 12.5469 | 0 | 0 | 351 | Avg Turb. | 1.562 | 0.044733
| Average | 938800 | 112966.6667 | 1051766.6667 | 19933.3333 | 3533.3333 | 23466.6667 | 1032290 | 11.5233 | 1.4133 | 1.4133 | 0.093333 | -0.0033333 | 0.04 | 0.02 | 0.046667 | 1.0443 | 0.036333 | Avg Lbs. | 17.5975 | 2.5375 | 20.135 | 15.0929 | 0.99917 | 16.0921 | 0.41823 | 0 | 0 | 11.7 | Avg. Temp. | 10.96 | 11.2333
| High | 1349000 | 0 | 1349000 | 36000 | 36000 | 71000 | 1227700 | 16.5 | 11.2 | 11.2 | 0.2 | 0.3 | 0.1 | 0.2 | 0.2 | 1.13 | 0.19 | High Lbs. | 26.3963 | 23.625 | 29.6044 | 22 | 7.975 | 22 | 0.78125 | 0 | 0 | 17 | Avg pH | 7.5123 | 7.73
| Low | 0 | 0 | 719000 | 35000 | 0 | 0 | 766900 | 14.4 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0.1 | 0.97 | 0 | Low Lbs. | 0 | 0 | 13.1981 | 0 | 0 | 7.7 | 0 | 0 | 0 | 6
[19 empty] | Avg mg/L | 2.102 | 0.4467 |  | 1.7956 | 0.17313 |  | 0.048928 | 1.4871 | 0.22684 |  | High Turb. | 4.38 | 0.068
[19 empty] | High mg/L | 3.5562 | 3.1266 |  | 2.0071 | 1.116 |  | 0.07295 | 9.0633 | 1.8784 |  | High Temp. | 12.7 | 13.4
[19 empty] | Low mg/L | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 |  | High pH | 7.7 | 7.85
*Averages, Highs and Lows represent only days the plant was in operation
[30 empty] | Low Turb. | 0.94 | 0.031
[30 empty] | Low Temp. | 9.1 | 8.6
[30 empty] | Low pH | 7.36 | 7.54

## AprTotals
April, 2020
Combined Plant Daily Totals
Day | Gallons |  |  |  | Plant Hours | Rain Inches | Chemical Usage |  |  |  |  | Finished Water |  |  | Residual Chlorine
| Influent | Backwash | Flush | Totalizer |  |  | Value | ACH | SodaAsh | Polymer | NaOCl | Turbidity | pH | Temp
1 | 1172000 | 35000 | 15000 | 861100 | 14.4 | 0.11 | Lbs. | 26.3963 | 18.7 | 0.625 | 13 | 0.048 | 7.73 | 9.6 | 1
[7 empty] | mg/L | 2.7005 | 1.9131 | 0.063942 | 9.0633
2 | 827000 | 0 | 0 | 922700 | 10 | 0.02 | Lbs. | 13.1981 | 13.2 | 0.46875 | 9 | 0.068 | 7.58 | 9.4 | 1.03
[7 empty] | mg/L | 1.9136 | 1.9138 | 0.067963 | 1.3049
3 | 1100000 | 35000 | 24000 | 1105300 | 13.5 | 0.01 | Lbs. | 15.3978 | 17.6 | 0.65625 | 13 | 0.048 | 7.81 | 8.6 | 1.11
[7 empty] | mg/L | 1.6784 | 1.9185 | 0.071534 | 1.417
4 | 1265000 | 35000 | 6000 | 1066600 | 15.5 | 0.08 | Lbs. | 24.1966 | 20.35 | 0.6875 | 14 | 0.048 | 7.68 | 8.9 | 1.03
[7 empty] | mg/L | 2.2935 | 1.9289 | 0.065165 | 1.327
5 | 719000 | 0 | 0 | 766900 | 9 | 0 | Lbs. | 13.1981 | 11.825 | 0.375 | 8 | 0.046 | 7.75 | 9.3 | 1.06
[7 empty] | mg/L | 2.201 | 1.972 | 0.062537 | 1.3341
6 | 1068000 | 35000 | 15000 | 981900 | 12.9 | 0 | Lbs. | 21.9969 | 17.05 | 0.5625 | 11 | 0.048 | 7.69 | 9.5 | 1.04
[7 empty] | mg/L | 2.4696 | 1.9142 | 0.063152 | 1.235
7 | 758000 | 0 | 0 | 1030500 | 9.4 | 0 | Lbs. | 13.1981 | 11.55 | 0.4375 | 9 | 0.048 | 7.69 | 12.3 | 1.07
[7 empty] | mg/L | 2.0877 | 1.827 | 0.069206 | 1.4237
8 | 1123000 | 35000 | 0 | 1063800 | 13.8 | 0 | Lbs. | 21.9969 | 18.7 | 0.625 | 13 | 0.052 | 7.73 | 10.8 | 1.04
[7 empty] | mg/L | 2.3486 | 1.9966 | 0.066732 | 1.388
9 | 1022000 | 35000 | 0 | 1004700 | 12.5 | 0 | Lbs. | 17.5975 | 16.5 | 0.59375 | 12 | 0.047 | 7.7 | 12 | 1.08
[7 empty] | mg/L | 2.0646 | 1.9358 | 0.069661 | 1.4079
10 | 1139000 | 36000 | 15000 | 1083100 | 13.9 | 0 | Lbs. | 21.9969 | 18.425 | 0.625 | 13 | 0.047 | 7.61 | 12.9 | 1.02
[7 empty] | mg/L | 2.3156 | 1.9396 | 0.065795 | 1.3685
11 | 1109000 | 0 | 15000 | 999100 | 13.7 | 0 | Lbs. | 17.5975 | 18.15 | 0 | 13 | 0.048 | 7.72 | 11.8 | 1
[7 empty] | mg/L | 1.9026 | 1.9624 | 0 | 1.4055
12 | 875000 | 35000 | 0 | 1084200 | 10.9 | 0 | Lbs. | 13.1981 | 14.025 | 0 | 10 | 0.047 | 7.73 | 11.2 | 1.05
[7 empty] | mg/L | 1.8086 | 1.9219 | 0 | 1.3703
13 | 1105000 | 35000 | 0 | 1076000 | 13.7 | 0 | Lbs. | 17.7553 | 13.0625 | 0 | 11 | 0.048 | 7.85 | 10.2 | 0.99
[7 empty] | mg/L | 1.8985 | 1.482 | 0 | 1.2122
14 | 1196000 | 35000 | 0 | 1159400 | 14.7 | 0 | Lbs. | 19.7972 | 19.8 | 0.28125 | 14 | 0.047 | 7.74 | 10.5 | 0.99
[7 empty] | mg/L | 1.9848 | 1.985 | 0.028197 | 1.4036
15 | 1168000 | 0 | 15000 | 1036500 | 14.5 | 0 | Lbs. | 19.7972 | 19.25 | 0.34375 | 14 | 0.038 | 7.73 | 11.2 | 1.06
[7 empty] | mg/L | 2.0323 | 1.9762 | 0.035289 | 1.4372
16 | 1189000 | 35000 | 0 | 1131900 | 14.4 | 0 | Lbs. | 19.7972 | 18.975 | 0.375 | 14 | 0.035 | 7.7 | 10.6 | 1.04
[7 empty] | mg/L | 1.9964 | 1.9135 | 0.037817 | 1.4118
17 | 1153000 | 35000 | 30000 | 1227700 | 14.6 | 0.04 | Lbs. | 21.9969 | 18.7 | 0.46875 | 13 | 0.031 | 7.54 | 11.7 | 1.1
[7 empty] | mg/L | 2.2314 | 1.897 | 0.047551 | 1.3187
18 | 953000 | 0 | 0 | 1077900 | 11.5 | 0.05 | Lbs. | 15.3978 | 15.4 | 0.4375 | 11 | 0.047 | 7.7 | 10.8 | 1.01
[7 empty] | mg/L | 1.9981 | 1.9984 | 0.056773 | 1.4274
19 | 1056000 | 35000 | 15000 | 885200 | 12.9 | 0 | Lbs. | 17.5975 | 17.05 | 0.4375 | 12 | 0.048 | 7.77 | 11.5 | 0.98
[7 empty] | mg/L | 1.9981 | 1.936 | 0.049676 | 1.3625
20 | 1035000 | 0 | 0 | 1149600 | 12.8 | 0 | Lbs. | 17.5975 | 17.325 | 0.5625 | 13 | 0.057 | 7.74 | 10.8 | 0.98
[7 empty] | mg/L | 2.0387 | 2.0071 | 0.065165 | 1.506
21 | 1066000 | 36000 | 0 | 1018400 | 12.9 | 0.12 | Lbs. | 21.9969 | 17.325 | 0.625 | 17 | 0.036 | 7.73 | 11.9 | 1.03
[7 empty] | mg/L | 2.4742 | 1.9487 | 0.0703 | 1.9122
22 | 1127000 | 35000 | 15000 | 1003100 | 13.9 | 0.19 | Lbs. | 21.9969 | 17.875 | 0.59375 | 11 | 0.04 | 7.79 | 12.7 | 1.12
[7 empty] | mg/L | 2.3403 | 1.9018 | 0.06317 | 1.1703
23 | 890000 | 0 | 0 | 1059200 | 11.1 | 0.03 | Lbs. | 26.3963 | 13.75 | 0.5 | 8 | 0.042 | 7.74 | 12 | 1.13
[7 empty] | mg/L | 3.5562 | 1.8525 | 0.067362 | 1.0778
24 | 1130000 | 35000 | 0 | 1033700 | 13.8 | 0.09 | Lbs. | 21.9969 | 18.15 | 0.6875 | 10 | 0.036 | 7.77 | 11.8 | 1.05
[7 empty] | mg/L | 2.3341 | 1.9259 | 0.07295 | 1.0611
25 | 1349000 | 35000 | 15000 | 1115600 | 16.5 | 0.14 | Lbs. | 26.3963 | 22 | 0.78125 | 12 | 0.036 | 7.81 | 13 | 1.03
[7 empty] | mg/L | 2.3462 | 1.9554 | 0.06944 | 1.0666
26 | 723000 | 0 | 15000 | 1005832 | 9.1 | 0 | Lbs. | 15.3978 | 11.825 | 0.375 | 6 | 0.038 | 7.83 | 11.6 | 1.06
[7 empty] | mg/L | 2.5536 | 1.9611 | 0.062191 | 0.99505
27 | 1321000 | 0 | 0 | 1111768 | 16.4 | 0 | Lbs. | 29.6044 | 15.4 | 0.23438 | 17 | 0.041 | 7.84 | 12 | 0.97
[7 empty] | mg/L | 2.7097 | 1.4671 | 0.050635 | 1.4793
28 | 906000 | 36000 | 0 | 974600 | 11.2 | 0 | Lbs. | 23.625 | 7.975 | 0 | 11 | 0.034 | 7.73 | 13.4 | 1.07
[7 empty] | mg/L | 1.5633 | 0.52772 | 0 | 0.72789
29 | 847000 | 0 | 0 | 936900 | 10.7 | 0.1 | Lbs. | 19.6875 | 7.7 | 0.125 | 9 | 0.047 | 7.71 | 12.5 | 1.1
[7 empty] | mg/L | 1.3935 | 0.54502 | 0.017695 | 0.63703
30 | 1162000 | 71000 | 15000 | 995500 | 13.9 | 0 | Lbs. | 27.2469 | 15.125 | 0.0625 | 10 | 0.046 | 7.76 | 12.5 | 1.09
[7 empty] | mg/L | 2.8306 | 1.3072 | 0.0079554 | 1.0542
Monthly Totals
| 31553000 | 704000 | 210000 | 30968700 | 388.1 | 0.98 | Lbs. | 604.05 | 482.7625 | 12.5469 | 351 | N/A | N/A | N/A | N/A
[7 empty] | mg/L | N/A | N/A | N/A | N/A
Daily Averages
| 1051766.6667 | 23466.6667 | 7000 | 1032290 | 12.9367 | 0.032667 | Lbs. | 20.135 | 16.0921 | 0.41823 | 11.7 | 0.044733 | 7.73 | 11.2333 | 1.0443
[7 empty] | mg/L | 2.2021 | 1.791 | 0.048928 | 1.5435
Maximum Daily Totals
| 1349000 | 71000 | 30000 | 1227700 | 16.5 | 0.19 | Lbs. | 29.6044 | 22 | 0.78125 | 17 | 0.068 | 7.85 | 13.4 | 1.13
[7 empty] | mg/L | 3.5562 | 2.0071 | 0.07295 | 9.0633
Minimum Daily Totals
| 719000 | 0 | 0 | 766900 | 9 | 0 | Lbs. | 13.1981 | 7.7 | 0 | 6 | 0.031 | 7.54 | 8.6 | 0.97
[7 empty] | mg/L | 1.3935 | 0.52772 | 0 | 0.63703

## May
May, 2020
Day | Value | Influent | Influent 2 | Combined Inf | Backwash | Backwash 2 | Comb. BW | Totalizer | EP-1 | FE-1 | FE-2 | BWP-1 | BWP-2 | SWP-1 | SWP-2 | BL-1 | Residual | Rain | Value | ACH | ACH-2 | Comb Lbs. | SA | SA-2 | Comb Lbs. | Polymer | Chlorine | Chlorine2 | Comb. Cl2 | Value | Raw | Finished
1 | Present | 201126 | 421815 | 977000 | 157056 | 124676 | 36000 | 647258800 | 5288 | 42891.4 | 37603.9 | 396.1 | 939.5 | 334.9 | 696.8 | 228.1 | 1.11 | 0.12 | inches | 0.5625 | 0 | 19.7972 | 7 | 0 | 15.4 | 0 | 8 | 0 | 8 | Turbidity | 0.89 | 0.049
| Previous | 200149 | 421815 |  | 157020 | 124676 |  | 646212500 | 5275.8 | 42891.4 | 37603.9 | 395.9 | 939.5 | 334.8 | 696.8 | 228.1 |  |  | Lbs. | 19.7972 | 0 |  | 15.4 | 0 |  | 0 |  |  |  | Temp. | 11.4 | 13.1
| Total | 977000 | 0 |  | 36000 | 0 |  | 1046300 | 12.2 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0 |  |  | mg/L | 2.4296 | 0 |  | 1.89 | 0 |  | 0 | 0.98181 | 0 |  | pH | 7.6 | 7.65
2 | Present | 202121 | 421815 | 995000 | 157056 | 124676 | 0 | 648315600 | 5300.3 | 42891.4 | 37603.9 | 396.1 | 939.5 | 334.9 | 696.8 | 228.1 | 0.98 | 0.6 | inches | 0.625 | 0 | 21.9969 | 7.25 | 0 | 15.95 | 0 | 9 | 0 | 9 | Turbidity | 1.02 | 0.049
| Total | 995000 | 0 |  | 0 | 0 |  | 1056800 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 21.9969 | 0 |  | 15.95 | 0 |  | 0 |  |  |  | Temp. | 13.5 | 12.9
[19 empty] | mg/L | 2.6508 | 0 |  | 1.9221 | 0 |  | 0 | 1.0846 | 0 |  | pH | 7.44 | 7.77
3 | Present | 202955 | 421815 | 834000 | 157092 | 124676 | 36000 | 649107800 | 5310.5 | 42891.4 | 37603.9 | 396.3 | 939.5 | 335 | 696.8 | 228.2 | 0.95 | 0.16 | inches | 0.75 | 0 | 26.3963 | 6 | 0 | 13.2 | 0 | 7 | 0 | 7 | Turbidity | 1.76 | 0.061
| Total | 834000 | 0 |  | 36000 | 0 |  | 792200 | 10.2 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0.1 |  |  | Lbs. | 26.3963 | 0 |  | 13.2 | 0 |  | 0 |  |  |  | Temp. | 12 | 11.9
[19 empty] | mg/L | 3.795 | 0 |  | 1.8978 | 0 |  | 0 | 1.0064 | 0 |  | pH | 7.45 | 7.77
4 | Present | 204061 | 421815 | 1106000 | 157128 | 124676 | 36000 | 650082100 | 5323.9 | 42891.4 | 37603.9 | 396.4 | 939.5 | 335 | 696.8 | 228.2 | 0.95 | 0.01 | inches | 0.75 | 0 | 26.3963 | 8.25 | 0 | 18.15 | 5 | 11 | 0 | 11 | Turbidity | 1.59 | 0.046
| Total | 1106000 | 0 |  | 36000 | 0 |  | 974300 | 13.4 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 |  |  | Lbs. | 26.3963 | 0 |  | 18.15 | 0 |  | 1.25 |  |  |  | Temp. | 11.5 | 10.9
[19 empty] | mg/L | 2.8617 | 0 |  | 1.9677 | 0 |  | 0.13552 | 1.1925 | 0 |  | pH | 7.5 | 7.77
5 | Present | 204927 | 421815 | 866000 | 157128 | 124676 | 0 | 651072300 | 5334.7 | 42891.4 | 37603.9 | 396.4 | 939.5 | 335 | 696.8 | 228.2 | 1.02 | 0.1 | inches | 0.5625 | 0 | 19.7972 | 6.375 | 0 | 14.025 | 3.125 | 9 | 0 | 9 | Turbidity | 1.48 | 0.048
| Total | 866000 | 0 |  | 0 | 0 |  | 990200 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 19.7972 | 0 |  | 14.025 | 0 |  | 0.78125 |  |  |  | Temp. | 12.3 | 12.9
[19 empty] | mg/L | 2.7411 | 0 |  | 1.9419 | 0 |  | 0.10817 | 1.2461 | 0 |  | pH | 7.51 | 7.55
6 | Present | 205875 | 421815 | 948000 | 157165 | 124676 | 37000 | 652014600 | 5346.2 | 42891.4 | 37603.9 | 396.5 | 939.5 | 335.1 | 696.8 | 228.3 | 0.99 | 0.07 | inches | 0.625 | 0 | 21.9969 | 6.875 | 0 | 15.125 | 2 | 10 | 0 | 10 | Turbidity | 1.37 | 0.049
| Total | 948000 | 0 |  | 37000 | 0 |  | 942300 | 11.5 | 0 | 0 | 0.1 | 0 | 0.1 | 0 | 0.1 |  |  | Lbs. | 21.9969 | 0 |  | 15.125 | 0 |  | 0.5 |  |  |  | Temp. | 12.5 | 13.8
[19 empty] | mg/L | 2.7822 | 0 |  | 1.913 | 0 |  | 0.063241 | 1.2648 | 0 |  | pH | 7.51 | 7.6
7 | Present | 206966 | 421815 | 1091000 | 157200 | 124676 | 35000 | 653120600 | 5359.5 | 42891.4 | 37603.9 | 396.7 | 939.5 | 335.1 | 696.8 | 228.4 | 1.09 | 0 | inches | 0.625 | 0 | 21.9969 | 7.875 | 0 | 17.325 | 2 | 12 | 0 | 12 | Turbidity | 1.25 | 0.048
| Total | 1091000 | 0 |  | 35000 | 0 |  | 1106000 | 13.3 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 21.9969 | 0 |  | 17.325 | 0 |  | 0.5 |  |  |  | Temp. | 11 | 13.6
[19 empty] | mg/L | 2.4175 | 0 |  | 1.9041 | 0 |  | 0.054951 | 1.3188 | 0 |  | pH | 7.57 | 7.75
8 | Present | 208200 | 421815 | 1234000 | 157200 | 124676 | 0 | 654389600 | 5374.8 | 42891.4 | 37603.9 | 396.7 | 939.5 | 335.1 | 696.8 | 228.4 | 1.05 | 0 | inches | 0.75 | 0 | 26.3963 | 9.25 | 0 | 20.35 | 2.25 | 13 | 0 | 13 | Turbidity | 1.34 | 0.049
| Total | 1234000 | 0 |  | 0 | 0 |  | 1269000 | 15.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 26.3963 | 0 |  | 20.35 | 0 |  | 0.5625 |  |  |  | Temp. | 13.3 | 13.8
[19 empty] | mg/L | 2.5648 | 0 |  | 1.9773 | 0 |  | 0.054656 | 1.2632 | 0 |  | pH | 7.58 | 7.72
9 | Present | 209460 | 421815 | 1260000 | 157236 | 124676 | 36000 | 655549000 | 5390.4 | 42891.4 | 37603.9 | 396.9 | 939.5 | 335.2 | 696.8 | 228.4 | 1.03 | 0 | inches | 0.75 | 0 | 26.3963 | 9.625 | 0 | 21.175 | 2.375 | 13 | 0 | 13 | Turbidity | 1.12 | 0.05
| Total | 1260000 | 0 |  | 36000 | 0 |  | 1159400 | 15.6 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 26.3963 | 0 |  | 21.175 | 0 |  | 0.59375 |  |  |  | Temp. | 14.1 | 14.9
[19 empty] | mg/L | 2.5119 | 0 |  | 2.0151 | 0 |  | 0.056502 | 1.2371 | 0 |  | pH | 7.62 | 7.77
10 | Present | 210550 | 421815 | 1090000 | 157272 | 124676 | 36000 | 656654000 | 5403.9 | 42891.4 | 37603.9 | 397.1 | 939.5 | 335.3 | 696.8 | 228.6 | 1.05 | 0 | inches | 0.625 | 0 | 21.9969 | 8.25 | 0 | 18.15 | 2.0625 | 9 | 0 | 9 | Turbidity | 1.21 | 0.033
| Total | 1090000 | 0 |  | 36000 | 0 |  | 1105000 | 13.5 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0.2 |  |  | Lbs. | 21.9969 | 0 |  | 18.15 | 0 |  | 0.51562 |  |  |  | Temp. | 14.2 | 14.6
[19 empty] | mg/L | 2.4197 | 0 |  | 1.9966 | 0 |  | 0.056721 | 0.99003 | 0 |  | pH | 7.57 | 7.74
11 | Present | 211148 | 421815 | 598000 | 157272 | 124676 | 0 | 657736200 | 5411.1 | 42891.4 | 37603.9 | 397.1 | 939.5 | 335.3 | 696.8 | 228.6 | 0.88 | 0.3 | inches | 0.5 | 0 | 17.5975 | 4 | 0 | 8.8 | 0.75 | 6 | 0 | 6 | Turbidity | 1.92 | 0.05
| Total | 598000 | 0 |  | 0 | 0 |  | 1082200 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 17.5975 | 0 |  | 8.8 | 0 |  | 0.1875 |  |  |  | Temp. | 15.9 | 15.3
[19 empty] | mg/L | 3.5284 | 0 |  | 1.7645 | 0 |  | 0.037595 | 1.2031 | 0 |  | pH | 7.55 | 7.86
12 | Present | 211148 | 423083 | 1268000 | 157272 | 124694 | 18000 | 658564300 | 5411.1 | 42907.4 | 37619.9 | 397.1 | 939.6 | 335.3 | 696.9 | 228.6 | 1.11 | 0.12 | inches | 0 | 5.875 | 30.8438 | 0 | 8 | 17.6 | 0.375 | 0 | 16 | 16 | Turbidity | 1.35 | 0.05
| Total | 0 | 1268000 |  | 0 | 18000 |  | 828100 | 0 | 16 | 16 | 0 | 0.1 | 0 | 0.1 | 0 |  |  | Lbs. | 0 | 30.8438 |  | 0 | 17.6 |  | 0.09375 |  |  |  | Temp. | 14.1 | 15.4
[19 empty] | mg/L | 0 | 2.9166 |  | 0 | 1.6643 |  | 0.0088651 | 0 | 1.513 |  | pH | 7.52 | 7.62
13 | Present | 211970 | 423234 | 973000 | 157308 | 124712 | 54000 | 659449900 | 5421.4 | 42909.3 | 37621.8 | 397.3 | 939.7 | 335.4 | 697 | 228.6 | 1.06 | 0.02 | inches | 0.5625 | 1 | 25.0472 | 6.25 | 0 | 13.75 | 0.375 | 14 | 2 | 16 | Turbidity | 1.43 | 0.046
| Total | 822000 | 151000 |  | 36000 | 18000 |  | 885600 | 10.3 | 1.9 | 1.9 | 0.2 | 0.1 | 0.1 | 0.1 | 0 |  |  | Lbs. | 19.7972 | 5.25 |  | 13.75 | 0 |  | 0.09375 |  |  |  | Temp. | 13 | 13.8
[19 empty] | mg/L | 2.8878 | 4.1689 |  | 2.0057 | 0 |  | 0.074444 | 2.0422 | 1.5881 |  | pH | 7.54 | 7.73
14 | Present | 213039 | 423234 | 1069000 | 157344 | 124712 | 36000 | 660380000 | 5434.3 | 42909.3 | 37621.8 | 397.4 | 939.7 | 335.4 | 697 | 228.7 | 1.06 | 0.19 | inches | 0.75 | 0 | 26.3963 | 8 | 0 | 17.6 | 2 | 11 | 0 | 11 | Turbidity | 1.28 | 0.048
| Total | 1069000 | 0 |  | 36000 | 0 |  | 930100 | 12.9 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 26.3963 | 0 |  | 17.6 | 0 |  | 0.5 |  |  |  | Temp. | 13.2 | 13.5
[19 empty] | mg/L | 2.9607 | 0 |  | 1.9741 | 0 |  | 0.056082 | 1.2338 | 0 |  | pH | 7.47 | 7.8
15 | Present | 213887 | 423243 | 857000 | 157344 | 124712 | 0 | 661425200 | 5444.9 | 42909.3 | 37621.8 | 397.4 | 939.7 | 335.5 | 697 | 228.7 | 1.04 | 0 | inches | 0.5625 | 0 | 19.7972 | 6.5 | 0 | 14.3 | 0.75 | 9 | 0 | 9 | Turbidity | 1.73 | 0.046
| Total | 848000 | 9000 |  | 0 | 0 |  | 1045200 | 10.6 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 19.7972 | 0 |  | 14.3 | 0 |  | 0.1875 |  |  |  | Temp. | 12.1 | 13
[19 empty] | mg/L | 2.7992 | 0 |  | 2.022 | 0 |  | 0.026512 | 1.2726 | 0 |  | pH | 7.5 | 7.76
16 | Present | 214861 | 423243 | 974000 | 157380 | 124712 | 36000 | 662309000 | 5456.8 | 42909.3 | 37621.8 | 397.6 | 939.7 | 335.5 | 697 | 228.8 | 0.97 | 0.11 | inches | 0.625 | 0 | 21.9969 | 5.625 | 0 | 12.375 | 1.25 | 11 | 0 | 11 | Turbidity | 1.29 | 0.045
| Total | 974000 | 0 |  | 36000 | 0 |  | 883800 | 11.9 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 21.9969 | 0 |  | 12.375 | 0 |  | 0.3125 |  |  |  | Temp. | 12.9 | 13.5
[19 empty] | mg/L | 2.7079 | 0 |  | 1.5234 | 0 |  | 0.03847 | 1.3542 | 0 |  | pH | 7.46 | 7.81
17 | Present | 215771 | 423243 | 910000 | 157380 | 124712 | 0 | 663178800 | 5468 | 42909.3 | 37621.8 | 397.6 | 939.7 | 335.5 | 697 | 228.9 | 1.03 | 0.38 | inches | 0.6875 | 0 | 24.1966 | 5.875 | 0 | 12.925 | 1.125 | 10 | 0 | 10 | Turbidity | 1.32 | 0.052
| Total | 910000 | 0 |  | 0 | 0 |  | 869800 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 24.1966 | 0 |  | 12.925 | 0 |  | 0.28125 |  |  |  | Temp. | 13.3 | 13.6
[19 empty] | mg/L | 3.1882 | 0 |  | 1.703 | 0 |  | 0.037058 | 1.3176 | 0 |  | pH | 7.62 | 7.84
18 | Present | 216510 | 423243 | 739000 | 157380 | 124712 | 0 | 664118200 | 5477 | 42909.3 | 37621.8 | 397.6 | 939.7 | 335.5 | 697 | 228.9 | 1.01 | 0.14 | inches | 0.625 | 0 | 21.9969 | 5.5 | 0 | 12.1 | 0 | 8 | 0 | 8 | Turbidity | 2.74 | 0.039
| Total | 739000 | 0 |  | 0 | 0 |  | 939400 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 21.9969 | 0 |  | 12.1 | 0 |  | 0 |  |  |  | Temp. | 13.1 | 13.5
[19 empty] | mg/L | 3.569 | 0 |  | 1.9632 | 0 |  | 0 | 1.298 | 0 |  | pH | 7.47 | 7.78
19 | Present | 217168 | 423243 | 658000 | 157416 | 124712 | 36000 | 665060600 | 5484.9 | 42909.3 | 37621.8 | 397.7 | 939.7 | 335.6 | 697 | 229 | 1.08 | 0.02 | inches | 0.625 | 0 | 21.9969 | 5.625 | 0 | 12.375 | 0 | 7 | 0 | 7 | Turbidity | 3.93 | 0.046
| Total | 658000 | 0 |  | 36000 | 0 |  | 942400 | 7.9 | 0 | 0 | 0.1 | 0 | 0.1 | 0 | 0.1 |  |  | Lbs. | 21.9969 | 0 |  | 12.375 | 0 |  | 0 |  |  |  | Temp. | 12.7 | 12.8
[19 empty] | mg/L | 4.0084 | 0 |  | 2.255 | 0 |  | 0 | 1.2756 | 0 |  | pH | 7.52 | 7.77
20 | Present | 217821 | 423847 | 1257000 | 157416 | 124747 | 35000 | 665957500 | 5493 | 42917.1 | 37629.6 | 397.7 | 940 | 335.6 | 697.2 | 229 | 1.02 | 0.07 | inches | 0.625 | 4.125 | 43.6531 | 5.25 | 4 | 20.35 | 0 | 8 | 8 | 16 | Turbidity | 2.87 | 0.077
| Total | 653000 | 604000 |  | 0 | 35000 |  | 896900 | 8.1 | 7.8 | 7.8 | 0 | 0.3 | 0 | 0.2 | 0 |  |  | Lbs. | 21.9969 | 21.6562 |  | 11.55 | 8.8 |  | 0 |  |  |  | Temp. | 12.2 | 14.2
[19 empty] | mg/L | 4.0391 | 4.2991 |  | 2.1208 | 1.7469 |  | 0 | 1.469 | 1.5881 |  | pH | 7.53 | 7.71
21 | Present | 218976 | 423847 | 1155000 | 157452 | 124747 | 36000 | 666893900 | 5506.9 | 42917.1 | 37629.6 | 397.9 | 940 | 335.6 | 697.2 | 229.1 | 1.06 | 0.12 | inches | 1.125 | 0 | 39.5944 | 8.5 | 0 | 18.7 | 0 | 12 | 0 | 12 | Turbidity | 3.49 | 0.053
| Total | 1155000 | 0 |  | 36000 | 0 |  | 936400 | 13.9 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 39.5944 | 0 |  | 18.7 | 0 |  | 0 |  |  |  | Temp. | 12.6 | 14
[19 empty] | mg/L | 4.1104 | 0 |  | 1.9413 | 0 |  | 0 | 1.2458 | 0 |  | pH | 7.57 | 7.66
22 | Present | 219646 | 423847 | 670000 | 157487 | 124747 | 35000 | 667809400 | 5515.1 | 42917.1 | 37629.6 | 398 | 940 | 335.7 | 697.2 | 229.1 | 1.04 | 0.04 | inches | 0.5 | 0 | 17.5975 | 4.75 | 0 | 10.45 | 0 | 7 | 0 | 7 | Turbidity | 3.3 | 0.049
| Total | 670000 | 0 |  | 35000 | 0 |  | 915500 | 8.2 | 0 | 0 | 0.1 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 17.5975 | 0 |  | 10.45 | 0 |  | 0 |  |  |  | Temp. | 11.7 | 13
[19 empty] | mg/L | 3.1493 | 0 |  | 1.8701 | 0 |  | 0 | 1.2527 | 0 |  | pH | 7.56 | 7.7
23 | Present | 220838 | 423847 | 1192000 | 157524 | 124747 | 37000 | 668851200 | 5529.7 | 42917.1 | 37629.6 | 398.2 | 940 | 335.8 | 697.2 | 229.2 | 0.99 | 0 | inches | 0.75 | 0 | 26.3963 | 8.875 | 0 | 19.525 | 0 | 14 | 0 | 14 | Turbidity | 2.1 | 0.032
| Total | 1192000 | 0 |  | 37000 | 0 |  | 1041800 | 14.6 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0.1 |  |  | Lbs. | 26.3963 | 0 |  | 19.525 | 0 |  | 0 |  |  |  | Temp. | 12 | 13.6
[19 empty] | mg/L | 2.6552 | 0 |  | 1.964 | 0 |  | 0 | 1.4083 | 0 |  | pH | 7.56 | 7.78
24 | Present | 221767 | 423847 | 929000 | 157524 | 124747 | 0 | 669874500 | 5541.3 | 42917.1 | 37629.6 | 398.2 | 940 | 335.8 | 697.2 | 229.2 | 1.02 | 0 | inches | 0.75 | 0 | 26.3963 | 7.25 | 0 | 15.95 | 0 | 11 | 0 | 11 | Turbidity | 1.8 | 0.034
| Total | 929000 | 0 |  | 0 | 0 |  | 1023300 | 11.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 26.3963 | 0 |  | 15.95 | 0 |  | 0 |  |  |  | Temp. | 14.1 | 14.9
[19 empty] | mg/L | 3.4069 | 0 |  | 2.0586 | 0 |  | 0 | 1.4197 | 0 |  | pH | 7.6 | 7.88
25 | Present | 222618 | 423847 | 851000 | 157524 | 124747 | 0 | 670808100 | 5551.8 | 42917.1 | 37629.6 | 398.2 | 940 | 335.8 | 697.2 | 229.3 | 1.03 | 0.02 | inches | 0.5 | 0 | 17.5975 | 6.5 | 0 | 14.3 | 0 | 10 | 0 | 10 | Turbidity | 1.73 | 0.031
| Total | 851000 | 0 |  | 0 | 0 |  | 933600 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 17.5975 | 0 |  | 14.3 | 0 |  | 0 |  |  |  | Temp. | 15.5 | 15
[19 empty] | mg/L | 2.4795 | 0 |  | 2.0148 | 0 |  | 0 | 1.409 | 0 |  | pH | 7.52 | 7.8
26 | Present | 222618 | 425216 | 1369000 | 157524 | 124782 | 35000 | 671892100 | 5551.8 | 42935.8 | 37648.3 | 398.2 | 940.3 | 335.8 | 697.4 | 229.3 | 1 | 0 | inches | 0 | 5.375 | 28.2188 | 0 | 6 | 13.2 | 0 | 0 | 16 | 16 | Turbidity | 1.67 | 0.051
| Total | 0 | 1369000 |  | 0 | 35000 |  | 1084000 | 0 | 18.7 | 18.7 | 0 | 0.3 | 0 | 0.2 | 0 |  |  | Lbs. | 0 | 28.2188 |  | 0 | 13.2 |  | 0 |  |  |  | Temp. | 13.6 | 13.9
[19 empty] | mg/L | 0 | 2.4715 |  | 0 | 1.1561 |  | 0 | 0 | 1.4014 |  | pH | 7.48 | 7.72
27 | Present | 223544 | 425554 | 1264000 | 157812 | 124782 | 288000 | 673191600 | 5563 | 42940.3 | 37652.8 | 399 | 940.3 | 335.9 | 697.4 | 229.4 | 1.08 | 0 | inches | 0.5 | 1.5 | 25.4725 | 6.875 | 2.5 | 20.625 | 0 | 11 | 3 | 14 | Turbidity | 1.64 | 0.061
| Total | 926000 | 338000 |  | 288000 | 0 |  | 1299500 | 11.2 | 4.5 | 4.5 | 0.8 | 0 | 0.1 | 0 | 0.1 |  |  | Lbs. | 17.5975 | 7.875 |  | 15.125 | 5.5 |  | 0 |  |  |  | Temp. | 13 | 13.6
[19 empty] | mg/L | 2.2786 | 2.7936 |  | 1.9585 | 1.9511 |  | 0 | 1.4243 | 1.0642 |  | pH | 7.54 | 7.76
28 | Present | 224807 | 425554 | 1263000 | 157848 | 124782 | 36000 | 674502200 | 5578.5 | 42940.3 | 37652.8 | 399.3 | 940.3 | 336 | 697.4 | 229.4 | 1.1 | 0 | inches | 0.5625 | 0 | 19.7972 | 9.5 | 0 | 20.9 | 0 | 14 | 0 | 14 | Turbidity | 1.98 | 0.032
| Total | 1263000 | 0 |  | 36000 | 0 |  | 1310600 | 15.5 | 0 | 0 | 0.3 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 19.7972 | 0 |  | 20.9 | 0 |  | 0 |  |  |  | Temp. | 14.3 | 14.8
[19 empty] | mg/L | 1.8795 | 0 |  | 1.9842 | 0 |  | 0 | 1.3291 | 0 |  | pH | 7.58 | 7.64
29 | Present | 226227 | 425554 | 1420000 | 157883 | 124782 | 35000 | 675827500 | 5596.1 | 42940.3 | 37652.8 | 399.3 | 940.3 | 336.1 | 697.4 | 229.6 | 1.01 | 0 | inches | 0.875 | 0 | 30.7956 | 11 | 0 | 24.2 | 0 | 17 | 0 | 17 | Turbidity | 1.69 | 0.034
| Total | 1420000 | 0 |  | 35000 | 0 |  | 1325300 | 17.6 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.2 |  |  | Lbs. | 30.7956 | 0 |  | 24.2 | 0 |  | 0 |  |  |  | Temp. | 15.2 | 15.8
[19 empty] | mg/L | 2.6004 | 0 |  | 2.0434 | 0 |  | 0 | 1.4355 | 0 |  | pH | 7.5 | 7.88
30 | Present | 227395 | 425554 | 1168000 | 157883 | 124782 | 0 | 676852900 | 5610.6 | 42940.3 | 37652.8 | 399.5 | 940.3 | 336.1 | 697.4 | 229.6 | 1.01 | 0 | inches | 0.625 | 0 | 21.9969 | 8.875 | 0 | 19.525 | 0 | 13 | 0 | 13 | Turbidity | 1.4 | 0.051
| Total | 1168000 | 0 |  | 0 | 0 |  | 1025400 | 14.5 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 |  |  | Lbs. | 21.9969 | 0 |  | 19.525 | 0 |  | 0 |  |  |  | Temp. | 16.5 | 16
[19 empty] | mg/L | 2.2581 | 0 |  | 2.0044 | 0 |  | 0 | 1.3345 | 0 |  | pH | 7.52 | 7.97
31 | Present | 228403 | 425554 | 1008000 | 157918 | 124782 | 35000 | 677808300 | 5623.1 | 42940.3 | 37652.8 | 399.7 | 940.3 | 336.2 | 697.4 | 229.6 | 1.05 | 0 | inches | 0.625 | 0 | 21.9969 | 7.75 | 0 | 17.05 | 0 | 12 | 0 | 12 | Turbidity | 1.48 | 0.042
| Total | 1008000 | 0 |  | 35000 | 0 |  | 955400 | 12.5 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 21.9969 | 0 |  | 17.05 | 0 |  | 0 |  |  |  | Temp. | 13.6 | 14.8
[19 empty] | mg/L | 2.6166 | 0 |  | 2.0281 | 0 |  | 0 | 1.4274 | 0 |  | pH | 7.59 | 7.9
| Total | 28254000 | 3739000 | 31993000 | 898000 | 106000 | 1004000 | 31595800 | 347.3 | 48.9 | 48.9 | 3.8 | 0.8 | 1.4 | 0.6 | 1.5 | N/A | 2.59 | Total Lbs. | 668.705 | 93.8438 | 762.5488 | 460.35 | 45.1 | 505.45 | 6.3594 |  | 45 | 351 | Avg Turb. | 1.7345 | 0.045161
| Average | 911419.3548 | 120612.9032 | 1032032.2581 | 28967.7419 | 3419.3548 | 32387.0968 | 1019219.3548 | 11.2032 | 1.5774 | 1.5774 | 0.12258 | 0.025806 | 0.045161 | 0.019355 | 0.048387 | 1.0281 | 0.083548 | Avg Lbs. | 21.5711 | 3.0272 | 24.5983 | 14.85 | 1.4548 | 16.3048 | 0.20514 | 0 | 1.4516 | 11.3226 | Avg. Temp. | 12.7065 | 13.3677
| High | 1420000 | 1369000 | 2588000 | 288000 | 35000 | 288000 | 1325300 | 17.6 | 18.7 | 18.7 | 0.8 | 0.3 | 0.1 | 0.2 | 0.2 | 1.11 | 0.6 | High Lbs. | 39.5944 | 30.8438 | 43.6531 | 24.2 | 17.6 | 24.2 | 1.25 | 17 | 16 | 17 | Avg pH | 7.2913 | 7.4997
| Low | 0 | 0 | 598000 | 0 | 0 | 0 | 792200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88 | 0 | Low Lbs. | 0 | 0 | 17.5975 | 0 | 0 | 8.8 | 0 | 0 | 0 | 6
[19 empty] | Avg mg/L | 2.7193 | 0.53709 |  | 1.8266 | 0.21027 |  | 0.02609 | 1.2173 | 0.2308 |  | High Turb. | 3.93 | 0.077
[19 empty] | High mg/L | 4.1104 | 4.2991 |  | 2.255 | 1.9511 |  | 0.13552 | 2.0422 | 1.5881 |  | High Temp. | 16.5 | 16
[19 empty] | Low mg/L | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 |  | High pH | 7.62 | 7.97
*Averages, Highs and Lows represent only days the plant was in operation
[30 empty] | Low Turb. | 0.89 | 0.031
[30 empty] | Low Temp. | 11 | 10.9
[30 empty] | Low pH | 7.44 | 7.55

## MayTotals
May, 2020
Combined Plant Daily Totals
Day | Gallons |  |  |  | Plant Hours | Rain Inches | Chemical Usage |  |  |  |  | Finished Water |  |  | Residual Chlorine
| Influent | Backwash | Flush | Totalizer |  |  | Value | ACH | SodaAsh | Polymer | NaOCl | Turbidity | pH | Temp
1 | 977000 | 36000 | 0 | 1046300 | 12.2 | 0.12 | Lbs. | 19.7972 | 15.4 | 0 | 8 | 0.049 | 7.65 | 13.1 | 1.11
[7 empty] | mg/L | 2.4296 | 1.89 | 0 | 0.98181
2 | 995000 | 0 | 0 | 1056800 | 12.3 | 0.6 | Lbs. | 21.9969 | 15.95 | 0 | 9 | 0.049 | 7.77 | 12.9 | 0.98
[7 empty] | mg/L | 2.6508 | 1.9221 | 0 | 1.0846
3 | 834000 | 36000 | 15000 | 792200 | 10.2 | 0.16 | Lbs. | 26.3963 | 13.2 | 0 | 7 | 0.061 | 7.77 | 11.9 | 0.95
[7 empty] | mg/L | 3.795 | 1.8978 | 0 | 1.0064
4 | 1106000 | 36000 | 0 | 974300 | 13.4 | 0.01 | Lbs. | 26.3963 | 18.15 | 1.25 | 11 | 0.046 | 7.77 | 10.9 | 0.95
[7 empty] | mg/L | 2.8617 | 1.9677 | 0.13552 | 1.1925
5 | 866000 | 0 | 0 | 990200 | 10.8 | 0.1 | Lbs. | 19.7972 | 14.025 | 0.78125 | 9 | 0.048 | 7.55 | 12.9 | 1.02
[7 empty] | mg/L | 2.7411 | 1.9419 | 0.10817 | 1.2461
6 | 948000 | 37000 | 15000 | 942300 | 11.5 | 0.07 | Lbs. | 21.9969 | 15.125 | 0.5 | 10 | 0.049 | 7.6 | 13.8 | 0.99
[7 empty] | mg/L | 2.7822 | 1.913 | 0.063241 | 1.2648
7 | 1091000 | 35000 | 15000 | 1106000 | 13.3 | 0 | Lbs. | 21.9969 | 17.325 | 0.5 | 12 | 0.048 | 7.75 | 13.6 | 1.09
[7 empty] | mg/L | 2.4175 | 1.9041 | 0.054951 | 1.3188
8 | 1234000 | 0 | 0 | 1269000 | 15.3 | 0 | Lbs. | 26.3963 | 20.35 | 0.5625 | 13 | 0.049 | 7.72 | 13.8 | 1.05
[7 empty] | mg/L | 2.5648 | 1.9773 | 0.054656 | 1.2632
9 | 1260000 | 36000 | 0 | 1159400 | 15.6 | 0 | Lbs. | 26.3963 | 21.175 | 0.59375 | 13 | 0.05 | 7.77 | 14.9 | 1.03
[7 empty] | mg/L | 2.5119 | 2.0151 | 0.056502 | 1.2371
10 | 1090000 | 36000 | 30000 | 1105000 | 13.5 | 0 | Lbs. | 21.9969 | 18.15 | 0.51562 | 9 | 0.033 | 7.74 | 14.6 | 1.05
[7 empty] | mg/L | 2.4197 | 1.9966 | 0.056721 | 0.99003
11 | 598000 | 0 | 0 | 1082200 | 7.2 | 0.3 | Lbs. | 17.5975 | 8.8 | 0.1875 | 6 | 0.05 | 7.86 | 15.3 | 0.88
[7 empty] | mg/L | 3.5284 | 1.7645 | 0.037595 | 1.2031
12 | 1268000 | 18000 | 0 | 828100 | 16 | 0.12 | Lbs. | 30.8438 | 17.6 | 0.09375 | 16 | 0.05 | 7.62 | 15.4 | 1.11
[7 empty] | mg/L | 1.4583 | 0.83214 | 0.0088651 | 0.75649
13 | 973000 | 54000 | 0 | 885600 | 12.2 | 0.02 | Lbs. | 25.0472 | 13.75 | 0.09375 | 16 | 0.046 | 7.73 | 13.8 | 1.06
[7 empty] | mg/L | 3.5283 | 2.0057 | 0.074444 | 1.8151
14 | 1069000 | 36000 | 15000 | 930100 | 12.9 | 0.19 | Lbs. | 26.3963 | 17.6 | 0.5 | 11 | 0.048 | 7.8 | 13.5 | 1.06
[7 empty] | mg/L | 2.9607 | 1.9741 | 0.056082 | 1.2338
15 | 857000 | 0 | 0 | 1045200 | 10.6 | 0 | Lbs. | 19.7972 | 14.3 | 0.1875 | 9 | 0.046 | 7.76 | 13 | 1.04
[7 empty] | mg/L | 2.7992 | 2.022 | 0.026512 | 1.2726
16 | 974000 | 36000 | 15000 | 883800 | 11.9 | 0.11 | Lbs. | 21.9969 | 12.375 | 0.3125 | 11 | 0.045 | 7.81 | 13.5 | 0.97
[7 empty] | mg/L | 2.7079 | 1.5234 | 0.03847 | 1.3542
17 | 910000 | 0 | 15000 | 869800 | 11.2 | 0.38 | Lbs. | 24.1966 | 12.925 | 0.28125 | 10 | 0.052 | 7.84 | 13.6 | 1.03
[7 empty] | mg/L | 3.1882 | 1.703 | 0.037058 | 1.3176
18 | 739000 | 0 | 0 | 939400 | 9 | 0.14 | Lbs. | 21.9969 | 12.1 | 0 | 8 | 0.039 | 7.78 | 13.5 | 1.01
[7 empty] | mg/L | 3.569 | 1.9632 | 0 | 1.298
19 | 658000 | 36000 | 15000 | 942400 | 7.9 | 0.02 | Lbs. | 21.9969 | 12.375 | 0 | 7 | 0.046 | 7.77 | 12.8 | 1.08
[7 empty] | mg/L | 4.0084 | 2.255 | 0 | 1.2756
20 | 1257000 | 35000 | 0 | 896900 | 15.9 | 0.07 | Lbs. | 43.6531 | 20.35 | 0 | 16 | 0.077 | 7.71 | 14.2 | 1.02
[7 empty] | mg/L | 4.1691 | 1.9339 | 0 | 1.5285
21 | 1155000 | 36000 | 15000 | 936400 | 13.9 | 0.12 | Lbs. | 39.5944 | 18.7 | 0 | 12 | 0.053 | 7.66 | 14 | 1.06
[7 empty] | mg/L | 4.1104 | 1.9413 | 0 | 1.2458
22 | 670000 | 35000 | 0 | 915500 | 8.2 | 0.04 | Lbs. | 17.5975 | 10.45 | 0 | 7 | 0.049 | 7.7 | 13 | 1.04
[7 empty] | mg/L | 3.1493 | 1.8701 | 0 | 1.2527
23 | 1192000 | 37000 | 15000 | 1041800 | 14.6 | 0 | Lbs. | 26.3963 | 19.525 | 0 | 14 | 0.032 | 7.78 | 13.6 | 0.99
[7 empty] | mg/L | 2.6552 | 1.964 | 0 | 1.4083
24 | 929000 | 0 | 0 | 1023300 | 11.6 | 0 | Lbs. | 26.3963 | 15.95 | 0 | 11 | 0.034 | 7.88 | 14.9 | 1.02
[7 empty] | mg/L | 3.4069 | 2.0586 | 0 | 1.4197
25 | 851000 | 0 | 15000 | 933600 | 10.5 | 0.02 | Lbs. | 17.5975 | 14.3 | 0 | 10 | 0.031 | 7.8 | 15 | 1.03
[7 empty] | mg/L | 2.4795 | 2.0148 | 0 | 1.409
26 | 1369000 | 35000 | 0 | 1084000 | 18.7 | 0 | Lbs. | 28.2188 | 13.2 | 0 | 16 | 0.051 | 7.72 | 13.9 | 1
[7 empty] | mg/L | 1.2358 | 0.57806 | 0 | 0.70068
27 | 1264000 | 288000 | 15000 | 1299500 | 15.7 | 0 | Lbs. | 25.4725 | 20.625 | 0 | 14 | 0.061 | 7.76 | 13.6 | 1.08
[7 empty] | mg/L | 2.5361 | 1.9548 | 0 | 1.2443
28 | 1263000 | 36000 | 0 | 1310600 | 15.5 | 0 | Lbs. | 19.7972 | 20.9 | 0 | 14 | 0.032 | 7.64 | 14.8 | 1.1
[7 empty] | mg/L | 1.8795 | 1.9842 | 0 | 1.3291
29 | 1420000 | 35000 | 30000 | 1325300 | 17.6 | 0 | Lbs. | 30.7956 | 24.2 | 0 | 17 | 0.034 | 7.88 | 15.8 | 1.01
[7 empty] | mg/L | 2.6004 | 2.0434 | 0 | 1.4355
30 | 1168000 | 0 | 0 | 1025400 | 14.5 | 0 | Lbs. | 21.9969 | 19.525 | 0 | 13 | 0.051 | 7.97 | 16 | 1.01
[7 empty] | mg/L | 2.2581 | 2.0044 | 0 | 1.3345
31 | 1008000 | 35000 | 0 | 955400 | 12.5 | 0 | Lbs. | 21.9969 | 17.05 | 0 | 12 | 0.042 | 7.9 | 14.8 | 1.05
[7 empty] | mg/L | 2.6166 | 2.0281 | 0 | 1.4274
Monthly Totals
| 31993000 | 1004000 | 225000 | 31595800 | 396.2 | 2.59 | Lbs. | 762.5487 | 505.45 | 6.3594 | 351 | N/A | N/A | N/A | N/A
[7 empty] | mg/L | N/A | N/A | N/A | N/A
Daily Averages
| 1032032.2581 | 32387.0968 | 7258.0645 | 1019219.3548 | 12.7806 | 0.083548 | Lbs. | 24.5983 | 16.3048 | 0.20514 | 11.3226 | 0.046806 | 7.7568 | 13.8839 | 1.0281
[7 empty] | mg/L | 2.8393 | 1.8659 | 0.02609 | 1.2531
Maximum Daily Totals
| 1420000 | 288000 | 30000 | 1325300 | 18.7 | 0.6 | Lbs. | 43.6531 | 24.2 | 1.25 | 17 | 0.077 | 7.97 | 16 | 1.11
[7 empty] | mg/L | 4.1691 | 2.255 | 0.13552 | 1.8151
Minimum Daily Totals
| 598000 | 0 | 0 | 792200 | 7.2 | 0 | Lbs. | 17.5975 | 8.8 | 0 | 6 | 0.031 | 7.55 | 10.9 | 0.88
[7 empty] | mg/L | 1.2358 | 0.57806 | 0 | 0.70068

## Jun
June, 2020
Day | Value | Influent | Influent 2 | Combined Inf | Backwash | Backwash 2 | Comb. BW | Totalizer | EP-1 | FE-1 | FE-2 | BWP-1 | BWP-2 | SWP-1 | SWP-2 | BL-1 | Residual | Rain | Value | ACH | ACH-2 | Comb Lbs. | SA | SA-2 | Comb Lbs. | Polymer | Chlorine | Chlorine2 | Comb. Cl2 | Value | Raw | Finished
1 | Present | 228403 | 426526 | 972000 | 157918 | 124818 | 36000 | 678978400 | 5623.1 | 42952.7 | 37665.2 | 399.7 | 940.6 | 336.2 | 697.6 | 229.6 | 1.03 | 0 | inches | 0 | 4.5 | 23.625 | 0 | 4.3 | 9.46 | 0 | 0 | 10 | 10 | Turbidity | 1.38 | 0.049
| Previous | 228403 | 425554 |  | 157918 | 124782 |  | 677808300 | 5623.1 | 42940.3 | 37652.8 | 399.7 | 940.3 | 336.2 | 697.4 | 229.6 |  |  | Lbs. | 0 | 23.625 |  | 0 | 9.46 |  | 0 |  |  |  | Temp. | 12.4 | 15.2
| Total | 0 | 972000 |  | 0 | 36000 |  | 1170100 | 0 | 12.4 | 12.4 | 0 | 0.3 | 0 | 0.2 | 0 |  |  | mg/L | 0 | 2.9143 |  | 0 | 1.167 |  | 0 | 0 | 1.2336 |  | pH | 7.53 | 7.85
2 | Present | 229424 | 426734 | 1229000 | 157918 | 124818 | 0 | 680219400 | 5635.5 | 42955.2 | 37667.7 | 399.7 | 940.6 | 336.2 | 697.6 | 229.7 | 1.02 | 0 | inches | 0.625 | 0.75 | 25.9344 | 9.125 | 1.125 | 22.55 | 0 | 11 | 2 | 13 | Turbidity | 1.45 | 0.049
| Total | 1021000 | 208000 |  | 0 | 0 |  | 1241000 | 12.4 | 2.5 | 2.5 | 0 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 21.9969 | 3.9375 |  | 20.075 | 2.475 |  | 0 |  |  |  | Temp. | 13.5 | 15.1
[19 empty] | mg/L | 2.5833 | 2.2698 |  | 2.3576 | 1.4267 |  | 0 | 1.2918 | 1.1529 |  | pH | 7.55 | 7.69
3 | Present | 230680 | 426734 | 1256000 | 157954 | 124818 | 36000 | 681482000 | 5651 | 42955.2 | 37667.7 | 399.9 | 940.6 | 336.3 | 697.6 | 229.9 | 1.03 | 0 | inches | 0.75 | 0 | 26.3963 | 9.75 | 0 | 21.45 | 0 | 16 | 0 | 16 | Turbidity | 1.43 | 0.039
| Total | 1256000 | 0 |  | 36000 | 0 |  | 1262600 | 15.5 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0.2 |  |  | Lbs. | 26.3963 | 0 |  | 21.45 | 0 |  | 0 |  |  |  | Temp. | 13.8 | 15
[19 empty] | mg/L | 2.5199 | 0 |  | 2.0477 | 0 |  | 0 | 1.5274 | 0 |  | pH | 7.54 | 7.73
4 | Present | 232175 | 426734 | 1495000 | 157990 | 124818 | 36000 | 682768700 | 5668.8 | 42955.2 | 37667.7 | 400 | 940.6 | 336.3 | 697.6 | 229.9 | 1.03 | 0 | inches | 0.75 | 0 | 26.3963 | 11.25 | 0 | 24.75 | 0 | 19 | 0 | 19 | Turbidity | 1.67 | 0.045
| Total | 1495000 | 0 |  | 36000 | 0 |  | 1286700 | 17.8 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 |  |  | Lbs. | 26.3963 | 0 |  | 24.75 | 0 |  | 0 |  |  |  | Temp. | 15.3 | 15.5
[19 empty] | mg/L | 2.1171 | 0 |  | 1.985 | 0 |  | 0 | 1.5239 | 0 |  | pH | 7.48 | 7.82
5 | Present | 233188 | 426734 | 1013000 | 157990 | 124818 | 0 | 683909400 | 5680.9 | 42955.2 | 37667.7 | 400.2 | 940.6 | 336.4 | 697.6 | 229.9 | 1.06 | 0 | inches | 0.5625 | 0 | 19.7972 | 7.5 | 0 | 16.5 | 0 | 11 | 0 | 11 | Turbidity | 1.44 | 0.038
| Total | 1013000 | 0 |  | 0 | 0 |  | 1140700 | 12.1 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 19.7972 | 0 |  | 16.5 | 0 |  | 0 |  |  |  | Temp. | 14.4 | 15.4
[19 empty] | mg/L | 2.3433 | 0 |  | 1.953 | 0 |  | 0 | 1.302 | 0 |  | pH | 7.62 | 7.73
6 | Present | 234334 | 426734 | 1146000 | 158025 | 124818 | 35000 | 685069000 | 5694.4 | 42955.2 | 37667.7 | 400.2 | 940.6 | 336.4 | 697.6 | 230 | 1.02 | 0.48 | inches | 0.625 | 0 | 21.9969 | 5.628 | 0 | 12.3816 | 0 | 13 | 0 | 13 | Turbidity | 1.41 | 0.038
| Total | 1146000 | 0 |  | 35000 | 0 |  | 1159600 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 21.9969 | 0 |  | 12.3816 | 0 |  | 0 |  |  |  | Temp. | 14.1 | 15.2
[19 empty] | mg/L | 2.3015 | 0 |  | 1.2955 | 0 |  | 0 | 1.3602 | 0 |  | pH | 7.63 | 7.92
7 | Present | 235145 | 426734 | 811000 | 158025 | 124818 | 0 | 685904000 | 5704.1 | 42955.2 | 37667.7 | 400.2 | 940.6 | 336.4 | 697.6 | 230 | 0.98 | 0.16 | inches | 0.5625 | 0 | 19.7972 | 5.125 | 0 | 11.275 | 0 | 9 |  | 9 | Turbidity | 2.13 | 0.052
| Total | 811000 | 0 |  | 0 | 0 |  | 835000 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 19.7972 | 0 |  | 11.275 | 0 |  | 0 |  |  |  | Temp. | 13 | 14.3
[19 empty] | mg/L | 2.927 | 0 |  | 1.667 | 0 |  | 0 | 1.3306 | 0 |  | pH | 7.55 | 7.86
8 | Present | 235680 | 427204 | 1005000 | 158061 | 124854 | 72000 | 686865000 | 5710.4 | 42961.1 | 37673.6 | 400.4 | 940.8 | 336.5 | 697.8 | 230 | 0.99 | 0.3 | inches | 0.375 | 2.625 | 26.9794 | 4.25 | 1.25 | 12.1 | 1 | 7 | 6 | 13 | Turbidity | 2.32 | 0.045
| Total | 535000 | 470000 |  | 36000 | 36000 |  | 961000 | 6.3 | 5.9 | 5.9 | 0.2 | 0.2 | 0.1 | 0.2 | 0 |  |  | Lbs. | 13.1981 | 13.7812 |  | 9.35 | 2.75 |  | 0.25 |  |  |  | Temp. | 13 | 13.6
[19 empty] | mg/L | 2.958 | 3.5158 |  | 2.0955 | 0.70157 |  | 0.05603 | 1.5688 | 1.5307 |  | pH | 7.48 | 7.8
9 | Present | 236971 | 427204 | 1291000 | 158097 | 124854 | 36000 | 687888200 | 5725.3 | 42961.1 | 37673.6 | 400.5 | 940.8 | 336.5 | 697.8 | 230 | 0.99 | 0.15 | inches | 1 | 0 | 35.195 | 6.5 | 0 | 14.3 | 4.875 | 21 | 0 | 21 | Turbidity | 1.82 | 0.04
| Total | 1291000 | 0 |  | 36000 | 0 |  | 1023200 | 14.9 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 |  |  | Lbs. | 35.195 | 0 |  | 14.3 | 0 |  | 1.2188 |  |  |  | Temp. | 12.7 | 13.9
[19 empty] | mg/L | 3.2688 | 0 |  | 1.3281 | 0 |  | 0.11319 | 1.9504 | 0 |  | pH | 7.51 | 7.84
10 | Present | 238005 | 427204 | 1034000 | 158097 | 124854 | 0 | 688978300 | 5737.5 | 42961.1 | 37673.6 | 400.5 | 940.8 | 336.5 | 697.8 | 230.1 | 1.08 | 0.01 | inches | 0.875 | 0 | 30.7956 | 7.9375 | 0 | 17.4625 | 4 | 13 | 0 | 13 | Turbidity | 2.54 | 0.036
| Total | 1034000 | 0 |  | 0 | 0 |  | 1090100 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 30.7956 | 0 |  | 17.4625 | 0 |  | 1 |  |  |  | Temp. | 13.7 | 14.3
[19 empty] | mg/L | 3.5711 | 0 |  | 2.025 | 0 |  | 0.11596 | 1.5075 | 0 |  | pH | 7.42 | 7.88
11 | Present | 238986 | 427204 | 981000 | 158132 | 124854 | 35000 | 690031500 | 5749 | 42961.1 | 37673.6 | 400.6 | 940.8 | 336.6 | 697.8 | 230.1 | 1.05 | 0.04 | inches | 0.625 | 0 | 21.9969 | 7.125 | 0 | 15.675 | 3.875 | 13 | 0 | 13 | Turbidity | 1.98 | 0.032
| Total | 981000 | 0 |  | 35000 | 0 |  | 1053200 | 11.5 | 0 | 0 | 0.1 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 21.9969 | 0 |  | 15.675 | 0 |  | 0.96875 |  |  |  | Temp. | 14.8 | 15.7
[19 empty] | mg/L | 2.6886 | 0 |  | 1.9159 | 0 |  | 0.11841 | 1.5889 | 0 |  | pH | 7.49 | 7.72
12 | Present | 239972 | 427204 | 986000 | 158168 | 124854 | 36000 | 691003900 | 5760.6 | 42961.1 | 37673.6 | 400.8 | 940.8 | 336.7 | 697.8 | 230.2 | 1.07 | 0.11 | inches | 0.625 | 0 | 21.9969 | 7.125 | 0 | 15.675 | 3.875 | 12 | 0 | 12 | Turbidity | 1.84 | 0.032
| Total | 986000 | 0 |  | 36000 | 0 |  | 972400 | 11.6 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0.1 |  |  | Lbs. | 21.9969 | 0 |  | 15.675 | 0 |  | 0.96875 |  |  |  | Temp. | 14.9 | 15.7
[19 empty] | mg/L | 2.675 | 0 |  | 1.9062 | 0 |  | 0.11781 | 1.4593 | 0 |  | pH | 7.46 | 7.8
13 | Present | 240727 | 427204 | 755000 | 158239 | 124854 | 71000 | 691880300 | 5769 | 42961.1 | 37673.6 | 401.1 | 940.8 | 336.8 | 697.8 | 230.3 | 1.12 | 0.35 | inches | 0.5625 | 0 | 19.7972 | 5.1875 | 0 | 11.4125 | 3 | 9 | 0 | 9 | Turbidity | 1.73 | 0.046
| Total | 755000 | 0 |  | 71000 | 0 |  | 876400 | 8.4 | 0 | 0 | 0.3 | 0 | 0.1 | 0 | 0.1 |  |  | Lbs. | 19.7972 | 0 |  | 11.4125 | 0 |  | 0.75 |  |  |  | Temp. | 13.3 | 14.5
[19 empty] | mg/L | 3.1441 | 0 |  | 1.8125 | 0 |  | 0.11911 | 1.4293 | 0 |  | pH | 7.48 | 7.82
14 | Present | 241962 | 427204 | 1235000 | 158239 | 124854 | 0 | 693031500 | 5784.3 | 42961.1 | 37673.6 | 401.2 | 940.8 | 336.9 | 697.8 | 230.4 | 1.06 | 0.13 | inches | 1.75 | 0 | 61.5913 | 9.875 | 0 | 21.725 | 5 | 15 | 0 | 15 | Turbidity | 7.82 | 0.044
| Total | 1235000 | 0 |  | 0 | 0 |  | 1151200 | 15.3 | 0 | 0 | 0.1 | 0 | 0.1 | 0 | 0.1 |  |  | Lbs. | 61.5913 | 0 |  | 21.725 | 0 |  | 1.25 |  |  |  | Temp. | 14.8 | 14.7
[19 empty] | mg/L | 5.9798 | 0 |  | 2.1092 | 0 |  | 0.12136 | 1.4563 | 0 |  | pH | 7.48 | 7.63
15 | Present | 243111 | 427204 | 1149000 | 158275 | 124854 | 36000 | 694031300 | 5798.1 | 42961.1 | 37673.6 | 401.3 | 940.8 | 336.9 | 697.8 | 230.5 | 1.05 | 0.38 | inches | 1.1875 | 0 | 41.7941 | 8.875 | 0 | 19.525 | 1.75 | 13 | 0 | 13 | Turbidity | 3.02 | 0.054
| Total | 1149000 | 0 |  | 36000 | 0 |  | 999800 | 13.8 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 41.7941 | 0 |  | 19.525 | 0 |  | 0.4375 |  |  |  | Temp. | 12.6 | 13.9
[19 empty] | mg/L | 4.3614 | 0 |  | 2.0375 | 0 |  | 0.045655 | 1.3566 | 0 |  | pH | 7.49 | 7.88
16 | Present | 243825 | 427393 | 903000 | 158311 | 124854 | 36000 | 695015600 | 5806.8 | 42964.1 | 37676.6 | 401.5 | 940.9 | 337 | 697.8 | 230.5 | 1.03 | 0.01 | inches | 0.6875 | 1.125 | 30.1028 | 5.625 | 0.875 | 14.3 | 1.875 | 8 | 3 | 11 | Turbidity | 5.36 | 0.033
| Total | 714000 | 189000 |  | 36000 | 0 |  | 984300 | 8.7 | 3 | 3 | 0.2 | 0.1 | 0.1 | 0 | 0 |  |  | Lbs. | 24.1966 | 5.9062 |  | 12.375 | 1.925 |  | 0.46875 |  |  |  | Temp. | 12.3 | 13
[19 empty] | mg/L | 4.0634 | 3.747 |  | 2.0782 | 1.2212 |  | 0.078719 | 1.3435 | 1.9032 |  | pH | 7.4 | 7.6
17 | Present | 244925 | 427393 | 1100000 | 158311 | 124854 | 0 | 696077400 | 5820.3 | 42964.1 | 37676.6 | 401.5 | 940.9 | 337 | 697.8 | 230.6 | 1.01 | 0 | inches | 0.75 | 0 | 26.3963 | 8.625 | 0 | 18.975 | 2.375 | 13 | 0 | 13 | Turbidity | 2.49 | 0.037
| Total | 1100000 | 0 |  | 0 | 0 |  | 1061800 | 13.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 26.3963 | 0 |  | 18.975 | 0 |  | 0.59375 |  |  |  | Temp. | 12.8 | 14.6
[19 empty] | mg/L | 2.8773 | 0 |  | 2.0683 | 0 |  | 0.064721 | 1.417 | 0 |  | pH | 7.47 | 7.7
18 | Present | 246138 | 427393 | 1213000 | 158346 | 124854 | 35000 | 697164300 | 5835.3 | 42964.1 | 37676.6 | 401.7 | 940.9 | 337.1 | 697.8 | 230.7 | 1.1 | 0 | inches | 0.75 | 0 | 26.3963 | 7.5 | 0 | 16.5 | 2.1875 | 13 | 0 | 13 | Turbidity | 1.81 | 0.036
| Total | 1213000 | 0 |  | 35000 | 0 |  | 1086900 | 15 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0.1 |  |  | Lbs. | 26.3963 | 0 |  | 16.5 | 0 |  | 0.54688 |  |  |  | Temp. | 12.5 | 13.4
[19 empty] | mg/L | 2.6092 | 0 |  | 1.631 | 0 |  | 0.054058 | 1.285 | 0 |  | pH | 7.49 | 7.81
19 | Present | 247410 | 427393 | 1272000 | 158382 | 124854 | 36000 | 698602900 | 5850.9 | 42964.1 | 37676.6 | 401.9 | 940.9 | 337.2 | 697.8 | 230.8 | 1.06 | 0.18 | inches | 0.6875 | 0 | 24.1966 | 10 | 0 | 22 | 2.625 | 13 | 0 | 13 | Turbidity | 1.78 | 0.035
| Total | 1272000 | 0 |  | 36000 | 0 |  | 1438600 | 15.6 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0.1 |  |  | Lbs. | 24.1966 | 0 |  | 22 | 0 |  | 0.65625 |  |  |  | Temp. | 13.2 | 14.1
[19 empty] | mg/L | 2.2809 | 0 |  | 2.0738 | 0 |  | 0.061861 | 1.2254 | 0 |  | pH | 7.46 | 7.82
20 | Present | 248492 | 427393 | 1082000 | 158382 | 124854 | 0 | 699538700 | 5864.5 | 42964.1 | 37676.6 | 401.9 | 940.9 | 337.2 | 697.8 | 230.8 | 1.03 | 0.18 | inches | 0.5625 | 0 | 19.7972 | 8.625 | 0 | 18.975 | 2.3125 | 11 | 0 | 11 | Turbidity | 1.83 | 0.039
| Total | 1082000 | 0 |  | 0 | 0 |  | 935800 | 13.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 19.7972 | 0 |  | 18.975 | 0 |  | 0.57812 |  |  |  | Temp. | 14.3 | 15.2
[19 empty] | mg/L | 2.1939 | 0 |  | 2.1028 | 0 |  | 0.064066 | 1.219 | 0 |  | pH | 7.59 | 7.97
21 | Present | 249567 | 427393 | 1075000 | 158417 | 124854 | 35000 | 700592300 | 5877.6 | 42964.1 | 37676.6 | 402 | 940.9 | 337.2 | 697.8 | 230.9 | 1.05 | 0 | inches | 0.625 | 0 | 21.9969 | 8.375 | 0 | 18.425 | 2.25 | 11 | 0 | 11 | Turbidity | 1.74 | 0.037
| Total | 1075000 | 0 |  | 35000 | 0 |  | 1053600 | 13.1 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 21.9969 | 0 |  | 18.425 | 0 |  | 0.5625 |  |  |  | Temp. | 14.3 | 14.9
[19 empty] | mg/L | 2.4535 | 0 |  | 2.0551 | 0 |  | 0.062741 | 1.2269 | 0 |  | pH | 7.65 | 7.94
22 | Present | 250648 | 427393 | 1081000 | 158453 | 124854 | 36000 | 701958200 | 5890.3 | 42964.1 | 37676.6 | 402.1 | 940.9 | 337.3 | 697.8 | 230.9 | 0.99 | 0 | inches | 0.625 | 0 | 21.9969 | 8.25 | 0 | 18.15 | 0.25 | 11 | 0 | 11 | Turbidity | 1.71 | 0.036
| Total | 1081000 | 0 |  | 36000 | 0 |  | 1365900 | 12.7 | 0 | 0 | 0.1 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 21.9969 | 0 |  | 18.15 | 0 |  | 0.0625 |  |  |  | Temp. | 14.3 | 14.1
[19 empty] | mg/L | 2.4399 | 0 |  | 2.0132 | 0 |  | 0.0069325 | 1.2201 | 0 |  | pH | 7.49 | 7.91
23 | Present | 251364 | 428401 | 1724000 | 158453 | 124889 | 35000 | 703369800 | 5898.7 | 42977.2 | 37689.7 | 402.1 | 941.1 | 337.3 | 698 | 231 | 1.03 | 0 | inches | 0.5 | 3.75 | 37.285 | 5.25 | 3.875 | 20.075 | 1 | 8 | 13 | 21 | Turbidity | 2.56 | 0.042
| Total | 716000 | 1008000 |  | 0 | 35000 |  | 1411600 | 8.4 | 13.1 | 13.1 | 0 | 0.2 | 0 | 0.2 | 0.1 |  |  | Lbs. | 17.5975 | 19.6875 |  | 11.55 | 8.525 |  | 0.25 |  |  |  | Temp. | 15.5 | 15.4
[19 empty] | mg/L | 2.9469 | 2.3419 |  | 1.9342 | 1.0141 |  | 0.041866 | 1.3397 | 1.5464 |  | pH | 7.38 | 7.7
24 | Present | 252621 | 428401 | 1257000 | 158488 | 124889 | 35000 | 704693900 | 5913.8 | 42977.2 | 37689.7 | 402.3 | 941.1 | 337.3 | 698 | 231 | 1.09 | 0 | inches | 0.75 | 0 | 26.3963 | 9.875 | 0 | 21.725 | 3 | 13 | 0 | 13 | Turbidity | 1.59 | 0.044
| Total | 1257000 | 0 |  | 35000 | 0 |  | 1324100 | 15.1 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 |  |  | Lbs. | 26.3963 | 0 |  | 21.725 | 0 |  | 0.75 |  |  |  | Temp. | 16.6 | 16.3
[19 empty] | mg/L | 2.5179 | 0 |  | 2.0723 | 0 |  | 0.071542 | 1.2401 | 0 |  | pH | 7.44 | 7.77
25 | Present | 254163 | 428401 | 1542000 | 158524 | 124889 | 36000 | 706091700 | 5932.3 | 42977.2 | 37689.7 | 402.5 | 941.1 | 337.4 | 698 | 231.1 | 1.05 | 0 | inches | 0.9375 | 0 | 32.9953 | 11.75 | 0 | 25.85 | 3.5 | 17 | 0 | 17 | Turbidity | 1.17 | 0.027
| Total | 1542000 | 0 |  | 36000 | 0 |  | 1397800 | 18.5 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0.1 |  |  | Lbs. | 32.9953 | 0 |  | 25.85 | 0 |  | 0.875 |  |  |  | Temp. | 16.1 | 17.3
[19 empty] | mg/L | 2.5657 | 0 |  | 2.0101 | 0 |  | 0.068039 | 1.3219 | 0 |  | pH | 7.41 | 7.67
26 | Present | 255350 | 428401 | 1187000 | 158524 | 124889 | 0 | 707442100 | 5946.4 | 42977.2 | 37689.7 | 402.5 | 941.1 | 337.4 | 698 | 231.1 | 1.03 | 0 | inches | 0.75 | 0 | 26.3963 | 9.125 | 0 | 20.075 | 2.25 | 15 | 0 | 15 | Turbidity | 1.36 | 0.03
| Total | 1187000 | 0 |  | 0 | 0 |  | 1350400 | 14.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Lbs. | 26.3963 | 0 |  | 20.075 | 0 |  | 0.5625 |  |  |  | Temp. | 17 | 17.9
[19 empty] | mg/L | 2.6664 | 0 |  | 2.0279 | 0 |  | 0.056821 | 1.5152 | 0 |  | pH | 7.4 | 7.69
27 | Present | 256701 | 428401 | 1351000 | 158560 | 124889 | 36000 | 708766100 | 5962.5 | 42977.2 | 37689.7 | 402.6 | 941.1 | 337.5 | 698 | 231.2 | 1.07 | 0 | inches | 0.75 | 0 | 26.3963 | 9.9375 | 0 | 21.8625 | 3.125 | 16 | 0 | 16 | Turbidity | 1.34 | 0.023
| Total | 1351000 | 0 |  | 36000 | 0 |  | 1324000 | 16.1 | 0 | 0 | 0.1 | 0 | 0.1 | 0 | 0.1 |  |  | Lbs. | 26.3963 | 0 |  | 21.8625 | 0 |  | 0.78125 |  |  |  | Temp. | 16.8 | 17.7
[19 empty] | mg/L | 2.3427 | 0 |  | 1.9403 | 0 |  | 0.069338 | 1.42 | 0 |  | pH | 7.41 | 7.99
28 | Present | 257784 | 428401 | 1083000 | 158595 | 124889 | 35000 | 709727400 | 5975.3 | 42977.2 | 37689.7 | 402.9 | 941.1 | 337.6 | 698 | 231.3 | 1.12 | 0.02 | inches | 0.75 | 0 | 26.3963 | 8 | 0 | 17.6 | 2.375 | 12 | 0 | 12 | Turbidity | 1.1 | 0.024
| Total | 1083000 | 0 |  | 35000 | 0 |  | 961300 | 12.8 | 0 | 0 | 0.3 | 0 | 0.1 | 0 | 0.1 |  |  | Lbs. | 26.3963 | 0 |  | 17.6 | 0 |  | 0.59375 |  |  |  | Temp. | 15.7 | 16.6
[19 empty] | mg/L | 2.9225 | 0 |  | 1.9486 | 0 |  | 0.065737 | 1.3286 | 0 |  | pH | 7.49 | 7.95
29 | Present | 258809 | 428724 | 1348000 | 158639 | 124889 | 44000 | 711225300 | 5987.7 | 42981.5 | 37694 | 403 | 941.1 | 337.6 | 698.1 | 231.3 | 1.07 | 0 | inches | 0.625 | 1.375 | 29.2156 | 8 | 1.25 | 20.35 | 2.625 | 12 | 3 | 15 | Turbidity | 1.82 | 0.037
| Total | 1025000 | 323000 |  | 44000 | 0 |  | 1497900 | 12.4 | 4.3 | 4.3 | 0.1 | 0 | 0 | 0.1 | 0 |  |  | Lbs. | 21.9969 | 7.2188 |  | 17.6 | 2.75 |  | 0.65625 |  |  |  | Temp. | 14.5 | 16.2
[19 empty] | mg/L | 2.5732 | 2.6797 |  | 2.0588 | 1.0209 |  | 0.076768 | 1.4038 | 1.1137 |  | pH | 7.59 | 7.95
30 | Present | 260111 | 428724 | 1302000 | 158686 | 124889 | 47000 | 712514200 | 6003.2 | 42981.5 | 37694 | 403.1 | 941.1 | 337.7 | 698.1 | 231.4 | 1.02 | 0 | inches | 0.75 | 0 | 26.3963 | 9.875 | 0 | 21.725 | 3 | 15 | 0 | 15 | Turbidity | 1.13 | 0.025
| Total | 1302000 | 0 |  | 47000 | 0 |  | 1288900 | 15.5 | 0 | 0 | 0.1 | 0 | 0.1 | 0 | 0.1 |  |  | Lbs. | 26.3963 | 0 |  | 21.725 | 0 |  | 0.75 |  |  |  | Temp. | 15.4 | 16.2
[19 empty] | mg/L | 2.4309 | 0 |  | 2.0007 | 0 |  | 0.069069 | 1.3814 | 0 |  | pH | 7.49 | 7.83
| Total | 31708000 | 3170000 | 34878000 | 768000 | 107000 | 875000 | 34705900 | 380.1 | 41.2 | 41.2 | 3.4 | 0.8 | 1.5 | 0.7 | 1.8 | N/A | 2.5 | Total Lbs. | 752.2931 | 74.1562 | 826.4494 | 514.9441 | 27.885 | 542.8291 | 15.5312 | 370 | 37 | 407 | Avg Turb. | 2.0923 | 0.038133
| Average | 1056933.3333 | 105666.6667 | 1162600 | 25600 | 3566.6667 | 29166.6667 | 1156863.3333 | 12.67 | 1.3733 | 1.3733 | 0.11333 | 0.026667 | 0.05 | 0.023333 | 0.06 | 1.0443 | 0.083333 | Avg Lbs. | 25.0764 | 2.4719 | 27.5483 | 17.1648 | 0.9295 | 18.0943 | 0.51771 | 12.3333 | 1.2333 | 13.5667 | Avg. Temp. | 14.2533 | 15.1633
| High | 1542000 | 972000 | 1724000 | 71000 | 36000 | 72000 | 1497900 | 18.5 | 13.1 | 13.1 | 0.3 | 0.3 | 0.1 | 0.2 | 0.2 | 1.12 | 0.48 | High Lbs. | 61.5913 | 23.625 | 61.5913 | 25.85 | 9.46 | 25.85 | 1.25 | 21 | 13 | 21 | Avg pH | 7.4957 | 7.809
| Low | 0 | 972000 | 755000 | 0 | 36000 | 0 | 835000 | 0 | 12.4 | 12.4 | 0 | 0.3 | 0 | 0.2 | 0 | 0.98 | 0 | Low Lbs. | 0 | 0 | 19.7972 | 0 | 0 | 9.46 | 0 | 0 | 0 | 9
[19 empty] | Avg mg/L | 2.7774 | 0.58229 |  | 1.885 | 0.21838 |  | 0.057327 | 1.3514 | 0.28268 |  | High Turb. | 7.82 | 0.054
[19 empty] | High mg/L | 5.9798 | 3.747 |  | 2.3576 | 1.4267 |  | 0.12136 | 1.9504 | 1.9032 |  | High Temp. | 17 | 17.9
[19 empty] | Low mg/L | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 |  | High pH | 7.65 | 7.99
*Averages, Highs and Lows represent only days the plant was in operation
[30 empty] | Low Turb. | 1.1 | 0.023
[30 empty] | Low Temp. | 12.3 | 13
[30 empty] | Low pH | 7.38 | 7.6

## JunTotals
June, 2020
Combined Plant Daily Totals
Day | Gallons |  |  |  | Plant Hours | Rain Inches | Chemical Usage |  |  |  |  | Finished Water |  |  | Residual Chlorine
| Influent | Backwash | Flush | Totalizer |  |  | Value | ACH | SodaAsh | Polymer | NaOCl | Turbidity | pH | Temp
1 | 972000 | 36000 | 0 | 1170100 | 12.4 | 0 | Lbs. | 23.625 | 9.46 | 0 | 10 | 0.049 | 7.85 | 15.2 | 1.03
[7 empty] | mg/L | 1.4572 | 0.58348 | 0 | 0.61679
2 | 1229000 | 0 | 15000 | 1241000 | 14.9 | 0 | Lbs. | 25.9344 | 22.55 | 0 | 13 | 0.049 | 7.69 | 15.1 | 1.02
[7 empty] | mg/L | 2.4265 | 1.8922 | 0 | 1.2224
3 | 1256000 | 36000 | 30000 | 1262600 | 15.5 | 0 | Lbs. | 26.3963 | 21.45 | 0 | 16 | 0.039 | 7.73 | 15 | 1.03
[7 empty] | mg/L | 2.5199 | 2.0477 | 0 | 1.5274
4 | 1495000 | 36000 | 0 | 1286700 | 17.8 | 0 | Lbs. | 26.3963 | 24.75 | 0 | 19 | 0.045 | 7.82 | 15.5 | 1.03
[7 empty] | mg/L | 2.1171 | 1.985 | 0 | 1.5239
5 | 1013000 | 0 | 0 | 1140700 | 12.1 | 0 | Lbs. | 19.7972 | 16.5 | 0 | 11 | 0.038 | 7.73 | 15.4 | 1.06
[7 empty] | mg/L | 2.3433 | 1.953 | 0 | 1.302
6 | 1146000 | 35000 | 15000 | 1159600 | 13.5 | 0.48 | Lbs. | 21.9969 | 12.3816 | 0 | 13 | 0.038 | 7.92 | 15.2 | 1.02
[7 empty] | mg/L | 2.3015 | 1.2955 | 0 | 1.3602
7 | 811000 | 0 | 0 | 835000 | 9.7 | 0.16 | Lbs. | 19.7972 | 11.275 | 0 | 9 | 0.052 | 7.86 | 14.3 | 0.98
[7 empty] | mg/L | 2.927 | 1.667 | 0 | 1.3306
8 | 1005000 | 72000 | 0 | 961000 | 12.2 | 0.3 | Lbs. | 26.9794 | 12.1 | 0.25 | 13 | 0.045 | 7.8 | 13.6 | 0.99
[7 empty] | mg/L | 3.2369 | 1.3985 | 0.05603 | 1.5498
9 | 1291000 | 36000 | 0 | 1023200 | 14.9 | 0.15 | Lbs. | 35.195 | 14.3 | 1.2188 | 21 | 0.04 | 7.84 | 13.9 | 0.99
[7 empty] | mg/L | 3.2688 | 1.3281 | 0.11319 | 1.9504
10 | 1034000 | 0 | 15000 | 1090100 | 12.2 | 0.01 | Lbs. | 30.7956 | 17.4625 | 1 | 13 | 0.036 | 7.88 | 14.3 | 1.08
[7 empty] | mg/L | 3.5711 | 2.025 | 0.11596 | 1.5075
11 | 981000 | 35000 | 0 | 1053200 | 11.5 | 0.04 | Lbs. | 21.9969 | 15.675 | 0.96875 | 13 | 0.032 | 7.72 | 15.7 | 1.05
[7 empty] | mg/L | 2.6886 | 1.9159 | 0.11841 | 1.5889
12 | 986000 | 36000 | 15000 | 972400 | 11.6 | 0.11 | Lbs. | 21.9969 | 15.675 | 0.96875 | 12 | 0.032 | 7.8 | 15.7 | 1.07
[7 empty] | mg/L | 2.675 | 1.9062 | 0.11781 | 1.4593
13 | 755000 | 71000 | 15000 | 876400 | 8.4 | 0.35 | Lbs. | 19.7972 | 11.4125 | 0.75 | 9 | 0.046 | 7.82 | 14.5 | 1.12
[7 empty] | mg/L | 3.1441 | 1.8125 | 0.11911 | 1.4293
14 | 1235000 | 0 | 15000 | 1151200 | 15.3 | 0.13 | Lbs. | 61.5913 | 21.725 | 1.25 | 15 | 0.044 | 7.63 | 14.7 | 1.06
[7 empty] | mg/L | 5.9798 | 2.1092 | 0.12136 | 1.4563
15 | 1149000 | 36000 | 15000 | 999800 | 13.8 | 0.38 | Lbs. | 41.7941 | 19.525 | 0.4375 | 13 | 0.054 | 7.88 | 13.9 | 1.05
[7 empty] | mg/L | 4.3614 | 2.0375 | 0.045655 | 1.3566
16 | 903000 | 36000 | 0 | 984300 | 11.7 | 0.01 | Lbs. | 30.1028 | 14.3 | 0.46875 | 11 | 0.033 | 7.6 | 13 | 1.03
[7 empty] | mg/L | 3.9052 | 1.6497 | 0.078719 | 1.6234
17 | 1100000 | 0 | 15000 | 1061800 | 13.5 | 0 | Lbs. | 26.3963 | 18.975 | 0.59375 | 13 | 0.037 | 7.7 | 14.6 | 1.01
[7 empty] | mg/L | 2.8773 | 2.0683 | 0.064721 | 1.417
18 | 1213000 | 35000 | 15000 | 1086900 | 15 | 0 | Lbs. | 26.3963 | 16.5 | 0.54688 | 13 | 0.036 | 7.81 | 13.4 | 1.1
[7 empty] | mg/L | 2.6092 | 1.631 | 0.054058 | 1.285
19 | 1272000 | 36000 | 15000 | 1438600 | 15.6 | 0.18 | Lbs. | 24.1966 | 22 | 0.65625 | 13 | 0.035 | 7.82 | 14.1 | 1.06
[7 empty] | mg/L | 2.2809 | 2.0738 | 0.061861 | 1.2254
20 | 1082000 | 0 | 0 | 935800 | 13.6 | 0.18 | Lbs. | 19.7972 | 18.975 | 0.57812 | 11 | 0.039 | 7.97 | 15.2 | 1.03
[7 empty] | mg/L | 2.1939 | 2.1028 | 0.064066 | 1.219
21 | 1075000 | 35000 | 15000 | 1053600 | 13.1 | 0 | Lbs. | 21.9969 | 18.425 | 0.5625 | 11 | 0.037 | 7.94 | 14.9 | 1.05
[7 empty] | mg/L | 2.4535 | 2.0551 | 0.062741 | 1.2269
22 | 1081000 | 36000 | 0 | 1365900 | 12.7 | 0 | Lbs. | 21.9969 | 18.15 | 0.0625 | 11 | 0.036 | 7.91 | 14.1 | 0.99
[7 empty] | mg/L | 2.4399 | 2.0132 | 0.0069325 | 1.2201
23 | 1724000 | 35000 | 15000 | 1411600 | 21.5 | 0 | Lbs. | 37.285 | 20.075 | 0.25 | 21 | 0.042 | 7.7 | 15.4 | 1.03
[7 empty] | mg/L | 2.6444 | 1.4741 | 0.041866 | 1.443
24 | 1257000 | 35000 | 0 | 1324100 | 15.1 | 0 | Lbs. | 26.3963 | 21.725 | 0.75 | 13 | 0.044 | 7.77 | 16.3 | 1.09
[7 empty] | mg/L | 2.5179 | 2.0723 | 0.071542 | 1.2401
25 | 1542000 | 36000 | 15000 | 1397800 | 18.5 | 0 | Lbs. | 32.9953 | 25.85 | 0.875 | 17 | 0.027 | 7.67 | 17.3 | 1.05
[7 empty] | mg/L | 2.5657 | 2.0101 | 0.068039 | 1.3219
26 | 1187000 | 0 | 0 | 1350400 | 14.1 | 0 | Lbs. | 26.3963 | 20.075 | 0.5625 | 15 | 0.03 | 7.69 | 17.9 | 1.03
[7 empty] | mg/L | 2.6664 | 2.0279 | 0.056821 | 1.5152
27 | 1351000 | 36000 | 15000 | 1324000 | 16.1 | 0 | Lbs. | 26.3963 | 21.8625 | 0.78125 | 16 | 0.023 | 7.99 | 17.7 | 1.07
[7 empty] | mg/L | 2.3427 | 1.9403 | 0.069338 | 1.42
28 | 1083000 | 35000 | 15000 | 961300 | 12.8 | 0.02 | Lbs. | 26.3963 | 17.6 | 0.59375 | 12 | 0.024 | 7.95 | 16.6 | 1.12
[7 empty] | mg/L | 2.9225 | 1.9486 | 0.065737 | 1.3286
29 | 1348000 | 44000 | 0 | 1497900 | 16.7 | 0 | Lbs. | 29.2156 | 20.35 | 0.65625 | 15 | 0.037 | 7.95 | 16.2 | 1.07
[7 empty] | mg/L | 2.6265 | 1.5398 | 0.076768 | 1.2587
30 | 1302000 | 47000 | 15000 | 1288900 | 15.5 | 0 | Lbs. | 26.3963 | 21.725 | 0.75 | 15 | 0.025 | 7.83 | 16.2 | 1.02
[7 empty] | mg/L | 2.4309 | 2.0007 | 0.069069 | 1.3814
Monthly Totals
| 34878000 | 875000 | 270000 | 34705900 | 421.3 | 2.5 | Lbs. | 826.4494 | 542.8291 | 15.5312 | 407 | N/A | N/A | N/A | N/A
[7 empty] | mg/L | N/A | N/A | N/A | N/A
Daily Averages
| 1162600 | 29166.6667 | 9000 | 1156863.3333 | 14.0433 | 0.083333 | Lbs. | 27.5483 | 18.0943 | 0.51771 | 13.5667 | 0.038133 | 7.809 | 15.1633 | 1.0443
[7 empty] | mg/L | 2.8165 | 1.8188 | 0.057327 | 1.3769
Maximum Daily Totals
| 1724000 | 72000 | 30000 | 1497900 | 21.5 | 0.48 | Lbs. | 61.5913 | 25.85 | 1.25 | 21 | 0.054 | 7.99 | 17.9 | 1.12
[7 empty] | mg/L | 5.9798 | 2.1092 | 0.12136 | 1.9504
Minimum Daily Totals
| 755000 | 0 | 0 | 835000 | 8.4 | 0 | Lbs. | 19.7972 | 9.46 | 0 | 9 | 0.023 | 7.6 | 13 | 0.98
[7 empty] | mg/L | 1.4572 | 0.58348 | 0 | 0.61679

## Jul
July, 2020
Day | Value | Influent | Influent 2 | Combined Inf | Backwash | Backwash 2 | Comb. BW | Totalizer | EP-1 | FE-1 | FE-2 | BWP-1 | BWP-2 | SWP-1 | SWP-2 | BL-1 | Residual | Rain | Value | ACH | ACH-2 | Comb Lbs. | SA | SA-2 | Comb Lbs. | Polymer | Chlorine | Chlorine2 | Comb. Cl2 | Value | Raw | Finished
1 | Present | 261421 | 428724 | 1310000 | 158749 | 124889 | 63000 | 713769800 | 6019.3 | 42981.5 | 37694 | 403.4 | 941.1 | 337.8 | 698.1 | 231.4 | 1.02 | 0 | inches | 0.875 | 0 | 30.7956 | 9.875 | 0 | 21.725 | 3 | 15 | 0 | 15 | Turbidity | 1.47 | 0.027
| Previous | 260111 | 428724 |  | 158686 | 124889 |  | 712514200 | 6003.2 | 42981.5 | 37694 | 403.1 | 941.1 | 337.7 | 698.1 | 231.4 |  |  | Lbs. | 30.7956 | 0 |  | 21.725 | 0 |  | 0.75 |  |  |  | Temp. | 15.7 | 16.3
| Total | 1310000 | 0 |  | 63000 | 0 |  | 1255600 | 16.1 | 0 | 0 | 0.3 | 0 | 0.1 | 0 | 0 |  |  | mg/L | 2.8187 | 0 |  | 1.9885 | 0 |  | 0.068647 | 1.3729 | 0 |  | pH | 7.66 | 7.77
2 | Present | 262849 | 428724 | 1428000 | 158749 | 124889 | 0 | 715097800 | 6036.5 | 42981.5 | 37694 | 403.5 | 941.1 | 337.8 | 698.1 | 231.6 | 1 | 0 | inches | 0.75 | 0 | 26.3963 | 10.75 | 0 | 23.65 | 3 | 16 | 0 | 16 | Turbidity | 1.02 | 0.038
| Total | 1428000 | 0 |  | 0 | 0 |  | 1328000 | 17.2 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0.2 |  |  | Lbs. | 26.3963 | 0 |  | 23.65 | 0 |  | 0.75 |  |  |  | Temp. | 15 | 15.7
[19 empty] | mg/L | 2.2164 | 0 |  | 1.9858 | 0 |  | 0.062975 | 1.3435 | 0 |  | pH | 7.65 | 7.81
3 | Present | 264168 | 428724 | 1319000 | 158784 | 124889 | 35000 | 716552500 | 6052.2 | 42981.5 | 37694 | 403.7 | 941.1 | 337.9 | 698.1 | 231.6 | 1 | 0 | inches | 0.75 | 0 | 26.3963 | 9.5 | 0 | 20.9 | 2.875 | 16 | 0 | 16 | Turbidity | 1.13 | 0.039
| Total | 1319000 | 0 |  | 35000 | 0 |  | 1454700 | 15.7 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 26.3963 | 0 |  | 20.9 | 0 |  | 0.71875 |  |  |  | Temp. | 15.6 | 16.3
[19 empty] | mg/L | 2.3996 | 0 |  | 1.8999 | 0 |  | 0.065338 | 1.4545 | 0 |  | pH | 7.62 | 7.88
4 | Present | 265588 | 428724 | 1420000 | 158820 | 124889 | 36000 | 717872400 | 6069.1 | 42981.5 | 37694 | 403.8 | 941.1 | 338 | 698.1 | 231.6 | 0.97 | 0 | inches | 0.75 | 0 | 26.3963 | 10.5 | 0 | 23.1 | 3.125 | 17 | 0 | 17 | Turbidity | 1.16 | 0.056
| Total | 1420000 | 0 |  | 36000 | 0 |  | 1319900 | 16.9 | 0 | 0 | 0.1 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 26.3963 | 0 |  | 23.1 | 0 |  | 0.78125 |  |  |  | Temp. | 15.8 | 16.5
[19 empty] | mg/L | 2.2289 | 0 |  | 1.9506 | 0 |  | 0.065968 | 1.4355 | 0 |  | pH | 7.55 | 7.89
5 | Present | 266678 | 428724 | 1090000 | 158820 | 124889 | 0 | 719110700 | 6082.3 | 42981.5 | 37694 | 403.8 | 941.1 | 338 | 698.1 | 231.7 | 1.05 | 0 | inches | 0.625 | 0 | 21.9969 | 8.375 | 0 | 18.425 | 2.5 | 14 |  | 14 | Turbidity | 1.16 | 0.05
| Total | 1090000 | 0 |  | 0 | 0 |  | 1238300 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 21.9969 | 0 |  | 18.425 | 0 |  | 0.625 |  |  |  | Temp. | 15.9 | 16.9
[19 empty] | mg/L | 2.4197 | 0 |  | 2.0268 | 0 |  | 0.068752 | 1.5401 | 0 |  | pH | 7.55 | 7.91
6 | Present | 267864 | 429042 | 1504000 | 158856 | 124925 | 72000 | 720405500 | 6096.8 | 42987.1 | 37699.6 | 403.98 | 941.4 | 338.1 | 698.2 | 231.7 | 1.03 | 0 | inches | 0.5625 | 1 | 25.0472 | 9.125 | 1.125 | 22.55 | 3 | 15 | 3 | 18 | Turbidity | 1.36 | 0.047
| Total | 1186000 | 318000 |  | 36000 | 36000 |  | 1294800 | 14.5 | 5.6 | 5.6 | 0.18 | 0.3 | 0.1 | 0.1 | 0 |  |  | Lbs. | 19.7972 | 5.25 |  | 20.075 | 2.475 |  | 0.75 |  |  |  | Temp. | 15.9 | 16.1
[19 empty] | mg/L | 2.0015 | 1.9795 |  | 2.0296 | 0.93322 |  | 0.075825 | 1.5165 | 1.1312 |  | pH | 7.56 | 7.93
7 | Present | 269518 | 429042 | 1654000 | 158949 | 124925 | 93000 | 722005500 | 6116.4 | 42987.1 | 37699.6 | 404.3 | 941.4 | 338.1 | 698.2 | 231.7 | 1.09 | 0.03 | inches | 1 | 0 | 35.195 | 12.375 | 0 | 27.225 | 3.625 | 21 | 0 | 21 | Turbidity | 1.19 | 0.043
| Total | 1654000 | 0 |  | 93000 | 0 |  | 1600000 | 19.6 | 0 | 0 | 0.32 | 0 | 0 | 0 | 0 |  |  | Lbs. | 35.195 | 0 |  | 27.225 | 0 |  | 0.90625 |  |  |  | Temp. | 15.4 | 15.7
[19 empty] | mg/L | 2.5514 | 0 |  | 1.9736 | 0 |  | 0.065697 | 1.5224 | 0 |  | pH | 7.56 | 7.87
8 | Present | 270453 | 429042 | 935000 | 158985 | 124925 | 36000 | 723103600 | 6127.5 | 42987.1 | 37699.6 | 404.5 | 941.4 | 338.2 | 698.2 | 231.7 | 1.08 | 0 | inches | 0.5 | 0 | 17.5975 | 7.375 | 0 | 16.225 | 2.0625 | 12 | 0 | 12 | Turbidity | 1.05 | 0.027
| Total | 935000 | 0 |  | 36000 | 0 |  | 1098100 | 11.1 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 17.5975 | 0 |  | 16.225 | 0 |  | 0.51562 |  |  |  | Temp. | 18.4 | 17
[19 empty] | mg/L | 2.2567 | 0 |  | 2.0807 | 0 |  | 0.066124 | 1.5389 | 0 |  | pH | 7.72 | 7.95
9 | Present | 271895 | 429042 | 1442000 | 158985 | 124925 | 0 | 724516400 | 6144.7 | 42987.1 | 37699.6 | 404.5 | 941.4 | 338.2 | 698.2 | 231.8 | 1.03 | 0 | inches | 0.75 | 0 | 26.3963 | 10.9375 | 0 | 24.0625 | 3.25 | 18 | 0 | 18 | Turbidity | 1.08 | 0.042
| Total | 1442000 | 0 |  | 0 | 0 |  | 1412800 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 26.3963 | 0 |  | 24.0625 | 0 |  | 0.8125 |  |  |  | Temp. | 15.9 | 16.4
[19 empty] | mg/L | 2.1949 | 0 |  | 2.0008 | 0 |  | 0.06756 | 1.4967 | 0 |  | pH | 7.58 | 8.01
10 | Present | 273379 | 429042 | 1484000 | 159020 | 124925 | 35000 | 726004500 | 6162.3 | 42987.1 | 37699.6 | 404.7 | 941.4 | 338.2 | 698.2 | 231.9 | 1.02 | 0 | inches | 0.875 | 0 | 30.7956 | 11.125 | 0 | 24.475 | 3.25 | 19 | 0 | 19 | Turbidity | 1.08 | 0.026
| Total | 1484000 | 0 |  | 35000 | 0 |  | 1488100 | 17.6 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 30.7956 | 0 |  | 24.475 | 0 |  | 0.8125 |  |  |  | Temp. | 16.5 | 17.1
[19 empty] | mg/L | 2.4882 | 0 |  | 1.9775 | 0 |  | 0.065648 | 1.5352 | 0 |  | pH | 7.67 | 7.94
11 | Present | 275035 | 429042 | 1656000 | 159056 | 124925 | 36000 | 727538000 | 6182 | 42987.1 | 37699.6 | 404.8 | 941.4 | 338.3 | 698.2 | 232 | 0.99 | 0 | inches | 1 | 0 | 35.195 | 12.125 | 0 | 26.675 | 3.375 | 23 | 0 | 23 | Turbidity | 1.12 | 0.03
| Total | 1656000 | 0 |  | 36000 | 0 |  | 1533500 | 19.7 | 0 | 0 | 0.1 | 0 | 0.1 | 0 | 0.1 |  |  | Lbs. | 35.195 | 0 |  | 26.675 | 0 |  | 0.84375 |  |  |  | Temp. | 16.7 | 18.9
[19 empty] | mg/L | 2.5483 | 0 |  | 1.9314 | 0 |  | 0.061092 | 1.6653 | 0 |  | pH | 7.66 | 7.88
12 | Present | 276331 | 429042 | 1296000 | 159091 | 124925 | 35000 | 728957300 | 6197.7 | 42987.1 | 37699.6 | 405 | 941.4 | 338.4 | 698.2 | 232 | 1.08 | 0 | inches | 0.875 | 0 | 30.7956 | 9.75 | 0 | 21.45 | 3 | 17 | 0 | 17 | Turbidity | 1.05 | 0.031
| Total | 1296000 | 0 |  | 35000 | 0 |  | 1419300 | 15.7 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 30.7956 | 0 |  | 21.45 | 0 |  | 0.75 |  |  |  | Temp. | 17.4 | 19.1
[19 empty] | mg/L | 2.8492 | 0 |  | 1.9845 | 0 |  | 0.069389 | 1.5728 | 0 |  | pH | 7.78 | 7.91
13 | Present | 277752 | 429491 | 1870000 | 159127 | 124925 | 36000 | 730517900 | 6214.2 | 42993.1 | 37705.6 | 405.1 | 941.4 | 338.5 | 698.2 | 232.1 | 1.08 | 0 | inches | 0.875 | 1.75 | 39.9831 | 11 | 1.875 | 28.325 | 3.875 | 19 | 5 | 24 | Turbidity | 1.08 | 0.057
| Total | 1421000 | 449000 |  | 36000 | 0 |  | 1560600 | 16.5 | 6 | 6 | 0.1 | 0 | 0.1 | 0 | 0.1 |  |  | Lbs. | 30.7956 | 9.1875 |  | 24.2 | 4.125 |  | 0.96875 |  |  |  | Temp. | 17.3 | 17.6
[19 empty] | mg/L | 2.5985 | 2.4535 |  | 2.042 | 1.1016 |  | 0.081743 | 1.6032 | 1.3352 |  | pH | 7.6 | 7.89
14 | Present | 277752 | 431035 | 1544000 | 159127 | 124978 | 53000 | 732158300 | 6214.2 | 43013.1 | 37725.6 | 405.1 | 941.8 | 338.5 | 698.5 | 232.1 | 1.08 | 0 | inches | 0 | 6 | 31.5 | 0 | 5 | 11 | 1.75 | 0 | 19 | 19 | Turbidity | 1.38 | 0.068
| Total | 0 | 1544000 |  | 0 | 53000 |  | 1640400 | 0 | 20 | 20 | 0 | 0.4 | 0 | 0.3 | 0 |  |  | Lbs. | 0 | 31.5 |  | 0 | 11 |  | 0.4375 |  |  |  | Temp. | 16 | 17.5
[19 empty] | mg/L | 0 | 2.4462 |  | 0 | 0.85424 |  | 0.033975 | 0 | 1.4755 |  | pH | 7.55 | 7.67
15 | Present | 277752 | 432728 | 1693000 | 159127 | 125031 | 53000 | 733917500 | 6214.2 | 43032.9 | 37745.4 | 405.1 | 942.2 | 338.5 | 698.9 | 232.1 | 1.06 | 0 | inches | 0 | 5.5 | 28.875 | 0 | 2.625 | 5.775 | 1.5 | 0 | 23 | 23 | Turbidity | 1.08 | 0.045
| Total | 0 | 1693000 |  | 0 | 53000 |  | 1759200 | 0 | 19.8 | 19.8 | 0 | 0.4 | 0 | 0.4 | 0 |  |  | Lbs. | 0 | 28.875 |  | 0 | 5.775 |  | 0.375 |  |  |  | Temp. | 16.8 | 18
[19 empty] | mg/L | 0 | 2.045 |  | 0 | 0.40901 |  | 0.026559 | 0 | 1.6289 |  | pH | 7.49 | 7.62
16 | Present | 277752 | 434206 | 1478000 | 159127 | 125031 | 0 | 735564700 | 6214.2 | 43052.7 | 37765.2 | 405.1 | 942.3 | 338.5 | 698.9 | 232.1 | 1.04 | 0 | inches | 0 | 4.5 | 23.625 | 0 | 4.875 | 10.725 | 1.5 | 0 | 21 | 21 | Turbidity | 1.06 | 0.075
| Total | 0 | 1478000 |  | 0 | 0 |  | 1647200 | 0 | 19.8 | 19.8 | 0 | 0.1 | 0 | 0 | 0 |  |  | Lbs. | 0 | 23.625 |  | 0 | 10.725 |  | 0.375 |  |  |  | Temp. | 18.9 | 18.8
[19 empty] | mg/L | 0 | 1.9166 |  | 0 | 0.87008 |  | 0.030422 | 0 | 1.7036 |  | pH | 7.54 | 7.5
17 | Present | 277752 | 436037 | 1831000 | 159127 | 125067 | 36000 | 737337800 | 6214.2 | 43074.4 | 37786.9 | 405.1 | 942.5 | 338.5 | 699 | 232.1 | 1.06 | 0 | inches | 0 | 7.125 | 37.4062 | 0 | 6.125 | 13.475 | 2.25 | 0 | 26 | 26 | Turbidity | 1 | 0.053
| Total | 0 | 1831000 |  | 0 | 36000 |  | 1773100 | 0 | 21.7 | 21.7 | 0 | 0.2 | 0 | 0.1 | 0 |  |  | Lbs. | 0 | 37.4062 |  | 0 | 13.475 |  | 0.5625 |  |  |  | Temp. | 18.5 | 19.3
[19 empty] | mg/L | 0 | 2.4496 |  | 0 | 0.88242 |  | 0.036836 | 0 | 1.7026 |  | pH | 7.4 | 7.78
18 | Present | 277752 | 437632 | 1595000 | 159127 | 125102 | 35000 | 738921700 | 6214.2 | 43092.5 | 37805.1 | 405.1 | 942.8 | 338.5 | 699.2 | 232.1 | 1.11 | 0 | inches | 0 | 5 | 26.25 | 0 | 5.5 | 12.1 | 1.375 | 0 | 21 | 21 | Turbidity | 1.01 | 0.039
| Total | 0 | 1595000 |  | 0 | 35000 |  | 1583900 | 0 | 18.1 | 18.2 | 0 | 0.3 | 0 | 0.2 | 0 |  |  | Lbs. | 0 | 26.25 |  | 0 | 12.1 |  | 0.34375 |  |  |  | Temp. | 17.6 | 18.4
[19 empty] | mg/L | 0 | 1.9733 |  | 0 | 0.90962 |  | 0.025841 | 0 | 1.5787 |  | pH | 7.74 | 7.78
19 | Present | 277752 | 439130 | 1498000 | 159127 | 125138 | 36000 | 740482900 | 6214.2 | 43110.2 | 37822.7 | 405.1 | 943.1 | 338.5 | 699.5 | 232.1 | 1.06 | 0 | inches | 0 | 4.5 | 23.625 | 0 | 6 | 13.2 | 1.5 | 0 | 20 | 20 | Turbidity | 1.04 | 0.039
| Total | 0 | 1498000 |  | 0 | 36000 |  | 1561200 | 0 | 17.7 | 17.6 | 0 | 0.3 | 0 | 0.3 | 0 |  |  | Lbs. | 0 | 23.625 |  | 0 | 13.2 |  | 0.375 |  |  |  | Temp. | 17.8 | 18.9
[19 empty] | mg/L | 0 | 1.891 |  | 0 | 1.0566 |  | 0.030016 | 0 | 1.6009 |  | pH | 7.67 | 7.79
20 | Present | 277752 | 440786 | 1656000 | 159127 | 125173 | 35000 | 742102900 | 6214.2 | 43131 | 37843.5 | 405.1 | 943.4 | 338.5 | 699.7 | 232.1 | 1.02 | 0 | inches | 0 | 5 | 26.25 | 0 | 6.5 | 14.3 | 2.5 | 0 | 24 | 24 | Turbidity | 1.15 | 0.042
| Total | 0 | 1656000 |  | 0 | 35000 |  | 1620000 | 0 | 20.8 | 20.8 | 0 | 0.3 | 0 | 0.2 | 0 |  |  | Lbs. | 0 | 26.25 |  | 0 | 14.3 |  | 0.625 |  |  |  | Temp. | 18.6 | 19.3
[19 empty] | mg/L | 0 | 1.9007 |  | 0 | 1.0354 |  | 0.045254 | 0 | 1.7377 |  | pH | 7.53 | 7.73
21 | Present | 277752 | 442447 | 1661000 | 159127 | 125209 | 36000 | 743986300 | 6214.2 | 43151.1 | 37863.6 | 405.1 | 943.6 | 338.5 | 699.8 | 232.1 | 0.95 | 0 | inches | 0 | 6 | 31.5 | 0 | 7 | 15.4 | 3 | 0 | 25 | 25 | Turbidity | 1.32 | 0.041
| Total | 0 | 1661000 |  | 0 | 36000 |  | 1883400 | 0 | 20.1 | 20.1 | 0 | 0.2 | 0 | 0.1 | 0 |  |  | Lbs. | 0 | 31.5 |  | 0 | 15.4 |  | 0.75 |  |  |  | Temp. | 23.8 | 21.8
[19 empty] | mg/L | 0 | 2.2739 |  | 0 | 1.1117 |  | 0.054141 | 0 | 1.8047 |  | pH | 7.72 | 7.81
22 | Present | 277752 | 444061 | 1614000 | 159127 | 125244 | 35000 | 745618600 | 6214.2 | 43170.4 | 37882.9 | 405.1 | 943.9 | 338.5 | 700.1 | 232.1 | 0.99 | 0 | inches | 0 | 6 | 31.5 | 0 | 7 | 15.4 | 1.75 | 0 | 24 | 24 | Turbidity | 1.04 | 0.059
| Total | 0 | 1614000 |  | 0 | 35000 |  | 1632300 | 0 | 19.3 | 19.3 | 0 | 0.3 | 0 | 0.3 | 0 |  |  | Lbs. | 0 | 31.5 |  | 0 | 15.4 |  | 0.4375 |  |  |  | Temp. | 19.8 | 20.9
[19 empty] | mg/L | 0 | 2.3401 |  | 0 | 1.1441 |  | 0.032502 | 0 | 1.783 |  | pH | 7.43 | 7.54
23 | Present | 277752 | 445757 | 1696000 | 159127 | 125244 | 0 | 747236800 | 6214.2 | 43191.1 | 37903.6 | 405.1 | 944.2 | 338.5 | 700.3 | 232.1 | 1.02 | 0 | inches | 0 | 6.5 | 34.125 | 0 | 8.25 | 18.15 | 2.625 | 0 | 27 | 27 | Turbidity | 0.94 | 0.058
| Total | 0 | 1696000 |  | 0 | 0 |  | 1618200 | 0 | 20.7 | 20.7 | 0 | 0.3 | 0 | 0.2 | 0 |  |  | Lbs. | 0 | 34.125 |  | 0 | 18.15 |  | 0.65625 |  |  |  | Temp. | 23.8 | 20.5
[19 empty] | mg/L | 0 | 2.4126 |  | 0 | 1.2832 |  | 0.046396 | 0 | 1.9089 |  | pH | 7.71 | 7.59
24 | Present | 279444 | 445873 | 1808000 | 159307 | 125280 | 216000 | 748823400 | 6231.8 | 43192.3 | 37904.8 | 406.1 | 944.2 | 338.7 | 700.3 | 232.1 | 1.12 | 0 | inches | 1.375 | 0.5 | 51.0181 | 21 | 0.6 | 47.52 | 6.75 | 25 | 2 | 27 | Turbidity | 1.03 | 0.049
| Total | 1692000 | 116000 |  | 180000 | 36000 |  | 1586600 | 17.6 | 1.2 | 1.2 | 1 | 0 | 0.2 | 0 | 0 |  |  | Lbs. | 48.3931 | 2.625 |  | 46.2 | 1.32 |  | 1.6875 |  |  |  | Temp. | 18.6 | 19.7
[19 empty] | mg/L | 3.4294 | 2.7133 |  | 3.274 | 1.3644 |  | 0.11191 | 1.7716 | 2.0673 |  | pH | 7.61 | 7.8
25 | Present | 281543 | 445873 | 2099000 | 159346 | 125280 | 39000 | 750675400 | 6256.3 | 43192.3 | 37904.8 | 406.3 | 944.2 | 338.8 | 700.3 | 232.1 | 1.15 | 0 | inches | 1 | 0 | 35.195 | 30 | 0 | 66 | 8.25 | 23 | 0 | 23 | Turbidity | 1.14 | 0.035
| Total | 2099000 | 0 |  | 39000 | 0 |  | 1852000 | 24.5 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 35.195 | 0 |  | 66 | 0 |  | 2.0625 |  |  |  | Temp. | 16.9 | 19.2
[19 empty] | mg/L | 2.0105 | 0 |  | 3.7702 | 0 |  | 0.11782 | 1.3139 | 0 |  | pH | 7.57 | 7.99
26 | Present | 282841 | 445873 | 1298000 | 159385 | 125280 | 39000 | 752352400 | 6271.2 | 43192.3 | 37904.8 | 406.5 | 944.2 | 338.9 | 700.3 | 232.1 | 1.1 | 0 | inches | 0.625 | 0 | 21.9969 | 17.25 | 0 | 37.95 | 5.25 | 11 |  | 11 | Turbidity | 1.19 | 0.041
| Total | 1298000 | 0 |  | 39000 | 0 |  | 1677000 | 14.9 | 0 | 0 | 0.2 | 0 | 0.1 | 0 | 0 |  |  | Lbs. | 21.9969 | 0 |  | 37.95 | 0 |  | 1.3125 |  |  |  | Temp. | 17.7 | 18.6
[19 empty] | mg/L | 2.032 | 0 |  | 3.5057 | 0 |  | 0.12124 | 1.0161 | 0 |  | pH | 7.44 | 8.05
27 | Present | 283871 | 445961 | 1118000 | 159460 | 125280 | 75000 | 754199800 | 6285 | 43193.3 | 37905.8 | 406.8 | 944.2 | 338.9 | 700.3 | 232.2 | 1.15 | 0 | inches | 0.792 | 0.33333 | 29.6244 | 24.25 | 0.5 | 54.45 | 5.125 | 25 | 1 | 26 | Turbidity | 1.34 | 0.067
| Total | 1030000 | 88000 |  | 75000 | 0 |  | 1847400 | 13.8 | 1 | 1 | 0.3 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 27.8744 | 1.75 |  | 53.35 | 1.1 |  | 1.2812 |  |  |  | Temp. | 19 | 20
[19 empty] | mg/L | 3.2449 | 2.3845 |  | 6.2106 | 1.4988 |  | 0.13741 | 2.9103 | 1.3625 |  | pH | 7.54 | 7.95
28 | Present | 284838 | 445961 | 1797028 | 159497 | 125280 | 69516 | 756067000 | 6298.2 | 43193.3 | 37905.8 | 407.1 | 944.2 | 338.9 | 700.3 | 232.2 | 1.15 | 0 | inches | 1.2 |  | 42.234 | 8 | 0 | 17.6 | 4.75 | 14 | 0 | 14 | Turbidity | 1.37 | 0.034
| Total | 967000 | 830028 |  | 37000 | 32516 |  | 1867200 | 13.2 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 |  |  | Lbs. | 42.234 | 0 |  | 17.6 | 0 |  | 1.1875 |  |  |  | Temp. | 19.7 | 20.4
[19 empty] | mg/L | 5.2368 | 0 |  | 2.1823 | 0 |  | 0.079234 | 1.7359 | 0 |  | pH | 7.45 | 7.81
29 | Present | 1712050 | 445961 | 1712050 | 91977 | 125280 | 91977 | 757842600 | 6310.9 | 43193.3 | 37905.8 | 407.5 | 944.2 | 339 | 700.3 | 232.3 | 1.02 | 0 | inches | 1.125 | 0 | 39.5944 | 4.75 | 0 | 10.45 | 4.625 | 23 | 0 | 23 | Turbidity | 1.38 | 0.045
| Total | 1712050 |  |  | 91977 |  |  | 1775600 | 12.7 | 0 | 0 | 0.4 | 0 | 0.1 | 0 | 0.1 |  |  | Lbs. | 39.5944 | 0 |  | 10.45 | 0 |  | 1.1562 |  |  |  | Temp. | 20.5 | 20.9
[19 empty] | mg/L | 2.773 | 0 |  | 0.73187 | 0 |  | 0.080978 | 1.6108 | 0 |  | pH | 7.67 | 7.9
30 | Present | 1805870 | 445961 | 1805870 | 103998 | 125280 | 103998 | 759700200 | 6325.3 | 43193.3 | 37905.8 | 407.6 | 944.2 | 339 | 700.3 | 232.4 | 1 | 0 | inches | 7.625 | 0 | 81.8925 | 4.25 | 0 | 9.35 | 5.125 | 29 | 0 | 29 | Turbidity | 1.39 | 0.053
| Total | 1805870 |  |  | 103998 |  |  | 1857600 | 14.4 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0.1 |  |  | Lbs. | 81.8925 | 0 |  | 9.35 | 0 |  | 1.2812 |  |  |  | Temp. | 20 | 21.2
[19 empty] | mg/L | 5.4374 | 0 |  | 0.62081 | 0 |  | 0.085071 | 1.9255 | 0 |  | pH | 7.4 | 7.76
31 | Present | 1659567 | 445961 | 1659567 | 44913 | 125280 | 44913 | 761538700 | 6338.8 | 43193.3 | 37905.8 | 408.1 | 944.2 | 339.1 | 700.3 | 232.8 | 1.07 | 0 | inches | 8.5 | 0 | 91.29 | 4.25 | 0 | 9.35 | 4.875 | 28 | 0 | 28 | Turbidity | 1.39 | 0.033
| Total | 1659567 |  |  | 44913 |  |  | 1838500 | 13.5 | 0 | 0 | 0.5 | 0 | 0.1 | 0 | 0.4 |  |  | Lbs. | 91.29 | 0 |  | 9.35 | 0 |  | 1.2188 |  |  |  | Temp. | 20.1 | 21.5
[19 empty] | mg/L | 6.5957 | 0 |  | 0.67554 | 0 |  | 0.088055 | 2.023 | 0 |  | pH | 7.43 | 7.95
| Total | 29904487 | 18067028 | 47971515 | 1051888 | 423516 | 1475404 | 49024500 | 335.6 | 211.8 | 211.8 | 5 | 3.1 | 1.4 | 2.2 | 1.4 | N/A | 0.03 | Total Lbs. | 747.0194 | 313.4688 | 1060.4881 | 542.4375 | 138.545 | 680.9825 | 26.1094 | 400 | 241 | 641 | Avg Turb. | 1.1229 | 0.043097
| Average | 964660.871 | 582807.3548 | 1547468.2258 | 33931.871 | 13661.8065 | 47593.6774 | 1581435.4839 | 10.8258 | 6.8323 | 6.8323 | 0.16129 | 0.1 | 0.045161 | 0.070968 | 0.045161 | 1.0513 | 0.00096774 | Avg Lbs. | 24.0974 | 10.1119 | 34.2093 | 17.498 | 4.4692 | 21.9672 | 0.84224 | 12.9032 | 7.7742 | 20.6774 | Avg. Temp. | 17.2774 | 17.8484
| High | 2099000 | 1831000 | 3517920 | 180000 | 53000 | 216000 | 1883400 | 24.5 | 21.7 | 21.7 | 1 | 0.4 | 0.2 | 0.4 | 0.4 | 1.15 | 0.03 | High Lbs. | 91.29 | 37.4062 | 91.29 | 66 | 18.15 | 66 | 2.0625 | 29 | 27 | 29 | Avg pH | 7.3435 | 7.5774
| Low | 0 | 0 | 935000 | 0 | 0 | 0 | 1098100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0 | Low Lbs. | 0 | 0 | 17.5975 | 0 | 0 | 5.775 | 0.34375 | 0 | 0 | 11
[19 empty] | Avg mg/L | 2.0107 | 1.0058 |  | 1.5111 | 0.46627 |  | 0.066723 | 1.0937 | 0.73615 |  | High Turb. | 1.47 | 0.075
[19 empty] | High mg/L | 6.5957 | 2.7133 |  | 6.2106 | 1.4988 |  | 0.13741 | 2.9103 | 2.0673 |  | High Temp. | 23.8 | 21.8
[19 empty] | Low mg/L | 0 | 0 |  | 0 | 0 |  | 0.025841 | 0 | 0 |  | High pH | 7.78 | 8.05
*Averages, Highs and Lows represent only days the plant was in operation
[30 empty] | Low Turb. | 0.94 | 0.026
[30 empty] | Low Temp. | 15 | 15.7
[30 empty] | Low pH | 7.4 | 7.5

## JulTotals
July, 2020
Combined Plant Daily Totals
Day | Gallons |  |  |  | Plant Hours | Rain Inches | Chemical Usage |  |  |  |  | Finished Water |  |  | Residual Chlorine
| Influent | Backwash | Flush | Totalizer |  |  | Value | ACH | SodaAsh | Polymer | NaOCl | Turbidity | pH | Temp
1 | 1310000 | 63000 | 0 | 1255600 | 16.1 | 0 | Lbs. | 30.7956 | 21.725 | 0.75 | 15 | 0.027 | 7.77 | 16.3 | 1.02
[7 empty] | mg/L | 2.8187 | 1.9885 | 0.068647 | 1.3729
2 | 1428000 | 0 | 30000 | 1328000 | 17.2 | 0 | Lbs. | 26.3963 | 23.65 | 0.75 | 16 | 0.038 | 7.81 | 15.7 | 1
[7 empty] | mg/L | 2.2164 | 1.9858 | 0.062975 | 1.3435
3 | 1319000 | 35000 | 0 | 1454700 | 15.7 | 0 | Lbs. | 26.3963 | 20.9 | 0.71875 | 16 | 0.039 | 7.88 | 16.3 | 1
[7 empty] | mg/L | 2.3996 | 1.8999 | 0.065338 | 1.4545
4 | 1420000 | 36000 | 0 | 1319900 | 16.9 | 0 | Lbs. | 26.3963 | 23.1 | 0.78125 | 17 | 0.056 | 7.89 | 16.5 | 0.97
[7 empty] | mg/L | 2.2289 | 1.9506 | 0.065968 | 1.4355
5 | 1090000 | 0 | 15000 | 1238300 | 13.2 | 0 | Lbs. | 21.9969 | 18.425 | 0.625 | 14 | 0.05 | 7.91 | 16.9 | 1.05
[7 empty] | mg/L | 2.4197 | 2.0268 | 0.068752 | 1.5401
6 | 1504000 | 72000 | 0 | 1294800 | 20.1 | 0 | Lbs. | 25.0472 | 22.55 | 0.75 | 18 | 0.047 | 7.93 | 16.1 | 1.03
[7 empty] | mg/L | 1.9905 | 1.4814 | 0.075825 | 1.3238
7 | 1654000 | 93000 | 0 | 1600000 | 19.6 | 0.03 | Lbs. | 35.195 | 27.225 | 0.90625 | 21 | 0.043 | 7.87 | 15.7 | 1.09
[7 empty] | mg/L | 2.5514 | 1.9736 | 0.065697 | 1.5224
8 | 935000 | 36000 | 0 | 1098100 | 11.1 | 0 | Lbs. | 17.5975 | 16.225 | 0.51562 | 12 | 0.027 | 7.95 | 17 | 1.08
[7 empty] | mg/L | 2.2567 | 2.0807 | 0.066124 | 1.5389
9 | 1442000 | 0 | 15000 | 1412800 | 17.2 | 0 | Lbs. | 26.3963 | 24.0625 | 0.8125 | 18 | 0.042 | 8.01 | 16.4 | 1.03
[7 empty] | mg/L | 2.1949 | 2.0008 | 0.06756 | 1.4967
10 | 1484000 | 35000 | 15000 | 1488100 | 17.6 | 0 | Lbs. | 30.7956 | 24.475 | 0.8125 | 19 | 0.026 | 7.94 | 17.1 | 1.02
[7 empty] | mg/L | 2.4882 | 1.9775 | 0.065648 | 1.5352
11 | 1656000 | 36000 | 15000 | 1533500 | 19.7 | 0 | Lbs. | 35.195 | 26.675 | 0.84375 | 23 | 0.03 | 7.88 | 18.9 | 0.99
[7 empty] | mg/L | 2.5483 | 1.9314 | 0.061092 | 1.6653
12 | 1296000 | 35000 | 0 | 1419300 | 15.7 | 0 | Lbs. | 30.7956 | 21.45 | 0.75 | 17 | 0.031 | 7.91 | 19.1 | 1.08
[7 empty] | mg/L | 2.8492 | 1.9845 | 0.069389 | 1.5728
13 | 1870000 | 36000 | 15000 | 1560600 | 22.5 | 0 | Lbs. | 39.9831 | 28.325 | 0.96875 | 24 | 0.057 | 7.89 | 17.6 | 1.08
[7 empty] | mg/L | 2.526 | 1.5718 | 0.081743 | 1.4692
14 | 1544000 | 53000 | 0 | 1640400 | 20 | 0 | Lbs. | 31.5 | 11 | 0.4375 | 19 | 0.068 | 7.67 | 17.5 | 1.08
[7 empty] | mg/L | 1.2231 | 0.42712 | 0.033975 | 0.73775
15 | 1693000 | 53000 | 0 | 1759200 | 19.8 | 0 | Lbs. | 28.875 | 5.775 | 0.375 | 23 | 0.045 | 7.62 | 18 | 1.06
[7 empty] | mg/L | 1.0225 | 0.2045 | 0.026559 | 0.81447
16 | 1478000 | 0 | 0 | 1647200 | 19.8 | 0 | Lbs. | 23.625 | 10.725 | 0.375 | 21 | 0.075 | 7.5 | 18.8 | 1.04
[7 empty] | mg/L | 0.9583 | 0.43504 | 0.030422 | 0.85182
17 | 1831000 | 36000 | 0 | 1773100 | 21.7 | 0 | Lbs. | 37.4062 | 13.475 | 0.5625 | 26 | 0.053 | 7.78 | 19.3 | 1.06
[7 empty] | mg/L | 1.2248 | 0.44121 | 0.036836 | 0.85131
18 | 1595000 | 35000 | 0 | 1583900 | 18.1 | 0 | Lbs. | 26.25 | 12.1 | 0.34375 | 21 | 0.039 | 7.78 | 18.4 | 1.11
[7 empty] | mg/L | 0.98667 | 0.45481 | 0.025841 | 0.78934
19 | 1498000 | 36000 | 0 | 1561200 | 17.7 | 0 | Lbs. | 23.625 | 13.2 | 0.375 | 20 | 0.039 | 7.79 | 18.9 | 1.06
[7 empty] | mg/L | 0.94551 | 0.52828 | 0.030016 | 0.80043
20 | 1656000 | 35000 | 0 | 1620000 | 20.8 | 0 | Lbs. | 26.25 | 14.3 | 0.625 | 24 | 0.042 | 7.73 | 19.3 | 1.02
[7 empty] | mg/L | 0.95033 | 0.5177 | 0.045254 | 0.86887
21 | 1661000 | 36000 | 0 | 1883400 | 20.1 | 0 | Lbs. | 31.5 | 15.4 | 0.75 | 25 | 0.041 | 7.81 | 21.8 | 0.95
[7 empty] | mg/L | 1.137 | 0.55585 | 0.054141 | 0.90235
22 | 1614000 | 35000 | 0 | 1632300 | 19.3 | 0 | Lbs. | 31.5 | 15.4 | 0.4375 | 24 | 0.059 | 7.54 | 20.9 | 0.99
[7 empty] | mg/L | 1.1701 | 0.57203 | 0.032502 | 0.89148
23 | 1696000 | 0 | 0 | 1618200 | 20.7 | 0 | Lbs. | 34.125 | 18.15 | 0.65625 | 27 | 0.058 | 7.59 | 20.5 | 1.02
[7 empty] | mg/L | 1.2063 | 0.64159 | 0.046396 | 0.95443
24 | 1808000 | 216000 | 0 | 1586600 | 18.8 | 0 | Lbs. | 51.0181 | 47.52 | 1.6875 | 27 | 0.049 | 7.8 | 19.7 | 1.12
[7 empty] | mg/L | 3.0714 | 2.3192 | 0.11191 | 1.9195
25 | 2099000 | 39000 | 0 | 1852000 | 24.5 | 0 | Lbs. | 35.195 | 66 | 2.0625 | 23 | 0.035 | 7.99 | 19.2 | 1.15
[7 empty] | mg/L | 2.0105 | 3.7702 | 0.11782 | 1.3139
26 | 1298000 | 39000 | 0 | 1677000 | 14.9 | 0 | Lbs. | 21.9969 | 37.95 | 1.3125 | 11 | 0.041 | 8.05 | 18.6 | 1.1
[7 empty] | mg/L | 2.032 | 3.5057 | 0.12124 | 1.0161
27 | 1118000 | 75000 | 15000 | 1847400 | 14.8 | 0 | Lbs. | 29.6244 | 54.45 | 1.2812 | 26 | 0.067 | 7.95 | 20 | 1.15
[7 empty] | mg/L | 2.8147 | 3.8547 | 0.13741 | 2.1364
28 | 1797028 | 69516 | 0 | 1867200 | 13.2 | 0 | Lbs. | 42.234 | 17.6 | 1.1875 | 14 | 0.034 | 7.81 | 20.4 | 1.15
[7 empty] | mg/L | 5.2368 | 2.1823 | 0.079234 | 1.7359
29 | 1712050 | 91977 | 15000 | 1775600 | 12.7 | 0 | Lbs. | 39.5944 | 10.45 | 1.1562 | 23 | 0.045 | 7.9 | 20.9 | 1.02
[7 empty] | mg/L | 2.773 | 0.73187 | 0.080978 | 1.6108
30 | 1805870 | 103998 | 15000 | 1857600 | 14.4 | 0 | Lbs. | 81.8925 | 9.35 | 1.2812 | 29 | 0.053 | 7.76 | 21.2 | 1
[7 empty] | mg/L | 5.4374 | 0.62081 | 0.085071 | 1.9255
31 | 1659567 | 44913 | 60000 | 1838500 | 13.5 | 0 | Lbs. | 91.29 | 9.35 | 1.2188 | 28 | 0.033 | 7.95 | 21.5 | 1.07
[7 empty] | mg/L | 6.5957 | 0.67554 | 0.088055 | 2.023
Monthly Totals
| 47971515 | 1475404 | 210000 | 49024500 | 547.4 | 0.03 | Lbs. | 1060.4881 | 680.9825 | 26.1094 | 641 | N/A | N/A | N/A | N/A
[7 empty] | mg/L | N/A | N/A | N/A | N/A
Daily Averages
| 1547468.2258 | 47593.6774 | 6774.1935 | 1581435.4839 | 17.6581 | 0.00096774 | Lbs. | 34.2093 | 21.9672 | 0.84224 | 20.6774 | 0.044806 | 7.8277 | 18.5323 | 1.0513
[7 empty] | mg/L | 2.3318 | 1.5255 | 0.066723 | 1.3359
Maximum Daily Totals
| 2099000 | 216000 | 60000 | 1883400 | 24.5 | 0.03 | Lbs. | 91.29 | 66 | 2.0625 | 29 | 0.075 | 8.05 | 21.8 | 1.15
[7 empty] | mg/L | 6.5957 | 3.8547 | 0.13741 | 2.1364
Minimum Daily Totals
| 935000 | 0 | 0 | 1098100 | 11.1 | 0 | Lbs. | 17.5975 | 5.775 | 0.34375 | 11 | 0.026 | 7.5 | 15.7 | 0.95
[7 empty] | mg/L | 0.94551 | 0.2045 | 0.025841 | 0.73775

## 2020Totals
Jan - Jul, 2020
Combined Plant Monthly Totals & Averages
Month | Gallons |  |  |  | Plant Hours | Rain Inches | Chemical Usage |  |  |  |  | Finished Water Averages
| Influent | Backwash | Flush | Totalizer |  |  | Value | ACH | SodaAsh | Polymer | NaOCl | Turbidity | pH | Temp | Residual
Jan | 30906000 | 809000 | 270000 | 30403600 | 377.5 | 5.99 | Lbs. | 889.5841 | 545.875 | 16.9062 | 340 | 0.036065 | 7.5674 | 9.3839 | 1.0271
[7 empty] | mg/L | 3.3251 | 2.0905 | 0.067822 | 1.2669
Feb | 30024000 | 860000 | 105000 | 29722300 | 373 | 2.5 | Lbs. | 617.8016 | 360.525 | 6.5781 | 321 | 0.037793 | 7.6814 | 8.869 | 1.0407
[7 empty] | mg/L | 1.5984 | 1.0876 | 0.026525 | 1.2838
Mar | 30548000 | 809000 | 225000 | 30283300 | 375.6 | 3.37 | Lbs. | 608.6303 | 458.15 | 12.875 | 311 | 0.040226 | 7.7716 | 9.2742 | 1.0319
[7 empty] | mg/L | 2.1169 | 1.7108 | 0.053641 | 1.1101
Apr | 31553000 | 704000 | 210000 | 30968700 | 388.1 | 0.98 | Lbs. | 604.05 | 482.7625 | 12.5469 | 351 | 0.044733 | 7.73 | 11.2333 | 1.0443
[7 empty] | mg/L | 2.2021 | 1.791 | 0.048928 | 1.5435
May | 31993000 | 1004000 | 225000 | 31595800 | 396.2 | 2.59 | Lbs. | 762.5487 | 505.45 | 6.3594 | 351 | 0.046806 | 7.7568 | 13.8839 | 1.0281
[7 empty] | mg/L | 2.8393 | 1.8659 | 0.02609 | 1.2531
Jun | 34878000 | 875000 | 270000 | 34705900 | 421.3 | 2.5 | Lbs. | 826.4494 | 542.8291 | 15.5312 | 407 | 0.038133 | 7.809 | 15.1633 | 1.0443
[7 empty] | mg/L | 2.8165 | 1.8188 | 0.057327 | 1.3769
Jul | 47971515 | 1475404 | 210000 | 49024500 | 547.4 | 0.03 | Lbs. | 1060.4881 | 680.9825 | 26.1094 | 641 | 0.044806 | 7.8277 | 18.5323 | 1.0513
[7 empty] | mg/L | 2.3318 | 1.5255 | 0.066723 | 1.3359
2020 Totals
| 237873515 | 6536404 | 1515000 | 236704100 | 2879.1 | 17.96 | Lbs. | 5369.5522 | 3576.5741 | 96.9062 | 2722 | N/A | N/A | N/A | N/A
[7 empty] | mg/L | N/A | N/A | N/A | N/A
Monthly Averages
| 33981930.7143 | 933772 | 216428.5714 | 33814871.4286 | 411.3 | 2.5657 | Lbs. | 767.0789 | 510.9392 | 13.8438 | 388.8571 | 0.041223 | 7.7348 | 12.3343 | 1.0382
[7 empty] | mg/L | 2.4615 | 1.6986 | 0.049579 | 1.31
Maximum Monthly Totals
| 47971515 | 1475404 | 270000 | 49024500 | 547.4 | 5.99 | Lbs. | 1060.4881 | 680.9825 | 26.1094 | 641 | 0.046806 | 7.8277 | 18.5323 | 1.0513
[7 empty] | mg/L | 3.3251 | 2.0905 | 0.067822 | 1.5435
Minimum Monthly Totals
| 30024000 | 704000 | 105000 | 29722300 | 373 | 0.03 | Lbs. | 604.05 | 360.525 | 6.3594 | 311 | 0.036065 | 7.5674 | 8.869 | 1.0271
[7 empty] | mg/L | 1.5984 | 1.0876 | 0.02609 | 1.1101