May 2004

Biosolid Management Plan                 Attachment 2

for

The City of Newberg (CN).

File Number: 102894

I. Treatment Facility

Introduction:

The City of Newberg (CN) owns and operates a municipal sewage collection and treatment system (built 1987) under National Discharge Elimination System (NPDES) permit.  Wastewater processed by the sewage treatment works is principally of domestic origin.  Septage is accepted at this wastewater treatment facility.  The industrial discharges to the CN facility are minor and do not require regulation under a local pretreatment permit.  Treated effluent from the treatment plant is discharged to the Willamette River, in Yamhill County, Oregon.

A) Wastewater Processing:

CN operates a 4.0-Million Gallon per Day (MGD) average dry weather design flow activated sludge plant.  Secondary treatment is achieved in two oxidation ditches and three 80-foot diameter, center feed secondary clarifiers.

Influent passes through headworks, which consists of screening and grit removal.  Influent passes through a mechanical bar screen, an aerated grit chamber, cyclone separator and grit classifier.  All grit and debris are landfilled.

Influent from the head works is mixed with activated sludge into one of two oxidation ditches. Each oxidation ditch is 2 million gallons (gal.). The oxidation ditch effluent is transferred to one of three secondary clarifiers (XXX million gal. each) where solids are allowed to settle out. Solids are removed and routed to one of two (2) sludge storage tanks. Each storage tank has is 80,000 gal. capacity.

Clarifier effluent is directed to two (2) chlorine contact chambers (135,000 gal. each) for disinfection and then treated with sulfur dioxide to remove residual chlorine prior to being discharged to the Upper Willamette River (river mile 49).  The City uses chlorine gas to disinfect their effluent.

B) Solids Processing:

Sludge from the secondary claifiers and dredging from the oxidation ditches (when necessary) are pumped through this series of solid treatment processes: the sludge storage tanks, dissolved air floatation (sludge thickening), and two (2) 2 meter belt filter press prior to entering one of two (2) compost reactor vessel process. Each reactor tunnel is 18 feet wide, 12 feet high and 66 feet long. At maximum loading each tunnel has a detention time of approximately 14 days. All batches must meet the minimum vector attraction reduction requirement of aerobic treatment of the sludge for at least 14 days at over 40C (104F) with the average temperature of over 45C (Compost).

There is primarily one end route for biosolids generated from this facility and that is Class A compost.

C) Solids Storage Structure:

There are two (2) 0.08 million gallons sludge storage tanks at the biosolids facility. In addition, a 1/2-acre lined compost yard, which is located at this facility.

D) Septage Receiving Facility:

This facility does not receive septage.

F) Pretreatment Program:

The regions industrial wastewater pretreatment program protects the environment and the area’s wastewater collection, treatment facilities and biosolids quality by regulating potentially contaminated wastewater discharges from commercial and industrial activities.

The city of Newberg operates source control programs under a ordinance developed by the CN and adopted by the city.  The CN ordinance directs the establishment of local limits to maintain biosolids quality at or below 50-percent of the “clean sludge” metal concentration criteria identified in EPA 40 CFR Part 503.13 and Oregon DEQ’s Oregon Administrative Rules Chapter 340 Division 50.

Newberg administers the program within the urban growth boundary.  The regulatory activities include developing pollutant limits for industrial discharges, responding to permit violations and conducting industrial site inspections.

II Solid Treatment Processes

The EPA’s 40 CFR Part 503 and DEQ’s OAR340-50 allow permittees to use EPA approved alternatives to satisfy Class A and B biosolids pathogen and vector attraction reduction criteria.  The permittee must notify the Department in writing and get approval prior to any process change that would utilize pathogen reduction or vector attraction reduction alternatives other than their primary reduction alternatives contained in this management plan.  The permittee must also certify that the alternatives used are EPA approved and that sampling and monitoring conforms to the 40 CFR 503 and OAR 340-050 regulations.

Pathogen Reduction

To meet the Part 503 regulatory requirements, pathogen reduction must be met before vector attraction reduction or at the same time vector attraction reduction is achieved.

Class A Biosolids

With all Class A alternatives microbial monitoring for fecal coliforms or Salmonella sp. is required (see section A and B below).  This management plan lists the primary alternative and options employed by the permittee to meet Class A and B biosolids criteria.

A) Monitoring for Fecal Coliform or Salmonella sp.

Monitoring for Fecal Coliform or Salmonella sp. is required to detect growth of bacterial pathogens.  Because Class A biosolids may be used without site restrictions, all Class A material must be tested to show that the microbial requirements are met at the time when it is ready to be used, disposed, sold or given away.  In addition to meeting process requirements, Class A biosolids must meet one of the following requirements:

- Either the density of the fecal coliforms in the biosolids be less than 1,000 MPN per gram total solids (dry gram weight),

- Or the density of Salmonella sp. Bacteria in the biosolids be less than 3 MPN per 4 grams of total solids (dry weight basis).

Unlike Class B biosolids, Class A requirements are not based on an average value.  Sampling for Class A biosolids consists of at least seven (7) discrete samples taken over a 2-week period.  Test results are required before Class A material can be release for use or disposal.  The microbial requirement that a Class A biosolids must meet is either:

- At the time of use or disposal, or

- At the time the biosolids are prepared for sale or given away in a bag or other container for land application, or

- At time the biosolid or material derived from the biosolid is prepared to meet the requirements in 503.10(b), 503.10 (c), 503.10 (e) or 503.10 (f).

B) Class A Pathogen Reduction Alternatives

Alt.  4) Sewage Sludge treated in Unknown Processes 503.32(a)(6)

This requirement relies on comprehensive monitoring of bacteria, enteric viruses and viable helmith ova to demonstrate adequate reduction of pathogens:

- Either the density of the fecal coliforms in the sewage sludge be less than 1,000 MPN per gram total solids (dry gram weight), Or the density of Salmonella sp. Bacteria in the sewage be less than 3 MPN per 4 grams of total solids (dry weight basis).

- The density of enteric viruses in the sewage sludge after pathogen treatment must be less than 1 PFU per 4 grams of total solids (dry weight basis).

- The density of viable helmith ova in the sewage sludge after pathogen treatment must be less than 1 per 4 grams of total solids (dry weight basis). (Alt. 4 is for an unknown process and must be approved by the EPA prior to its implementation.  This should not be an alternative we use in Oregon.)

Alt. 5) Use of Processes to Further Reduce Pathogens (PFRP) 503.32(a)(7)

This requirement relies the process to demonstrate adequate reduction of pathogens to meet Class A biosolid criteria:

- Sludge has been treated in one of the PFRPs listed in Appendix B of the 503 regulation, and

- Either the density of the fecal coliforms in the sewage sludge be less than 1,000 MPN per gram total solids (dry gram weight), Or the density of Salmonella sp. Bacteria in the sewage be less than 3 MPN per 4 grams of total solids (dry weight basis).

Class B Biosolids

Class B biosolids can be met by using one of three alternatives, the two primary alternatives used by this facility are Alt. 1) Monitor sewage sludge for fecal coliform 503.32(b)(2), and Alt. 2) Use Process to Significantly Reduce Pathogen (PSRP) 503.32(b)(3).

Alt. 1) Monitor sewage sludge for fecal coliform 503.32(b)(2) requires that seven samples of treated sewage sludge (biosolids) be collected and that the geometric mean fecal coliform density of these samples be less than 2 million MPN per dry gram biosolid (dry weight basis).

Alt. 2) Use Process to Significantly Reduce Pathogen (PSRP) 503.32(b)(3) considers sludge treated in one of the PSRPs listed in Appendix B of the 40 CFR Part 503 to meet Class B biosolid criteria for pathogen reduction.

For this facility the following PSRP is primarily used:

- ##4 Composting, the temperature of the sewage sludge is raised to 40C (104F) or higher and remains at 40C or higher for 5 days.  For 4 hours during the 5-day period, the temperature in the compost pile must exceed 55C (131F).

B) Vector Attraction

This facility primarily uses the following vector attraction reduction options:

Note: if the compost process is the biosolid treatment method then the pathogen reduction must be met at or prior to vector attraction; therefore the only vector attraction reduction available for the compost process is option 5 below.

Opt. 1) The % volatile solid reduction calculation to use for anaerobic digester that is decanted and that does not have appreciable grit accumulation would be the Van Kleeck or Approximate Mass balance  (AMB) equation depending upon the percent solids in the decantante (Attachment A).

To meet the biosolid vector attraction reduction requirements an anaerobic digester must provide a 15 day detention time at 35C in a completely mixed high rate digester in order to achieve a volatile solids reduction of 38 % or more.  There are alternative vector attraction reduction methods that are deemed equivalent to the 38% volatile solid reduction criteria under the EPA’s and the DEQ’s regulations.

## Opt 4) The Specific Oxygen Uptake Rate (SOUR) for sewage sludge treated in an aerobic process shall be equal to or less than 1.5 milligrams of oxygen per hour per gram of total solids (dry weight basis) at a minimum temperature of 20 degrees Celsius.  The range of total solids for the SOUR test is 2% or less.

Opt.5) Aerobic treatment of the sludge for at least 14 days at over 40C (104F) with the average temperature of over 45C (Compost).

Opt. 7) 75% solid by drying prior to mixing with other materials.  Sewage sludge treated in aerobic or anaerobic process (i.e. Sewage sludge that do not contain unstabilized solids generated in primary wastewater treatment).

## Opt 10) Sludge applied to the land surface or placed on a surface disposal site shall be incorporated into the soil within six hours after application to or placement on the land.

C) Batch Processes

Class A Biosolids

Alt. 5, PFRP Compost, compost pile must meet PFRP) of 3 consecutive days at a minimum pile temperature of 55C. (Note: Class A PFRP must be met within the Class B PSRP treatment parameter, EPA requirement).

Class B Biosolids

Alt. 3,  # 4 PSRP) Compost, Process that Significantly Reduces Pathogens (PSRP) showing an average pile temperature of 45C and minimum temperature of 40C in the pile within 14 consecutive days.

Note: For solids to be composted which have already have achieved vector attraction criteria, i.e. compost solids that have been aerobically digested, lagoons stored and dewatered or air dried prior to composting; Pathogen reduction must be met at or before vector attraction reduction, therefore the composted biosolids must meet vector attraction through the compost process and have pathogen reduction and vector attraction reduction tested to meet the compost treatment criteria.

III Biosolid Characteristics

CN’s treatment works utilizes an activated sludge process.  The treatment facility wastes activated sludge form the secondary clarifiers through sludge storage, sludge belt filter press, and sludge composting treatment processes.

For the past five- (5) years the average volatile solids reduction criteria has been achieved by the  (CN) wastewater treatment Class A compost process.

Annually, CN had generated approximately 500 dry tons of biosolids.  For the year 2003 CN generated (573) dry metric tons of Class A compost biosolids. Under the 40 CFR Part 503, CN is required to sample biosolid every 90-days or four (4) times per year.  Frequency of monitoring depends on the amount biosolid generated that is marketed to be sold or given away, land application and surface disposal.    Frequency depends on the amount on bulk biosolid applied to the land, or the amount of sewage sludge received by a person who prepares biosolid that is sold or given away in a bag or other container for application to the land (dry weight basis), or the amount of biosolid (excluding domestic septage) placed on a surface disposal site.

Sampling

1) Sludge Belt Filter Press

Sample location: At discharge point to conveyor.

# Number and type of sample taken per day: 1-2 grab samples per day, minimum 9 samples to make a representative composite sample.

Sample storage and transport: Samples are stored at 4 degrees C in ice chest or refrigerator.  Samples are transported in ice chest to maintain temperature during delivery to laboratory. Pathogen samples are delivered to lab within 6 hour of sample collection.

Sample analysis method: EPA 9045; EPA 160.3;EPA 160.4; SM 4500-NH3B; EPA 353.2; EPA 365.3; EPA 351.3; SW-846 7060; SW-846 6010; SW-846; SW-846 7481; SW-847 7471; SW-846 7740; SM 18th, 9221E.1; SM 18:9260D.1; ASTM D 4994-89; EPA 600/1-87/014; EPA 8240; EPA 1613; EPA 8270; EPA 1613B; EPA 1668 (may include one or more of the referenced methods)

2) Compost

Sample location: Random depths and locations within the compost pile

Number and type of sample taken per batch: 7 discrete samples are mixed together to form a composite sample for metal analysis. For Class A Biosolid seven (7) discrete samples are required for pathogens.

Sample storage and transport: sample is stored at 4 degrees C in ice chest or refrigerator.  Samples are transported in ice chest to maintain temperature during delivery to laboratory.  Pathogen samples are delivered to lab within 6 hour of sample collection.

Sample analysis method: EPA 9045; EPA 160.3;EPA 160.4; SM 4500-NH3B;EPA 353.2; EPA 365.3; EPA 351.3; SW-846 7060; SW-846 6010; SW-846 ; SW-846 7481; SW-847 7471; SW-846 7740; SM 18th, 9221E.1; SM 18:9260D.1; ASTM D 4994-89; EPA 600/1-87/014; EPA 8240; EPA 1613; EPA 8270; EPA 1613B; EPA 1668 (may include one or more of the referenced methods)

Biosolid Analysis:

Biosolid Chemical Analysis:

From the  (CN)’s 2003 biosolids analysis the following is a representative sampling of the biosolid metal concentration.

Pounds(#)	Metal			lb./95 acre-yr.	site life

lb.	Arsenic (As)		0.053		683

lb.	Cadmium (Cd)	0.006		5783

lb.	Chromium (Cr)	0.155		6871

lb.	Copper (Cu)		2.22		603

lb.	Lead (PB)		0.21		1257

lb.	Mercury (Hg)		0.006		2334

lb.	Molybdenum (Mo)	0.022		2927

lb.	Nickel (Ni)		0.132		2837

lb.	Selenium (Se)		0.036		2474

lb.	Silver (Au)

lb.	Zinc (Zn)		4.12		607

The site life would be limited to (607) years based on the Zinc loading CN’s 2003-biosolid analysis (Attachment B).

Biosolid Nutrient Analysis:

For the year 2003, the composted biosolids contained about 9480 pounds (lb.) total nitrogen (N) of which about 572 lb. is in the nitrate form (NO3-NO2), 3280 lb. is in the ammonia form (NH3), and 5628 lb. Organic nitrogen. From the analysis the CN if were to land apply on to handle their annual biosolid nitrogen production they would need approximately (95) acres.

IV Biosolids Beneficial Reuse Program

Transportation and Land Application:

Biosolids are off loaded into city owned (XXXX gal.)-tanker trucks or XX-yard dump trailers at the Biosolids Management Facility.  The biosolids loading areas are impounded in case of accidental spillage of biosolids during the truck loading process.  These areas have drains that tie back into the on-site facultative lagoons.  During the summer months CN’s biosolids are land applied on a variable number of acres, depending on seasonal production from the facility.

For the year 2003, CN land applied to three DEQ authorized sites totaling 426 -acres.  The biosolid land application sites are capable of assimilating CN ’s annual total nitrogen production.  The perennial agronomic biosolid land application rate for pastures and grass is 140 lb. available N per acre–yr.  The agronomic land application rate for annual ryegrass, the predominate crop utilized by CN’s land application program, is 140 lb. available N per acre–yr.

Land application:  CN owns land and land applies on other farmlands.  All DEQ site authorizations for CN are part of CN’s Biosolid Management Plan.  The CN owns (XX) acres and has (XX) acres of additional farmlands to beneficially reuse their biosolids.

Long term biosolid application rates and site restrictions are contained in the biosolid site authorization letter.  References to the OAR 340-50, The 40 CFR Part 503, site setbacks, site agronomic loading rates, land application restrictions and site restrictions are also detailed out in the site authorization letter.

V Contingency Options

In the event Class B biosolids are spilled between the treatment facility and the land application site, CN’s sewage treatment works shall contain the spill, lime, absorb (via sand) and remove spilled sludge solids spills with a front end loader or shovels and dispose of the spillage at a DEQ authorized application or disposal site.  All spills into waters of the state or spills on the ground surface that are like to enter waters of the state shall be reported to immediately to Oregon Emergency Response System (OERS) at 1-800-452-0311 and your regional biosolids coordinator at (541) 440-3338.  All spills of 25 gallons or more on the ground surface shall be report to the regional biosolids coordinator at (541) 440-3338.

VI Reporting

Daily Reporting and Recordkeeping:

Each year prior to land application of biosolids the source operators shall check to see if contiguous property owners have changed.  The operators shall keep a record of contact (date, and/or written log of phone call w/ name and number, and/or xerox of postcard w/ name and address, etc.,) with contiguous property owners, and which notifies new neighbors of the biosolid land application practice.  Operator shall provide this documentation in the annual biosolid report.

Annual Reporting

The Annual Biosolid Report is due February 19, of each year for the previous years land applied biosolids.  Part of this report is the submittal of the daily site logs, which have the date, time, and quantity gal-lb. N/acre land applied for each day-tank-batch land applied.  Site logs shall have a scaled map showing the site and the land application location that coincides with the daily site loading methods (truck spreader bar, irrigation cannon).  Daily records should clearly show the location of daily biosolid loading site log.

Annual Report shall have a signed copy of the certification statements for pathogen reduction, vector attraction reduction and biosolids has been land applied at approved agronomic loading.  Person signing statements should be the operator of record at the treatment plant.  The operator shall shown how the vector attraction reduction was met i.e., volatile solids reduction was achieved by time and temperature, the Van Kleeck equation filled out with digester records (MCRT), bench scale test, sour test or any other EPA approved alternative method appropriated for biosolid generated at your facility.  Certification of pathogen reduction is required and is satisfied by submittal of test results in the Annual Biosolid Report.  All the previous year's biosolids sampling and analysis that is required by the permit shall be included in CN's Annual Biosolid Report (in each year's annual report appendix).

VII Certification Statement

CN’s facility is capable of meeting their primary alternatives for achieving Class A or B biosolid pathogen and vector attraction reduction criteria.  Signed Class A and/or B biosolid and vector attraction certification statements shall accompany all biosolids that are land applied (attachment C).  For Class A or B biosolid annual biosolid analysis must be provided upon request.  Certification statements must also show conformance with nutrient and land application loading rates where applicable.

Attachment A:

Calculation of the % volatile solids reduction for the anaerobic digesters is to be based on comparison of a representative grab sample of total and volatile solids entering the digestion process  (a weighted blend of the primary and secondary clarifier solids) and a representative composite sample of the solids existing the sludge holding tanks.

Typically in the past we’ve used the Van Kleeck equation for digesters.  The assumption is that there is no grit accumulation in the digester.   This volatile solids equation assumes the fixed solids input equals the fixed solids output.   The Van Kleeck equation is appropriate if the digester decatante is low in total solids. The Van Kleeck equation can be used to calculate the volatile solids reduction for a digester that decants provided VSb equal VSd

FVSR:  Fractional Volatile Solids Reduction

FVSR = 1 - VSb  * (1-VSf) / VSf (1- VSb)

VSf	Feed Sludge Fractional Volatile Solid, (kg/kg)

VSb	Digested Sludge (digester bottom) Fractional Volatile Solids, (kg/kg)

VSd	Decantate Fractional Volatile Solids

For this equation to be valid VSb must equal VSd.

For digesters with decant withdrawal (decant high in solids) and no grit accumulation, where the volatile and fixed concentrations are known for all streams as well as the volumetric flow rates for the decant and digester sludge then the Approximate Mass Balance equation should be used.

FVSR:  Fractional Volatile Solids Reduction

FVSR = Fyb - Byb – Dyd  / Fyb

Fyb	(F)	Feed Sludge Volumetric Flow Rate (m3/d)

(yb)	Feed Sludge Volatile Solids Concentration (kg/ m3)

Byb	(B)	Digester Sludge (bottom) Volumetric Flow Rate (m3/d)

(Bb)	Digester Sludge (bottom) Volatile Solids Concentration (kg/ m3)

Dyd	(D)	Decantate Volumetric Flow Rate (m3/d)

(yd)	Decantate Volumetric Solids Concentration (kg/ m3)

.

Assumptions:  Fixed Solids and Volatile Flows Streams.

Attachment C:

“I certify, under penalty of law, that the pathogen requirements in [insert either 503.32(a) or 503.32(b)], the management practices in 503.14 and the vector attraction reduction requirements in [insert 503.33(b)(1) through 503.33(b)(10)] have been met.  This determination has been made under my direction and supervision in accordance with the system designed to ensure that qualified personnel properly gather and evaluate the information used to determine that the pathogen requirements and vector attraction reduction requirements have been met.  I also certify that all biosolids were land applied at the approved agronomic loading rate noted in the respective Department site authorization letter.  I am aware that there are significant penalties for false certification including the possibility of fine and imprisonment.”

Signature……………………………………….	Date…………………….