## Cl-, NH3 Limits
Facility Name: | Newberg STP |  |  |  | Attachment #10 | [5 empty] | Date: | 2004-03-19
Dilution Values? (Y/N) | Y | calculated |  |  | Summer data |  | Effluent | Stream | Mixed
Low Flow Dilution @ ZID = | 2.4 | * | [6 empty] | ZID | MZ
Low Flow Dilution @ MZ = | 28.5 | * |  |  |  | pH * = | 7.3 | 7.7 | 7.3937 | 7.6404 | ( 6.5-9 )
High Flow Dilution @ ZID = | * | * |  |  |  | Temp * = | 22.5 | 22 | 22.2083 | 22.0175 | ° C
High Flow Dilution @ MZ = | * | * |  |  |  | Alkalinity = | 75 | 25
[6 empty] | Salmonids Present? (Y/N) |  | y
| Summer | Winter |  |  |  | Fresh Water ? (Y/N) |  | y
Effluent Flow (MGD) = | 1 | 1 |  |  |  | Salinity | 0 | 20 | 11.6667 | 19.2982
7Q10 (CFS) = | * | * |  |  | Winter data
1Q10 (CFS) = | * | * |  |  |  | pH * = | * | * | * | * | ( 6.5-9 ) |  |  |  | Calculations | [7 empty] | Ammonia Calculations
% dilution at MZ = | 25 | 25 |  |  |  | Temp * = | * | * | * | * | ° C
% dilution at ZID = | 10 | 10 |  |  |  | Alkalinity = | * | * | [8 empty] | C | C |  | M
[6 empty] | Salmonids Present? (Y/N) |  | * | [8 empty] | h | h |  | o |  | M
[6 empty] | Fresh Water ? (Y/N) |  | *
[6 empty] | Salinity | * | * | * | *
[16 empty] | A | r | r | D | n |  | o | [12 empty] | R | R
[5 empty] | probability basis | 99% | [8 empty] | A | c | o | o | a | t | D | n | T | T | T | T | [8 empty] | A | A
[5 empty] | (for WLA multipliers) | [9 empty] | c | u | n | n | i | h | a | t | C | C | C | C | F | F | F | F |  |  |  |  | T | T
| WATER QUALITY | [13 empty] | u | t | i | i | l | l | i | h | A | A | A | A | P | P | P | P | F | F | F | F | I | I
| CRITERIA | [9 empty] | PERMIT LIMITS |  | PERMIT LIMITS |  | t | e | c | c | y | y | l | l | P | P | P | P | H | H | H | H | T | T | T | T | O | O
| 1 Hour | 4 Day | Back- | Allocations |  |  | # | Acute | Chronic | Min | 95% | 99% | 95% | 99% | e | [5 empty] | y | y | a | c | a | c | l | l | h | h | a | c | a | c | l | l
PARAMETER | (CMC) | (CCC) | ground | Acute | Chronic |  | Samples | LTA | LTA | LTA | Monthly | Daily | Monthly | Daily |  | u | u | u | s | s |  |  | l | l | h | h | a | c | a | c | l | l | h | h | c | c
| mg/l | mg/l | mg/l | mg/l | mg/l | CV | /Mo | mg/l | mg/l | mg/l | mg/l | mg/l | lb/day | lb/day | s | 1 | 4 | 1 | 2 | 2 | u | u
Low Flow Season
CHLORINE | 0.019 | 0.011 | 0 | 0.0456 | 0.3135 | 0.6 | 30 | 0.014639 | 0.16533 | 0.014639 | 0.017415 | 0.0456 | 0.14524 | 0.3803 | 0.55451 | -4.3778 | -1.8429 | -1.9535 | 0.30748 | 0.011929 | -4.3778 | -4.2301
AMMONIA | 11.6614 | 1.0769 | 0.6 | 27.1474 | 14.1908 | 0.6 | 4 | 8.7149 | 7.4839 | 7.4839 | 11.6177 | 23.3128 | 96.8918 | 194.4291 | 0.55451 | 2.0113 | 1.9697 | 1.859 | 0.30748 | 0.086178 | 1.859 | 1.9697 | A P a l: 20; A P c l: 15; P H l a: 1.6117; P H l c: 1.26; F T a l: 1; F T c l: 1.4125; I O l c: 17.4814
High Flow Season
CHLORINE | 0.019 | 0.011 | 0 | #VALUE! | #VALUE! | 0.6 | 30 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.55451 | #VALUE! | #VALUE! | #VALUE! | 0.30748 | 0.011929 | #VALUE! | #VALUE!
AMMONIA | #VALUE! | #VALUE! | 0.6 | #VALUE! | #VALUE! | 0.6 | 2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.55451 | #VALUE! | #VALUE! | #VALUE! | 0.30748 | 0.16551 | #VALUE! | #VALUE! | A P a h: 25; A P c h: 20; P H h a: 1; P H h c: 1; F T a h: 0.70795; F T c h: 1; I O l c: 16
NOTES : | Temperature must be between 0 and 30 ° C
pH must be between 6.5 and 9
AMMONIA is mg/l ammonia as N.
Saltwater Ammonia Criteria |  | (taken from Ambient Water Quality Criteria for Ammonia (Saltwater) 1989
For LIMITS Spreadsheet | Temp | pH | Salinity | Pressure | Molal Ionic Strength | pKa8 | % Unionized: | Unionized |  | Total NH3 |  | Total NH3 as N
| (deg C) | (su) | (ppt) | (ATM) | (not valid if >0.85): | @ 25 deg C |  | Acute | Chronic | Acute | Chronic | Acute | Chronic
[12 empty] | mg/L | mg/L
Summer ZID | 22.2083 | 7.3937 | 11.6667 | 1 | 0.23524 | #N/A | #N/A | 0.233 | 0.035 | #N/A | #N/A | #N/A | #N/A
Summer MZ | 22.0175 | 7.6404 | 19.2982 | 1 | 0.39217 | #N/A | #N/A | 0.233 | 0.035 | #N/A | #N/A | #N/A | #N/A
Winter ZID | * | * | * | 1 | #VALUE! | #N/A | #VALUE! | 0.233 | 0.035 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Winter MZ | * | * | * | 1 | #VALUE! | #N/A | #VALUE! | 0.233 | 0.035 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Other | 20 | 8.2 | 10 | 1 | 0.2013 | #N/A | #N/A | 0.233 | 0.035 | #N/A | #N/A | #N/A | #N/A
Other | 20 | 8.2 | 10 | 1 | 0.2013 | #N/A | #N/A | 0.233 | 0.035 | #N/A | #N/A | #N/A | #N/A
Calculation of pH of a mixture of two flows.
Based on the procedure in EPA's DESCON program (EPA, 1988. Technical
Guidance on Supplementary Stream Design Conditions for Steady State
Modeling. USEPA Office of Water, Washington D.C.)
|  |  |  | Summer |  | Winter
INPUT |  |  |  | ZID | MZ | ZID | MZ
1. DILUTION FACTOR AT MIXING ZONE/ZID BOUNDARY |  |  |  | 2.4 | 28.5 | * | *
1. UPSTREAM/BACKGROUND CHARACTERISTICS
Temperature (deg C): |  |  |  | 22 | 22 | * | *
pH: |  |  |  | 7.7 | 7.7 | * | *
Alkalinity (mg CaCO3/L): |  |  |  | 25 | 25 | * | *
2. EFFLUENT CHARACTERISTICS
Temperature (deg C): |  |  |  | 22.5 | 22.5 | * | *
pH: |  |  |  | 7.3 | 7.3 | * | *
Alkalinity (mg CaCO3/L): |  |  |  | 75 | 75 | * | *
OUTPUT
1. IONIZATION CONSTANTS
Upstream/Background pKa: |  |  |  | 6.3685 | 6.3685 | #VALUE! | #VALUE!
Effluent pKa: |  |  |  | 6.3652 | 6.3652 | #VALUE! | #VALUE!
2. IONIZATION FRACTIONS
Upstream/Background Ionization Fraction: |  |  |  | 0.95547 | 0.95547 | #VALUE! | #VALUE!
Effluent Ionization Fraction: |  |  |  | 0.89589 | 0.89589 | #VALUE! | #VALUE!
3. TOTAL INORGANIC CARBON
Upstream/Background Total Inorganic Carbon (mg CaCO3/L): |  |  |  | 26.1653 | 26.1653 | #VALUE! | #VALUE!
Effluent Total Inorganic Carbon (mg CaCO3/L): |  |  |  | 83.7159 | 83.7159 | #VALUE! | #VALUE!
4. CONDITIONS AT MIXING ZONE BOUNDARY
Temperature (deg C): |  |  |  | 22.2083 | 22.0175 | #VALUE! | #VALUE!
Alkalinity (mg CaCO3/L): |  |  |  | 45.8333 | 26.7544 | #VALUE! | #VALUE!
Total Inorganic Carbon (mg CaCO3/L): |  |  |  | 50.1447 | 28.1846 | #VALUE! | #VALUE!
pKa: |  |  |  | 6.3671 | 6.3684 | #VALUE! | #VALUE!
pH at Mixing Zone/ZID Boundary: |  |  |  | 7.3937 | 7.6404 | #VALUE! | #VALUE!
Note on B3: Enter "Y" if dilution is known, and enter dilution values for ZID and MZ. If dilution is not known enter "N" and enter information for 7Q10, 1Q10, % dilution, and effluent flow below.
Note on B6: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on B7: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on B10: Effluent flow rate is necessary to calculate mass load limits
Note on B11: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on B12: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on C3: This is the calculated dilution based on the 7Q10, 1Q10 etc. data entered below. This calculated dilution will be used when "N" is entered into the adjacent box.
Note on C10: Effluent flow rate is necessary to calculate mass load limits
Note on C11: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on C12: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on G10: Enter salinity data if you answered "N" to Fresh Water (cell I9).
Note on G17: Enter salinity data if you answered "N" to Fresh Water (cell I18).
Note on G19: A probability basis for the WLA multipliers of 99% is Department protocol.
Note on G47: DEQ: Whitfield model "B"
Note on H12: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on H13: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on H14: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on H17: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on I12: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on I13: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on I14: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on I15: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on I16: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on I17: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on I47: DEQ: from EPA 440/5-88-004
Note on J12: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on J13: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on J17: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on K12: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on K13: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on K17: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on L23: Percentile may be changed if rationale is provided
Note on M23: Percentile may be changed if rationale is provided
Note on M47: DEQ: Total as N is what permit limits are based upon

## Metals Limits
Facility Name: | Enter Name Here | [9 empty] | Date: | 2002-08-12
Calculations
Dilution Values? (Y/N) | Y | calculated |  | Hardness | mg/L CaCO3
Dilution @ ZID | 1 | * |  | Effluent | 25 | (Hardness values should
Dilution @ MZ | 1 | * |  | Stream | 25 | be >25 and <400 mg/L)
Facility Effluent Flow | 1 | MGD |  | Mixed | calculated
If no dilution values enter info below |  |  |  | ZID | 25
7Q10 | * | CFS |  | MZ | 25
1Q10 | * | CFS
% dilution at ZID | 10 | % |  |  | probability basis | 99%
% dilution at MZ | 25 | % |  |  | (for WLA multipliers)
Fresh Water? (Y/N) | n
[16 empty] | S | S
| WATER QUALITY | [9 empty] | APPLICABLE PERMIT LIMITS |  |  |  | S | I | I
| CRITERIA | [9 empty] | CONCENTRATION |  | MASS |  | I | G | G
| 1 Hour | 4 Day | Back- | Allocations |  |  | # | Acute | Chronic | Min | 95% | 99% | 95% | 99% | G | M | M
PARAMETER | (CMC) | (CCC) | ground | Acute | Chronic |  | Samples | LTA | LTA | LTA | Monthly | Daily | Monthly | Daily | M | A | A
| µg/l | µg/l | µg/l | µg/l | µg/l | CV | /Mo | µg/l | µg/l | µg/l | µg/l | µg/l | lb/day | lb/day | A | 4 | n
ALUMINUM † | -- | -- | * | -- | -- | 0.6 | 2 | -- | -- | * | -- | -- | -- | -- | 0.55451 | 0.29356 | 0.40683
ARSENIC V * | 2319 | 13 | * | 2319 | 13 | 0.6 | 2 | 744.4484 | 6.8559 | * | -- | -- | -- | -- | 0.55451 | 0.29356 | 0.40683
ARSENIC III | 69 | 36 | * | 69 | 36 | 0.6 | 2 | 22.1505 | 18.9857 | * | -- | -- | -- | -- | 0.55451 | 0.29356 | 0.40683
CADMIUM + | 43 | 9.3 | * | 43 | 9.3 | 0.6 | 2 | 13.8039 | 4.9046 | * | -- | -- | -- | -- | 0.55451 | 0.29356 | 0.40683
CHROMIUM VI | 1100 | 50 | * | 1100 | 50 | 0.6 | 2 | 353.1234 | 26.369 | * | -- | -- | -- | -- | 0.55451 | 0.29356 | 0.40683
CHROMIUM III +^ | 10300 | -- | * | 10300 | -- | 0.6 | 2 | 3306.5192 | -- | * | -- | -- | -- | -- | 0.55451 | 0.29356 | 0.40683
TOTAL CHROMIUM † | 11400 | -- | * | 11400 | -- | 0.6 | 2 | 3659.6426 | -- | * | -- | -- | -- | -- | 0.55451 | 0.29356 | 0.40683
COPPER + | 2.9 | 2.9 | * | 2.9 | 2.9 | 0.6 | 2 | 0.93096 | 1.5294 | * | -- | -- | -- | -- | 0.55451 | 0.29356 | 0.40683
CYANIDE | 1 | 1 | * | 1 | 1 | 0.6 | 2 | 0.32102 | 0.52738 | * | -- | -- | -- | -- | 0.55451 | 0.29356 | 0.40683
FLUORIDE † | -- | -- | * | -- | -- | 0.6 | 2 | -- | -- | * | -- | -- | -- | -- | 0.55451 | 0.29356 | 0.40683
IRON ‡ | -- | -- | * | -- | -- | 0.6 | 2 | -- | -- | * | -- | -- | -- | -- | 0.55451 | 0.29356 | 0.40683
LEAD + | 140 | 5.6 | * | 140 | 5.6 | 0.6 | 2 | 44.943 | 2.9533 | * | -- | -- | -- | -- | 0.55451 | 0.29356 | 0.40683
MERCURY | 2.1 | 0.025 | * | 2.1 | 0.025 | 0.6 | 2 | 0.67414 | 0.013184 | * | -- | -- | -- | -- | 0.55451 | 0.29356 | 0.40683
NICKEL + | 75 | 8.3 | * | 75 | 8.3 | 0.6 | 2 | 24.0766 | 4.3773 | * | -- | -- | -- | -- | 0.55451 | 0.29356 | 0.40683
SILVER + | 2.3 | -- | * | 2.3 | -- | 0.6 | 2 | 0.73835 | -- | * | -- | -- | -- | -- | 0.55451 | 0.29356 | 0.40683
ZINC + | 95 | 86 | * | 95 | 86 | 0.6 | 2 | 30.497 | 45.3546 | * | -- | -- | -- | -- | 0.55451 | 0.29356 | 0.40683
Custom | * | * | * | * | * | 0.6 | 2 | * | * | * | * | * | * | * | 0.55451 | 0.29356 | 0.40683
[15 empty] | 0 | 0 | #DIV/0!
[15 empty] | 0 | 0 | #DIV/0!
[15 empty] | 0 | 0 | #DIV/0!
[15 empty] | 0 | 0 | #DIV/0!
[15 empty] | 0 | 0 | #DIV/0!
[15 empty] | 0 | 0 | #DIV/0!
NOTES :
All units in ug/L
* Insufficient data to develop criteria; value presented is the Lowest Observed Effect Level
‡ - No acute standard. The CMC is estimated as 2X the CCC.
† - Not DEQ Criteria
^ Marine acute criterion has insufficient data to develop criteria; value = LOEL
[19 empty] | Priority |  | Aquatic Life |  |  |  | Human Health
[19 empty] | Priority Pollutant | Carcinogen | Fresh Water |  | Marine Water |  | Water & Fish | Fish Consumption | Drinking
[21 empty] | Acute | Chronic | Acute | Chronic | Ingestion | Only | Water MCL
[18 empty] | ALUMINUM † | N | N | 750 | 87 | -- | -- | -- | -- | --
[18 empty] | ARSENIC V * | Y | Y | 850 | 48 | 2319 | 13 | -- | -- | --
[18 empty] | ARSENIC III | Y | Y | 360 | 190 | 69 | 36 | -- | -- | --
[18 empty] | CADMIUM + | Y | N | 0.8211 | 0.38192 | 43 | 9.3 | 10 | -- | 10
[18 empty] | CHROMIUM VI | Y | N | 16 | 11 | 1100 | 50 | 50 | -- | 50
[18 empty] | CHROMIUM III +^ | N | N | 557.9444 | 66.5038 | 10300 | -- | 170000 | 3433000 | 50
[18 empty] | TOTAL CHROMIUM † | N | N | 573.9444 | 77.5038 | 11400 | -- | 170050 | 3433000 | 100
[18 empty] | COPPER + | Y | N | 4.801 | 3.6166 | 2.9 | 2.9 | -- | -- | --
[18 empty] | CYANIDE | Y | N | 22 | 5.2 | 1 | 1 | 200 | -- | --
[18 empty] | FLUORIDE † | N | N | 2000 | 1000 | -- | -- | -- | -- | --
[18 empty] | IRON ‡ | N | N | 2000 | 1000 | -- | -- | 300 | -- | --
[18 empty] | LEAD + | Y | N | 13.98 | 0.54478 | 140 | 5.6 | 50 | -- | 50
[18 empty] | MERCURY | Y | N | 2.4 | 0.012 | 2.1 | 0.025 | 0.144 | 0.146 | 2
[18 empty] | NICKEL + | Y | N | 438.9427 | 48.797 | 75 | 8.3 | 13.4 | 100 | --
[18 empty] | SILVER + | Y | N | 0.37399 | 0.12 | 2.3 | -- | 50 | -- | 50
[18 empty] | ZINC + | Y | N | 36.1528 | 32.7451 | 95 | 86 | -- | --
NOTES :
All units in ug/L
* Insufficient data to develop criteria; value presented is the Lowest Observed Effect Level
‡ - No acute standard. The CMC is estimated as 2X the CCC.
† - Not DEQ Criteria
^ Marine acute criterion has insufficient data to develop criteria; value = LOEL
Note on B3: Enter "Y" if dilution is known, and enter dilution values for ZID and MZ. If dilution is not known enter "N" and enter information for 7Q10, 1Q10, and % dilution
Note on B6: Effluent flow rate is necessary to calculate mass load limits
Note on C3: This is the calculated dilution based on the 7Q10, 1Q10 etc. data entered below. This calculated dilution will be used when "N" is entered into the adjacent box.
Note on G10: A probability basis for the WLA multipliers of 99% is Department protocol as recommended by the TSD.
Note on L16: Percentile may be changed if rationale is provided
Note on M16: Percentile may be changed if rationale is provided