National Pollutant Discharge Elimination System PERMIT EVALUATION AND FACT SHEET

March 29, 2004

Oregon Department of Environmental Quality

Western Region

750 Front St NE, Suite 120

Salem OR 97301

(503) 378-8240

| Permittee: | City of Newberg |
| --- | --- |
|  | 414 East First Street |
|  | Newberg, OR 97132 |
|  | File Number: 102894 |
| Current Permit: | NPDES Permit Number: 100988 |
|  | EPA Reference Number: OR003235-2 |
|  | Issue Date: September 30, 1992 |
|  | Expiration Date: September 30, 1997 |
| Source Information: | Newberg Wastewater Treatment Facilities |
|  | 2301 Wynooski Road |
|  | Newberg, Oregon |
|  | Latitude 450 17’ 9” North, Longitude 1220 57’ 14” West |
| Source Contact: | Howard Hamilton, Utilities Superintendent |
|  | Phone: 503-537-1211 |
| Proposed Action: | #### NPDES Major Domestic Permit Renewal |
|  | #### Application Number: 992393 |
|  | #### Date Received: April 3, 1997 |
| Permit Writer: | #### Mark E. Hamlin |
|  | #### Phone: 503-378-8240, extension 239 |

# INTRODUCTION

The City of Newberg owns and operates a secondary wastewater treatment facility located in Newberg, Oregon (see Attachment #1).  Municipal wastewater is treated and discharged to the Willamette River in accordance with National Pollutant Discharge Elimination System (NPDES) Permit number 100988.  The Permit for the facility was issued on September 30, 1992 and expired on September 30, 1997.

The Department received a renewal application on April 3, 1997.  The permit shall not be deemed to expire until final action has been taken on the renewal application as per Oregon Administrative Rules (OAR) 340-045-0040.  A renewal permit is necessary to discharge to state waters pursuant to provisions of Oregon Revised Statutes (ORS) 468B.050 and the Federal Clean Water Act.  The Department proposes to renew the permit.  This permit evaluation report describes the basis and methodology used in developing the permit.

This permit is a joint federal and state permit and subject to federal and state regulations.  The Clean Water Act, the Code of Federal Regulations, and numerous guidelines of the Environmental Protection Agency provide the federal permit requirements.  The Oregon Revised Statutes, Oregon Administrative Rules, and policies and guidelines of the Department of Environmental Quality provide the state permitting requirements.

# Facility Description

The treatment facility serves the entire City of Newberg.  No service is currently provided outside the City limits.  The facilities (see Attachment #2) consist of a raw influent pump station, headworks, activated sludge oxidation ditches, secondary clarifiers, chlorine disinfection, dechlorination, effluent outfall and biosolids composting.  The facility was placed into operation in 1987.

The raw sewage pump station contains 4 centrifugal pumps that pump all wastewater received to the headworks.  The headworks currently consist of two influent channels with one mechanically cleaned bar screen and one bypass channel.  The facility has an aerated grit removal system with one cyclone grit classifier.  The headworks is being upgraded to three influent channels with two mechanically cleaned bar screens, one bypass channel and two cyclone grit classifier with washer/compactors.

Secondary treatment is provided by two oxidation ditches and three circular 80 foot diameter, center feed secondary clarifiers.  Influent flows above 18 million gallons per day (MGD) are diverted to an equalization basin for peak flow storage. All flow is eventually treated in the secondary system.

Disinfection is performed with chlorine gas.  Treated and disinfected effluent is dechlorinated with bisulfite prior to flow measurement and discharge.  The outfall is a single port diffuser in the Willamette River at river mile 49.7.

The facility is unmanned at night, but has 24 hour monitoring of alarms through telemetry through the treatment plant.  The facility also has redundant power and some standby electric generation at the treatment plant.  Some lift stations have standby power generators while others are served by mobile generators.

Only minor modifications were made to the facility during this permit cycle.  The facility was originally designed to compost biosolids but was unable due to a structural failure.  During this permit cycle, the composting facilities were repaired and lime stabilization of biosolids was discontinued.  In addition, dechlorination of the effluent was instituted toward the end of 1998.

The existing permit identifies the treatment facility ADWF capacity as 4.0 MGD.  During the last three dry seasons (2001, 2002 and 2003 from May 1 through October 31), the plant received an average of 1.78 MGD or 45 percent of its hydraulic capacity.  The plant’s design organic capacity is 7,200 pounds CBOD per day and 5,000 pounds per day of TSS.  Summer plant loading averaged 39 percent of the CBOD organic capacity and 78 percent of the TSS capacity.  The maximum CBOD loading (48 percent) occurred during October 2001 while the maximum TSS loading (98 percent) occurred during May 2003.

The plant's design AWWF is 6.5 MGD.  Monthly average plant flows during the winter are weather dependant.  During the last two wet weather periods (2001/02 and 2002/2003 from November 1 though April 30), the plant received an average of 4.16 MGD or 64 percent of its winter hydraulic capacity.  Winter plant loading averaged 41 percent of the CBOD organic capacity and 84 percent of the TSS capacity.  The maximum CBOD loading (54 percent) and the maximum TSS loading (119 percent) occurred during November 2001.  (The 2000/01 wet weather period occurred during a severe drought and plant flow is not considered representative.)

With the new headworks, peak instantaneous hydraulic capacity will be rated at 27 MGD.

## Biosolids Management and Utilization

All waste sludge must be managed in accordance with the Department approved Biosolids Management Plan to ensure compliance with the federal biosolids regulations (40 CFR Part 503) and the state rules (OAR 340-050).  The permittee’s biosolids management plan was originally approved June 22, 1989.  An updated management plan is proposed to be approved with this permit action.

The biosolids consistently meet the vector attraction and Class A pathogen reduction requirements in 40 CFR Part 503.  After treatment necessary to comply with vector attraction and pathogen reduction requirements, the Class A biosolids can be sold, given away or beneficially land applied with few additional restrictions.  The updated plan also allows land application of Class B biosolids (should it become necessary or desirable in the future).  The site selection criteria for land application include all of Oregon.  The Department is proposing to approve the plan (see Attachment #3).

Sludge from the secondary clarifiers and dredging from the oxidation ditches (when necessary) are pumped through the solid treatment processes.  Sludge can be stored in two 80,000 gallon sludge storage tanks or directly thickened with dissolved air floatation and two 2 meter belt filter presses.  Thickened sludge is mixed with sawdust and enters one of two compost reactor vessels to produce Class A biosolids. Each reactor tunnel is 18 feet wide, 12 feet high and 66 feet long.

At maximum loading each tunnel has a detention time of approximately 14 days. All batches must meet the minimum vector attraction reduction requirement of aerobic treatment of the sludge for at least 14 days at over 40 degrees C with the average temperature of over 45 degrees C.

The City uses composting time and temperature to demonstrate compliance with vector attraction requirements.  The compost pile must be over 40 degrees C for at least 14 days with the average temperature of over 45degrees C.

The City uses fecal coliform monitoring of the compost and Alternative 5 of Processes to Further Reduce Pathogens (PFRP) to demonstrate compliance with Class A pathogen reduction requirements.  The compost pile must be at a minimum pile temperature of 55 degrees C for three consecutive days.  The compost (Class A biosolids) is sold to interested parties for home and commercial use.  The City produces approximately 570 metric dry tons of composted biosolids per year.

If Class B biosolids are produced, the biosolids may be land applied.  However, the City no longer has authorized land application sites.  Any future land application sites must conform to the site selection criteria in the Biosolids Management Plan and must be located in Oregon.

The City conducts quarterly chemical testing of removed sludge (see Table 1).  Testing includes analyses for nutrients and 11 metals.  Based on the analyses, there are no known potential impacts from the current land application program.

Table 1 – Biosolids Metals Results for December 2003

| Parameter | Mg/dry Kg | §503.13 Table 3 Limit | Parameter | Mg/dry Kg | §503.13 Table 3 Limit |
| --- | --- | --- | --- | --- | --- |
| Arsenic | 5.7 | 41 mg/kg | Molybdenum | 3.2 | No limit |
| Cadmium | 1.5 | 39 mg/kg | Nickel | 13.7 | 420 mg/kg |
| Chromium | 15.6 | No limit | Selenium | 4.4 | 100 mg/kg |
| Copper | 150 | 1500 mg/kg | Silver | 8.92 | No limit |
| Lead | 21.2 | 300 mg/kg | Zinc | 442 | 2800 mg/kg |
| Mercury | 0.77 | 17 mg/kg |  |  |  |

The facility accepts septage from local septic pumpers on a regular basis.

## Inflow and Infiltration (I/I)

The plant received an average of 1.78 MGD during the last three dry seasons while it received an average of 4.16 MGD during the last two wet weather periods.  The wet period average flow is about 2.3 times the dry period average flow.  The maximum daily flow of 14.9 MGD occurred in January 2003.   The plant experiences significant but not extreme levels of I/I.

Collection system overflows can result from catastrophic failure of the treatment plant or pump station or high flows due to storm events.  According to the rules (OAR 340-041-0009(6) and (7)), the City is prohibited from discharging raw sewage during the period of November 1 through May 21, except during a storm event greater than the one-in-five-year, 24-hour duration storm.  In addition, they cannot discharge raw sewage during the period of May 22 through October 31, except during a storm event greater than the one-in-ten-year, 24-hour duration storm.  The City of Newberg can comply with these rules.

The current permit contains Carbonaceous Biochemical Oxygen Demand (CBOD5) and total suspended solids (TSS) removal efficiency limits of 85 percent.  The City has had no violations of the removal efficiency limits.  The Department is proposing to retain the existing limits.

## Industrial Pretreatment

The City of Newberg has a Department approved industrial pretreatment program.  Federal and state pretreatment requirements were included in the previous NPDES permit for this facility.  However, the City’s industrial pretreatment program has been inactive since the last significant industry closed.  The requirement to implement an industrial pretreatment program could be deleted from the permit but the City wishes to retain their program in order to attract new significant or categorical industries.  The City currently does not permit any industrial users.

A technical assistance inspection of the City’s Industrial Pretreatment Program was conducted on October 2, 2003 by DEQ.  The primary focus of the visit was to evaluate the status of the City’s inactive program.  As a result of the technical assistance visit, the Department determined that the City did not have the procedures necessary to adequately implement a pretreatment program.

The proposed permit contains Schedule C compliance conditions for developing the necessary program procedures.  The industrial pretreatment program would have to be complete and reactivated prior to the connection of a new significant or categorical industry.  Schedule B of the proposed permit contain the monitoring requirements normally included with a pretreatment program.  Schedule E includes the requirements for implementation of an industrial pretreatment program.  However, full implementation of the program is delayed until after Department approval of the program procedures required by the Schedule C compliance conditions.

## Groundwater Issues

The treatment plant is constructed entirely of impervious structures.  It is not anticipated that the treatment process and discharge to surface waters will cause groundwater impacts.  Schedule A of the proposed permit prohibits adverse impacts to groundwater.  A condition in Schedule D states that no groundwater evaluations will be required during this permit cycle.

## Stormwater Issues

General NPDES permits for stormwater are required for wastewater treatment facilities with a design flow of greater than 1 MGD if stormwater is collected and discharge from the plant site.  Because this facility discharges stormwater from the plant site, a separate stormwater permit is necessary.  This facility has been assigned a separate 1200-Z permit that regulates the discharge of stormwater.

## Outfalls

The proposed NPDES Permit allows the treatment facility to discharge treated effluent into the Willamette River approximately one-third mile southwest of the plant at River Mile 49.7.  Treated, disinfected and dechlorinated effluent is discharged through an outfall pipe to an outfall in the Willamette River.

Two emergency overflow points are identified in the current permit.  The proposed permit contains the same emergency overflow points.  Their use is restricted to storm events as allowed under OAR 340-041-0120(13) and (14) and instances of upset as defined in the General Conditions.  During the current permit period, the collection system has overflowed on rare occasions.

## Mixing Zone Analysis

Federal regulations (40 CFR 131.13) allow for the use of mixing zones, also known as “allocated impact zones”.  When using mixing zones acute toxicity to drifting organisms must be prevented and the integrity of the waterbody as a whole may not be impaired.  Mixing zones allow the initial mixing of waste and receiving water, but are not designed to allow for treatment.  EPA does not have specific regulations pertaining to mixing zones.  Each state must adopt its own mixing zone regulations that are subject to review and approval by EPA.  In States that lack approved mixing zone regulations, ambient water quality standards must be met at the end of the pipe.

The Department has adopted the two-number aquatic life criteria and developed mixing zone regulations with respect to that.  The regulations are primarily narrative and essentially require the permit writer to use best professional judgment in establishing the size of the mixing zone.  Based on EPA guidance and the Department’s mixing zone regulations, two mixing zones may be developed for each discharge that reflect acute and chronic effects: 1) The acute mixing zone, also known as the “zone of initial dilution” (ZID), and 2) the chronic mixing zone, usually referred to as “the mixing zone”.  The acute mixing zone is designed to prevent lethality to organisms passing through the ZID.  The chronic mixing zone is designed to protect the integrity of the entire water body as a whole.  The allowable size of the mixing zone should be based upon the relative size of the discharge to the receiving stream, the beneficial uses of the receiving stream, location of other discharges to the same water body, location of drinking water intakes, and other considerations.  More specific guidance is available from EPA regarding criteria used in appropriately sizing a ZID.  Primarily the ZID must be designed to prevent lethality to drifting organisms.

The Department’s mixing zone regulations state the mixing zone must be less than the total stream width as necessary to allow passage of fish and other aquatic organisms.  Early recommendations regarding the size of the zone of passage originated from the Department of Interior (1968).  They recommended a zone of passage of 75 percent of the cross-sectional area and/or volume of flow of the receiving stream.  Based on this recommendation, the Department’s standard practice is to allow no more than 25 percent of the stream flow for mixing zones.

The current permit provides for a mixing zone that consists of that portion of the Willamette River contained within a band extending out seventy five (75) feet from the west bank of the river and extending from a point fifteen (15) feet upstream of the outfall to a point one hundred fifty (150) feet downstream from the outfall. The Zone of Immediate Dilution (ZID) is defined as that portion of the allowable mixing zone that is within fifteen (15) feet of the point of discharge.  The Department proposes to retain the existing mixing zone.

## Receiving Stream Water Quality

The City’s discharge is to the Willamette River at River Mile 49.7.  The discharge is within the Willamette basin and Middle Willamette sub-basin.  The designated beneficial uses of the receiving stream are: public and private domestic water supply, industrial water supply, irrigation, livestock watering, fish and aquatic life (including salmon and steelhead migration corridor), wildlife and hunting, fishing, boating, water contact recreation, aesthetic quality and hydro Power.  The water quality standards for the Willamette Basin (OAR 340-041) were developed to protect the beneficial uses of the basin.

The Willamette River is included on the Department’s List of Water Quality Limited Water Bodies (also called the 303(d) List) as water quality limited for the following parameters:

| Record | Waterbody | R.M. | Parameter | Season | Criteria |
| --- | --- | --- | --- | --- | --- |
| 6038 | Willamette River | 24.8 to 54.8 | Fecal Coliform | Winter/Spring/Fall | Geometric Mean of 200, No more than 10%>400 |
| 9220 | Willamette River | 24.8 to 54.8 | PCB | Year Around | public health advisories |
| 9221 | Willamette River | 24.8 to 54.8 | Aldrin | Year Around | public health advisories |
| 9223 | Willamette River | 24.8 to 54.8 | Dieldrin | Year Around | public health advisories |
| 9224 | Willamette River | 24.8 to 54.8 | DDT | Year Around | public health advisories |
| 9225 | Willamette River | 24.8 to 54.8 | DDT Metabolite (DDE) | Year Around | public health advisories |
| 8381 | Willamette River | 24.8 to 54.8 | Iron | Year Around | Table 20 |
| 5864 | Willamette River | 24.8 to 54.8 | Temperature | Summer | Rearing: 17.8 C |
| 7087 | Willamette River | 24.8 to 54.8 | Mercury | Year Around | public health advisories |
| 6125 | Willamette River | 24.8 to 54.8 | Biological Criteria |  | Waters of the state shall be of sufficient quality |

A Total Maximum Daily Load (TMDL) addressing many of the water quality limited parameters should be issued in 2004.  The TMDL will likely assign Waste Load Allocations (WLA) to this source.  The WLA may be incorporated into the permit by modification or during the next permit renewal.

Fecal Coliform Issues

As stated, fecal bacterial levels exceed the standard during fall, winter and spring but no TMDL has been developed.  The NPDES Permit represents the Bacteria Control Management Plan for the City of Newberg.  As long as the discharge remains in compliance with the permit’s bacteria limits, the treated effluent discharge will not have a negative impact on the water quality of the Willamette River with respect to bacteria.  The sewage collection system has experienced minimal raw sewage overflows during the last several years.  Those overflows may have contributed slightly to the ambient fecal bacteria violations.

Temperature Issues

Water temperature affects the biological cycles of aquatic species and is a critical factor in maintaining and restoring healthy salmonid populations throughout the state.  It is the policy of the Environmental Quality Commission (EQC) to protect aquatic ecosystems from adverse temperature changes caused by anthropogenic activities.  The purpose of the temperature criteria listed in OAR 340-041-0028 is to protect designated beneficial uses that are temperature sensitive, including salmonids in waters of the State.

The Department utilizes Fish Use Designation and Salmon and Steelhead Spawning Use Designations maps to identify applicable temperature criteria for each basin.  The Willamette Basin maps are contained in OAR 340-041, Figures 340A and 340B, respectively.  According to the approved use designation maps, the Willamette River is designated as a migration corridor at this location.  Salmon and steelhead spawning is not a designated use.  Therefore, the applicable numeric temperature criteria is 20 C during the entire year.

The Department’s List of Water Quality Limited Water Bodies (also called the 303(d) List) for 2002 indicates the Willamette River is water quality limited for temperature during the summer.  However, the basis of that listing was violation of the old 64 F numeric criteria.  This evaluation assumes the Willamette River will continue to be included on future 303(d) lists for violation of the 20 C during the summer.

Prior to the completion of a temperature TMDL, each NPDES point source that discharges into a temperature water quality limited water is allowed a “Human Use Allowance”.  Each point source may cause the temperature of the water body to increase up to 0.3 degrees Celsius above the applicable criteria after mixing with either twenty five (25) percent of the stream flow, or the mixing zone, whichever is more restrictive.

Based on the existing discharge, the Department calculated in-stream temperature increases (using the existing facility design flow and maximum effluent temperatures) by two separate methods as required by rule (OAR 340-041-0028(12)(b)):

- Based on 25 percent of the 7Q10 stream flow (see Attachment 4a)

- Based on the estimated dilution achieved in the mixing zone at 7Q10 stream flow (see Attachment 4b)

Because the in-stream temperature increase is significantly smaller than the allowable increase, this facility has no reasonable potential to violate the temperature standard.  Therefore, a summer period Excess Thermal Load limit has not been included in this permit.

A similar evaluation was performed for the winter period (see Attachments 5a and 5b).  There was no reasonable potential for this facility to violate the temperature standard and no winter period Excess Thermal Load limit was included in this permit.

The permit may be reopened and a maximum allowable thermal load limit included when more accurate temperature data becomes available.  If the Total Maximum Daily Load (TMDL) for temperature for this sub-basin assigns a Waste Load Allocation (WLA) to this source, this permit may be re-opened to establish new thermal load limits and/or new temperature conditions or requirements.

Mercury Issues

The Department has no information about potential discharges of mercury by the permittee.  As stated, a TMDL addressing mercury should be issued in 2004.  The TMDL will likely require many sources to obtain a General NPDES Permit addressing mercury issues.  The General Permit may require monitoring and implementation of Best Management Practices (BMP).  In this permit, the Department proposes to require quarterly monitoring for mercury during the first year after permit issuance.  Monitoring for mercury must be performed in accordance with EPA Method 1631.  If the Department determines that there is an impact from the effluent for mercury, the permit may be modified to include limitations, additional monitoring or other requirements.

Iron Issues

The TMDL to be issued in 2004 will not address iron.  The Department does not have any information concerning the discharge of iron from this source.  The proposed permit requires the City to monitor the effluent for iron monthly for one year after permit issuance.  This monitoring will allow the Department to determine if iron in the discharge has a reasonable potential for causing or contributing to water quality standard violations.  The Department may require additional monitoring or reopen the permit to include new limits, conditions or requirements if it is determined that this discharge causes or contributes to the violations of the instream iron criteria.

Other Toxics (PCB, Aldrin, Dieldrin, DDT, DDE)

The TMDL to be issued in 2004 will not address these pollutants but it is not likely this discharge is a significant source of these pollutants.  However, the Department does not have any information concerning the discharge of these pollutants under this permit.  Therefore, the proposed permit includes the pesticide fraction in the annual monitoring of priority pollutants in Schedule B.

The Department is not aware of any other water quality violations that may be attributable to this source.  The Department is scheduled to develop a TMDL by 2004 that will determine the corrective actions necessary to bring the Willamette River back into compliance.  The TMDL may assign pollutant WLA to this point source discharge.  This permit may be reopened to incorporate any WLA.

# PERMIT HISTORY

## Previous Permit Actions

The Department issued NPDES Permit #100988 on September 30, 1992.  Because this was a new facility, this is the only NPDES Permit for this facility.  (The City’s previous treatment facility was at a different location and had a separate NPDES permit.)  The Permit was issued for discharge to the Willamette River at river mile 49.7.  The plant has a design dry weather average flow of 4.0 MGD.

The CBOD5 and TSS concentration and mass limits vary depending upon season.  Limits were also established for CBOD5 and TSS removal efficiency, pH, fecal coliform and total chlorine residual.  A mixing zone and Zone of Immediate Dilution (ZID) were established.  Two emergency discharge points were identified.

The permit was modified on March 24, 1997 to revise the total chlorine residual limitation and the mixing zone definition.  The Department received renewal application number 991591 on December 31, 1997.  The permit shall not be deemed to expire until final action has been taken on the renewal application.  The permit expired on September 30, 1997.

An Antidegradation Review was completed with a recommendation to proceed with this permit action (see Attachment #6).

## Current Permit Limits

Schedule A contains the effluent limits for the treatment facility.  Some limits are dependent upon the season (summer and winter) while others are year-round.  The current permit limits are as follows:

Outfall 001 – Treated Effluent

(1)	May 1 - October 31:

| Parameter | Average Effluent Concentrations Monthly Weekly | Monthly Average lb/day | Weekly Average lb/day | Daily Maximum lbs |
| --- | --- | --- | --- | --- |
| CBOD5 | 10 mg/L 15 mg/L | 330 | 500 | 660 |
| TSS | 10 mg/L 15 mg/L | 330 | 500 | 660 |

(2)	November 1 - April 30:

| Parameter | Average Effluent Concentrations Monthly Weekly | Monthly Average lb/day | Weekly Average lb/day | Daily Maximum lbs |
| --- | --- | --- | --- | --- |
| CBOD5 | 25 mg/L 40 mg/L | 1400 | 2200 | 2800 |
| TSS | 30 mg/L 45 mg/L | 1600 | 2400 | 3200 |

(3)	Other Parameters:

| Other parameters (year-round) | Limitations |
| --- | --- |
| Fecal Coliform | Shall not exceed 200 per 100 mL monthly geometric mean nor 400 per 100 mL weekly geometric mean |
| pH | Shall be within the range of 6.0 - 9.0 |
| CBOD5 and TSS Removal Efficiency | Shall not be less than 85% monthly average. |
| Total Residual Chlorine | Shall not exceed a daily average of 0.05 mg/L |

Schedule A also defines a mixing zone for Outfall 001 and includes restrictions on discharges from the emergency overflow outfalls.

## Compliance History

This facility was last inspected June 26, 2003 and was found to be operating in compliance with the permit.  The following Notices of Noncompliance (NON) have been issued for violations documented at this facility since 1994:

| Date of Enforcement Action | Type of Enforcement Action | Description |
| --- | --- | --- |
| 3/17/1998 | Class 2 NON | Exceeding Permit Discharge Limits & Failure To Obtain Departmental Approval Of Plans |

On October 2, 1992, the City of Newberg was issued a Stipulation and Final Order (SFO) that required the City to provide upgraded facilities to comply with the permit limit on total residual chlorine (TRC).  The SFO also contained an interim TRC limit based on the capabilities of the wastewater facilities.  The SFO was modified to extend the compliance deadline for providing upgraded facilities. However, the interim limit was not extended and expired on December 31, 1995.  At that time, the City could consistently comply with the interim TRC limit contained in the NPDES Permit.

On March 24, 1997, the NPDES Permit was modified to include a much lower, final TRC limit of 0.05 mg/L.  Through a Department oversight, the expiration of the SFO interim limit was not corrected at the same time.  The City regularly violated this new, lower TRC permit limit until June 5, 1997, when the Department again modified the SFO so that it would include an interim discharge limit on TRC.

In the same NON, the Department noted a violation of Oregon Administrative Rule (OAR) 340-52.  A forcemain extension to the City’s sanitary sewage collection system was completed without approval by the Department.  While the City of Newberg is exempt from Department plan review for gravity sewers, the exemption does not include forcemains.

NON’s are informal enforcement actions.  Formal enforcement actions include Notice of Permit Violation (NPV), Civil Penalties (CP) and administrative orders (such as the SFO).  The only formal enforcement action taken during this permit cycle were before 1994.  The previously mentioned SFO was issued on October 2, 1992.  In addition, civil penalties were assessed in November 1992 for deficiencies in the City’s pretreatment program.  Finally, a NPV was issued on June 30, 1993 for historical violations of permits limits.

The violations have been corrected.  Therefore, the Department considers this facility to be in substantial compliance with the terms of the current permit.  There is no record of any complaints about this facility.

# PERMIT LIMITATIONS

Two categories of effluent limitations exist for NPDES permits: 1) Technology based effluent limits, and 2) Water quality based effluent limits.  Technology based effluent limits have been established by EPA rules.  Technology based effluent limits were established to require a minimum level of treatment for industrial or municipal sources using available technology.  Water quality based effluent limits are designed to be protective of the beneficial uses of the receiving water and are independent of the available treatment technology.

In addition, when performing a permit renewal, there are existing permit limits (discussed above).  These may be technology-based limits, water quality-based limits, or limits based on best professional judgment.   When renewing a permit, the most stringent of technology-based, water quality-based, and existing effluent limits must be applied.

## Technology-Based Effluent Limits

EPA has established secondary treatment standards for domestic wastewater treatment facilities.  The standards are found in 40 CFR Part 133.  This facility must achieve a biochemical oxygen demand (BOD5) monthly average of 30 mg/L and a weekly average of 45 mg/L or a carbonaceous biochemical oxygen demand (CBOD5) monthly average of 25 mg/L and a weekly average of 40 mg/L.  The facility must also achieve a suspended solids (TSS) monthly average of 30 mg/L and a weekly average of 45 mg/L.  The pH must be between 6.0 and 9.0.  In addition, the facility must remove at least 85% of the influent CBOD5 and TSS.

Oregon Administrative Rules establish minimum design criteria for domestic treatment facilities.  In the Willamette Basin, the CBOD5 and TSS minimum design criteria is 10 mg/L as a monthly average in the summer period and secondary treatment in the winter period.  In addition, there are requirements for disinfection and dilution of oxygen demanding pollutants.

## Water Quality-Based Effluent Limits

Pollutant parameters should be limited if there is a reasonable potential for the discharge to cause or contribute to an excursion above any state water quality criteria or standard. The future TMDLs may assign additional WLAs to this source to address in-stream violations of water quality criteria.

A reasonable potential analysis (RPA) for ammonia, cyanide and metals was performed by evaluating effluent data in DEQ spreadsheets.  The spreadsheet uses acute and chronic water quality criteria, background concentrations and the available dilution.  The RPA (see Attachment #7) for ammonia indicated that there is no reasonable potential for the discharge to cause or contribute to an excursion above the water quality criteria for ammonia.  The RPA for the other toxics indicated that concentrations of cadmium, copper, lead, mercury and silver in the effluent could have a reasonable potential to cause an excursion above the state water quality criteria.

However, in each case, the effluent and/or ambient results were near or below the minimum detection level for that parameter.  In some cases, the upstream background concentrations were actually above the water quality criteria.  Therefore, the Department proposes to include a permit requirement for special monitoring of the effluent and receiving stream for cadmium, copper, lead and silver using a “clean” sampling method, an “ultra-clean” sampling method, EPA method 1669 or any other method approved by the Department.  Monitoring for mercury shall be conducted in accordance with EPA Method 1631.  The special monitoring must be conducted semi-annually on one day of the three consecutive days of toxics monitoring.  After 2 years, the permittee may discontinue special monitoring of the receiving stream.  At that time, special monitoring of the effluent may be discontinued unless otherwise notified in writing by the Department.

After special monitoring is complete, the Department will perform a RPA to determine if the discharge has a potential to cause or contribute to an excursion above the state water quality criteria.  If there is a reasonable potential, the Department may modify the permit as necessary.

# PERMIT DRAFT DISCUSSION

The proposed permit limits and conditions are described below.  Refer to the proposed permit and the discussion above when reviewing this section.

## Face Page

The face page provides information about the permittee, description of the wastewater, outfall locations, receiving stream information, permit approval authority, and a description of permitted activities.  The permittee is authorized to construct, install, modify, or operate a wastewater collection, treatment, control and disposal system.  Permits discharge of treated effluent to the Willamette River within limits set by Schedule A and the following schedules.  All other discharges are prohibited.

In accordance with OAR 340, Division 49 all permitted municipal wastewater collection and treatment facilities are to receive a classification based on the size and complexity of the systems.  The Department has incorporated the classification of the collection and treatment systems into the NPDES discharge permit.  Currently, the treatment is considered a Class IV system while the collection system is considered Class III.  Both systems were reevaluated to determine the appropriateness of the current classification for operator certification requirements (see Attachment #8).  The Department proposed to retain the current system classifications.

## Schedule A, Waste Discharge limitations

Schedule A contains the effluent limitations proposed for each Outfall.  In addition, there is a condition prohibiting adverse impacts on existing or potential beneficial uses of groundwater.

Outfall 001 - Treated Effluent

The Department is generally proposing to retain the existing limits shown above with one exception.  The fecal coliform limit will be based on the E. coli bacteria standard.

CBOD and TSS concentration and mass limits

Based on the Willamette Basin minimum design criteria, wastewater treatment resulting in a monthly average effluent concentration of 10 mg/L for CBOD5 and TSS must be provided from May 1 through October 31.  From November 1 through April 30, a minimum of secondary treatment is required.  Secondary treatment in Oregon is defined as monthly average concentration limit of 30 mg/L for BOD5 or 25 mg/L for Carbonaceous Biochemical Oxygen Demand (CBOD5) and 30 mg/L for TSS.

The Department is proposing concentration limits at least as stringent as the basin minimum design criteria.  The proposed monthly average summer CBOD5 and TSS concentration limits are 10 mg/L with a weekly average limit of 15 mg/L.  The proposed monthly average winter CBOD5 concentration limits are 25 mg/L with a weekly average limit of 40 mg/L.  The proposed monthly average winter TSS concentration limits are 30 mg/L with a weekly average limit of 45 mg/L.

The facility’s summer mass limits (monthly and weekly average and daily maximum) for CBOD5 and TSS are based on the design average dry weather flow (ADWF) of 4.0 MGD and the monthly average CBOD5 and TSS concentration limit of 10 mg/L.  The summer calculations are:

a)  4.0 MGD x 8.34 lbs/gal x 10 mg/L = 333 (330) lbs/day monthly avg.

b)  333 lbs/day monthly avg x 1.5 = 500 lbs/day weekly avg.

c)  333 lbs/day monthly avg x 2 = 666 (670) lbs daily maximum

The daily maximum mass limit could be as high as 670 pounds per day.  However, the current permit limits are 660 pounds per day.  The limits cannot be increased without approval of the Environmental Quality Commission (EQC).  No changes are proposed for the summer mass limits.

The winter mass load limits (monthly and weekly average and daily maximum) for CBOD5 are based on the design average wet weather flow (AWWF) of 6.5 MGD and the monthly average CBOD5 concentration limit.  The weekly average and daily maximum CBOD5 limits in the prior permit were incorrectly calculated.  The proposed permit corrects these errors.  The weekly average limit is reduced from 2200 lbs/day to 2000 lbs/day and the daily maximum limit is reduced from 2800 lbs/day to 2700 lbs/day.  The new limits are in accordance with OAR 340-041-041-120(9)(a).  The winter CBOD5 calculations are:

a)  6.5 MGD x 8.34 lbs/gal x 25 mg/L = 1355 (1400) lbs/day monthly avg.

b)  1355 lbs/day monthly avg x 1.5 = 2033 (2000) lbs/day weekly avg.

c)  1355 lbs/day monthly avg x 2 = 2710 (2700) lbs daily maximum

The winter mass load limits (monthly and weekly average and daily maximum) for TSS are based on the design average wet weather flow (AWWF) of 6.5 MGD and the monthly average TSS concentration limit.  The winter TSS calculations are:

a)  6.5 MGD x 8.34 lbs/gal x 30 mg/L = 1626 (1600) lbs/day monthly avg.

b)  1626 lbs/day monthly avg x 1.5 = 2439 (2400) lbs/day weekly avg.

c)  1626 lbs/day monthly avg x 2 = 3253 (3300) lbs daily maximum

The daily maximum mass limit could be as high as 3300 pounds per day.  However, the current permit limits are 3200 pounds per day.  The limits cannot be increased without approval of the Environmental Quality Commission (EQC).  No changes are proposed for the winter TSS mass limits.

On any day that the daily flow exceeds 8.0 MGD (twice the design ADWF), the daily mass load limits shall not apply.  In accordance with OAR 340-041-0061(10)(a)(G), the permittee is required to remove all inflow sources from the collection system because the winter mass limits are based on the design average wet weather flow (AWWF).  The proposed permit includes a Schedule C condition requiring submittal of a program and time schedule for identifying and removing inflow.

No other changes are proposed for the winter mass limits.  The mass load limitations are rounded to two significant figures.  A review of monitoring data (see Attachment #9) for the last three years indicate the City is generally able to comply with the permit limits.

BOD and TSS Percent Removal Efficiency

A minimum level of percent removal for BOD5 and TSS for municipal dischargers is required by the Code of Federal Regulations (CFR) secondary treatment standards (40 CFR, Part 133).  An 85 percent removal efficiency limit is included in the proposed permit to comply with federal requirements.  A review of monitoring data indicates the City should generally be able to comply with the BOD and TSS removal efficiency limits.

pH

The proposed effluent limits for pH remain unchanged at 6.0 to 9.0 for the facility.  The Willamette Basin water quality standards for pH are established in OAR 340-041-0345.  The allowed ambient range is 6.5 to 8.5.  The proposed permit limits pH to the range 6.0 to 9.0.  This limit is in accordance with Federal wastewater treatment guidelines for sewage treatment facilities (in 40 CFR 133.102(c)) and is applied to the majority of NPDES permittees in the state.  Within the permittee's mixing zone, the water quality standard for pH does not have to be met.  It is the Department's belief that mixing with ambient water within the mixing zone will ensure that the pH at the edge of the mixing zone meets the standard, and the Department considers the proposed permit limits to be protective of the water quality standard.

Fecal Bacteria

The current permit contains limits on fecal coliform bacteria.  The limits are 400 organisms/100 ml weekly geometric mean (or log mean) and 200 organisms/100 ml. monthly geometric mean.  In January 1996, the fecal bacteria water quality standard was changed and is now based on E. coli bacteria.

The proposed limits are a monthly geometric mean of 126 E. coli per 100 mL, with no single sample exceeding 406 E. coli per 100 mL.  The new bacteria standard allows that if a single sample exceeds 406 E coli per 100 mL, then the permittee may take five consecutive re-samples.  If the log mean of the five re-samples is less than or equal to 126, a violation is not triggered.  The re-sampling must be taken at four hour intervals beginning within 28 hours after the original sample was taken.  The E. coli effluent limitations are achievable through proper operation and maintenance.

Total Chlorine Residual

Chlorine is added to the discharge to disinfect the plant effluent and comply with the waste discharge limitations for bacteria.  The minimum design criteria (OAR 340-041-0007) for sewage wastes requires the City to provide disinfection facilities capable of achieving 1.0 mg/L total chlorine residual.  This level could be considered a technology based minimum concentration.

Chlorine is a known toxic substance and as such is subject to limitation under Oregon Administrative Rules.  The rule (OAR 340-041) states in part that toxic substances shall not be discharged to waters of the state at levels that adversely affect public health, aquatic life or other designated beneficial uses.  In addition, levels of toxic substances shall not exceed the criteria listed in Table 20 which were based on criteria established by the EPA and published in Quality Criteria for Water (1986), unless otherwise noted.

However, OAR 340-041-0245(4) states that the Department may allow a designated portion of a receiving water to serve as a zone of dilution for wastewaters and receiving waters to mix thoroughly and this zone will be defined as a mixing zone.  The Department may suspend all or part of the water quality standards, or set less restrictive standards, in the defined mixing zone, provided the water within the mixing zone is free of materials in concentrations that will cause acute toxicity to aquatic life as measured by the acute Whole Effluent Toxicity method and outside the boundary of the mixing zone is free of materials in concentrations that will cause chronic toxicity.

Furthermore, 40 CFR §122.44(d) states that permit limitations must control all pollutants or pollutant parameters which are or may be discharged at a level which will cause, have the reasonable potential to cause, or contribute to an excursion above any state water quality standard, including state narrative criteria for water quality.  The fresh water criteria for chlorine were used to calculate permit limitations.  According to OAR 340-041, Table 20, chlorine concentrations of 11 µg/L can result in chronic toxicity in fresh waters while 19 µg/L can result in acute chlorine toxicity in fresh waters.

Compliance with acute toxicity criteria is required at the edge of the Zone of Immediate Dilution (ZID) and compliance with chronic toxicity criteria is required at the edge of the mixing zone.  For the facility, outfall, and mixing zone as presently configured, the dilution factor at the edge of the ZID is 2.4:1 during critical low stream flow conditions.  The mixing zone study determined that the dilution factor at the edge of the mixing zone is 28.5:1 during critical low flow conditions.

Permit limits based on the acute and chronic criteria were calculated.  Since the acute and chronic criteria are based on different durations, the durations have to be equalized using a DEQ spreadsheet program to determine the more restrictive criteria (see Attachment #10).

In this case, the acute criterion is the more stringent of the two.  Thus, end-of-pipe limits based on that criteria were calculated.  The calculated limits are 0.02 mg/L monthly average and a daily maximum of 0.05 mg/L.

The current permit limits total residual chlorine to a daily average of 0.05 mg/L.  The water quality based limit is more restrictive than the technology based minimum and is essentially equal to the existing permit limit.  The Department is proposing to include total residual chlorine limits of 0.02 mg/L monthly average and a daily maximum of 0.05 mg/L.

The permittee has the ability to dechlorinate the discharge to reduce potential toxic effects on the receiving stream.  A file review of recent effluent monitoring data shows that the chlorine residual does not exceed this limit and the City should generally be able to comply with the limit.

The water quality based effluent limits for total residual chlorine proposed in this permit are lower than the Minimum Level (ML) for chlorine of 0.1 mg/L published by EPA.  In accordance with EPA Region X Guidance for WQBELs Below Analytical Detection Limits issued in 1996, the permit should include the ML as a "compliance evaluation level".  The Department is proposing to include a note in Schedule A establishing 0.10 mg/L as a compliance evaluation level for total residual chlorine.

Mixing Zone

The current permit provides for a mixing zone that consists of that portion of the Willamette River contained within a band extending out seventy five (75) feet from the west bank of the river and extending from a point fifteen (15) feet upstream of the outfall to a point one hundred fifty (150) feet downstream from the outfall. The Zone of Immediate Dilution (ZID) shall be defined as that portion of the allowable mixing zone that is within fifteen (15) feet of the point of discharge.  The Department proposes to retain the existing mixing zone.

Emergency Overflow Outfalls 002 and 003

The City has experienced occasional raw sewage overflows from the sewage collection system for many years.  Schedule A contains a condition prohibiting discharges from these outfalls unless the cause of the overflow is in accordance with the rules.

Groundwater

Based on the Department’s current information, this facility has a low potential for adversely impacting groundwater quality.  Therefore, the permit includes a condition in Schedule A that prohibits any adverse impact on groundwater quality.  In addition, Schedule D of the proposed permit states that no groundwater evaluations will be required during this permit cycle.

## Schedule B - Minimum Monitoring and Reporting Requirements

Schedule B describes the minimum monitoring and reporting necessary to demonstrate compliance with the conditions of this permit.  The authority to require periodic reporting by permittees is included in ORS 468.065(5).  Self-monitoring requirements are the primary means of ensuring that permit limitations are being met.  However, other parameters need to be monitored to collect information when insufficient information exists to establish a limit, but where there is a potential for a water quality concern.

In 1988, the Department developed a monitoring matrix for commonly monitored parameters.  Proposed monitoring frequencies for all parameters are based on this matrix and, in some cases, may have changed from the current permit.  The proposed monitoring frequencies for all parameters correspond to those of facilities of similar size and complexity in the state.

The permittee is required to have a laboratory Quality Assurance/Quality Control program.  The Department recognizes that some tests do not accurately reflect the performance of a treatment facility due to quality assurance/quality control problems.  These tests should not be considered when evaluating the compliance of the facility with the permit limitations.  Thus, the Department is also proposing to include in the opening paragraph of Schedule B a statement recognizing that some test results may be inaccurate, invalid, do not adequately represent the facility's performance and should not be used in calculations required by the permit.

Below is a discussion of some of the minimum monitoring requirements contained in the proposed permit that have not been previously discussed.

Influent and Outfall 001 (Treated Effluent)

Daily monitoring of influent and effluent flow is required in this permit.  Both flow meters must be calibrated every six months.  Monitoring of the influent and effluent for CBOD5 and TSS is retained at twice per week.  Pounds of effluent CBOD5 and TSS must be calculated at the same frequency.

Federal secondary treatment standards require municipal sources to achieve a specific CBOD5 and TSS removal efficiency as a monthly average.  Reporting of the removal efficiencies is required in the proposed permit.

The proposed permit requires monitoring of the quantity of chlorine used and the total chlorine residual on a daily basis to confirm consistent performance of the disinfection system.  Bacteria monitoring on the discharge has been changed from fecal coliform to E. coli but the frequency has been retained at twice per week.  Monitoring for E. coli must be performed in accordance with one of the methods approved by the Department.  Monitoring of the influent and effluent for pH has been retained at three times per week.  The effluent temperature must be monitored on a continuous basis year-round.

Ammonia monitoring is required both because CBOD5 replaces BOD5.  Monitoring must be performed on the same samples as CBOD5 so the frequency is proposed at twice per week.

In order to fully characterize the facility’s contribution of nutrients to the receiving stream, the Department is proposing to effluent monitoring for nutrients.  Weekly monitoring of Total Kjeldahl Nitrogen (TKN), nitrate plus nitrite and phosphorus is proposed for the period from May through October each year.

The City previously monitored the influent and effluent for 9 metals, cyanide and total phenols semi-annually for three consecutive days.  The proposed permit requires monitoring the influent and effluent for 11 metals and cyanide semi-annually for three consecutive days.  The total phenols monitoring requirement has been deleted.  Monitoring results are to be submitted in the annual pretreatment report and are not required to be submitted with the monthly DMR.

For the first two years after permit issuance, the City must perform special toxics monitoring on the effluent for cadmium, copper, lead, mercury and silver during one of the three consecutive days of toxics monitoring.  The special toxics monitoring shall be conducted using a “clean” sampling method, an “ultra-clean” sampling method, EPA method 1669 or any other test method approved by the Department with a detection limit of 0.1 µg/L or less.  Monitoring for mercury shall be conducted in accordance with EPA Method 1631.  The Willamette River shall be monitored for cadmium, copper, lead and silver at the same time. The Willamette River shall be sampled for hardness at the same time the river is sampled for metals.

After two years of this special toxics monitoring, the City may eliminate the special monitoring of the effluent unless otherwise notified by the Department.  The Department will base its determination upon the ability of the permittee to consistently comply with the water quality criteria.

The permittee must perform “priority pollutant” scans in order to complete Part D of EPA Form 2A for the next renewal application.  Three scans are required during the 4 ½ years after permit issuance.  Two of the three scans must be performed no fewer than 4 months and no more than 8 months apart.  As stated above, the proposed permit requires that the pesticide fraction be included in the monitoring of priority pollutants.

The Department has required annual whole effluent toxicity (WET) tests using three species in the proposed permit.  If the results of the first four tests show that the effluent is not toxic, no further Whole Effluent Toxicity testing will be required during this permit.  Whole Effluent Toxicity tests are to be conducted in accordance with EPA test methods and procedural requirements as defined in Schedule D.

Biosolids

OAR 340, Division 50, "Land Application of Domestic Wastewater Treatment Facility Biosolids, Biosolids Derived Products, and Domestic Septage" requires monitoring and reporting of specific sludge parameters under Section 35. These parameters are identified in Schedule B under "Biosolids Management” and include:  Total solids, Volatile solids, Nitrogen, eleven metals (Ag, As, Cd, Cr, Cu, Pb, Hg, Mo, Ni, Se & Zn), Phosphorus, Potassium and pH.

In order to demonstrate compliance with vector attraction requirements, the proposed permit requires monitoring of xxxx.  Monitoring the fecal coliform content and composting time and temperature is the method used to demonstrate compliance with federal biosolids pathogen reduction requirements.  The City must also record of amount of biosolids derived material sold or given away.  Many of these are new requirements.

Outfalls 002 and 003 (Emergency Overflows)

The estimated duration and volume of each overflow from the emergency outfalls must be recorded.  There is no change in this requirement.

Receiving Stream

The Department does not have adequate information on the background concentration of certain metals in the Willamette River and cannot perform a complete reasonable potential analysis.  For the first two years after permit issuance, the City must perform special toxics monitoring on the Willamette River during one of the three consecutive days of effluent toxics monitoring.  The special toxics monitoring shall be conducted using a “clean” sampling method, an “ultra-clean” sampling method, EPA method 1669 or any other test method approved by the Department with a detection limit of 0.1 µg/L or less.  Monitoring for mercury shall be conducted in accordance with EPA Method 1631.  The Willamette River shall be sampled for hardness at the same time the river is sampled for metals.  After two years of this special toxics monitoring, the City may eliminate the special monitoring of the receiving stream.

Reporting

The reporting period is the calendar month.  Discharge monitoring reports must be submitted to the Department monthly by the 15th day of the following month.  The monitoring reports need to identify the principal operators designated by the Permittee to supervise the treatment and collection systems.  The reports must also include records concerning application of biosolids and all applicable equipment breakdowns and bypassing.

Schedule B of the permit includes the requirement for the submittal of annual reports.  The conditions are standard language requirements concerning:

Annual report which details progress towards reducing overflow frequency

Annual report of solids handling activities

Annual report on temperature monitoring results

## Schedule C, Compliance Schedules and Conditions

The permit contains five compliance conditions with deadlines:

- Within 180 days of permit issuance, the permittee must submit a proposed program and time schedule for identifying and reducing inflow.

- Within 90 days after permit issuance, the permittee must submit a report which identifies known sewage overflows.

- By no later than June 30, 2005, the permittee must submit to the Department Sewer Use Ordinance revisions that are consistent with federal pretreatment regulations.  The condition includes a note that provides for an accelerated time schedule should a categorical or significant industry connect to the City’s collection system.

- By no later than June 30, 2006, the permittee must submit to DEQ local pretreatment limits.  The condition includes a note that provides for an accelerated time schedule should a categorical or significant industry connect to the City’s collection system.

- By no later than June 30, 2006, the permittee must submit to the Department pretreatment program implementation procedures.  The condition includes a note that provides for an accelerated time schedule should a categorical or significant industry connect to the City’s collection system.

The final condition requires the permittee to meet the compliance dates established in this schedule or notify the Department within 14 days following any lapsed compliance date.

## Schedule D - Special Conditions

The permit contains seven special conditions.  The requirements include:

- Schedule D of this permit includes conditions requiring biosolids be managed in accordance with the approved biosolids management plan. Biosolids that do not meet the Class A criteria shall not be sold or given away.

- The permit may be modified to incorporate changes in federal biosolids standards.

- The requirements for Whole Effluent Toxicity (WET) testing are specified.

- The permittee must have the facilities supervised by personnel certified by the Department in the operation of treatment and/or collection systems.

- The permittee must notify the Department of malfunctions.

- Unless otherwise approved in writing by the Department, all inflow sources are to be permanently disconnected from the sanitary sewer system.

- The permittee shall not be required to perform a hydrogeologic characterization or groundwater monitoring due during the term of this permit.

## Schedule E – Pretreatment Activities

The current permit contains a Schedule E which requires the City to conduct and enforce an industrial waste pretreatment program as approved by the Department and the General Pretreatment Regulations (40 CFR Part 403).  The Department is proposing to include similar conditions in the new permit with some minor changes.  However, some of the condition will not become effective until the Department approves the pretreatment program improvements required in Schedule C.

## Schedule F, NPDES General Conditions

All NPDES permits issued in the State of Oregon contain certain conditions that remain the same regardless of the type of discharge and the activity causing the discharge.  These conditions are called General Conditions.  These conditions can be changed or modified only on a statewide basis.  The latest edition of the NPDES General Conditions is December 1, 1995 and this edition is included as Schedule F of the draft permit.

Section A contains standard conditions which include compliance with the permit, assessment of penalties, mitigation of noncompliance, permit renewal application, enforcement actions, toxic discharges, property rights and referenced rules and statutes.  Section B contains requirements for operation and maintenance of the pollution control facilities.  This section includes conditions for proper operation and maintenance, duty to halt or reduce activity in order to maintain compliance, bypass of treatment facilities, upset conditions, treatment of single operational events, overflows from wastewater conveyance systems and associated pump stations, public notification of effluent violation or overflow, and disposal of removed substances.  Section C contains requirements for monitoring and reporting.  This section includes conditions for representative sampling, flow measurement, monitoring procedures, penalties of tampering, reporting of monitoring results, additional monitoring by the permittee, averaging of measurements, retention of records, contents of records, and inspection and entry.  Section D contains reporting requirements and includes conditions for reporting planned changes, anticipated noncompliance, permit transfers, progress on compliance schedules, noncompliance which may endanger public health or the environment, other noncompliances, and other information.  Section D also contains signatory requirements and the consequences of falsifying reports.  Section E contains the definitions used throughout the permit.

## PERMIT PROCESSING/PUBLIC COMMENT/APPEAL PROCESS

The beginning and end date of the public comment period to receive written comments regarding this permit, and the contact name and telephone number are included in the public notice.  The permittee is the only party having standing to file a permit appeal.  If the Permittee is dissatisfied with the conditions of the permit when issued, they may request a hearing before the EQC or its designated hearing officer, within 20 days of the final permit being mailed.  The request for hearing must be sent to the Director of the Department.  Any hearing held shall be conducted pursuant to regulations of the Department.