## 25%
Attachment 3a
| Facility Name: Newberg STP |  |  |  |  | Date: | 2004-03-18
Enter data into white cells below:
Equation used to calculate DT at edge of MZ
|  | 7Q10 = | 5200 | cfs
|  | Ambient Temperature or Criterion | 20 | ºC
|  | Effluent Flow = | 4 | mgd |  |  |  | Equation used to calculate thermal load limit
|  | Effluent Temperature | 22.5 | ºC
|  | Allowable increase = | 0.3 | ºC
Where:
|  | 25% of 7Q10 = | 1300 | cfs |  |  |  | Qe = | Effluent Flow in mgd
[8 empty] | S = | Dilution
|  | 25% dilution = | 210.9483 | dilution = (Qe+Qr)/Qe |  |  |  | DTall = | Allowable temperature increase
at edge of MZ (°C)
[8 empty] | Cp = | Specific Heat of Water (1 cal/g °C)
[8 empty] | r = | Density of Water (1 g/cm3)
|  | DT at edge of MZ = | 0.011851 | ºC | No Reasonable Potential |  |  | 3785.41 = | Flow conversion from mgd to m3/day
|  | Thermal Load Limit = | N/A | Million Kcals

## MZ Dilution
Attachment 3b
| Facility Name: Newberg STP |  |  |  |  | Date: | 2004-03-18
Enter data into white cells below:
Equation used to calculate DT at edge of MZ
|  | Dilution = | 28.5
|  | Ambient Temperature or Criterion | 20 | ºC
|  | Effluent Temperature | 22.5 | ºC |  |  |  | Equation used to calculate thermal load limit
|  | Allowable increase = | 0.3 | ºC
|  | Effluent Flow Rate = | 4 | mgd
Where:
[8 empty] | Qe = | Effluent Flow in mgd
[8 empty] | S = | Dilution
|  | DT at edge of MZ= | 0.087719 | ºC | No Reasonable Potential |  |  | DTall = | Allowable temperature increase
at edge of MZ (°C)
[8 empty] | Cp = | Specific Heat of Water (1 cal/g °C)
|  | Thermal Load Limit = | N/A | Million Kcals |  |  |  | r = | Density of Water (1 g/cm3)
[8 empty] | 3785.41 = | Flow conversion from mgd to m3/day