## Cl-, NH3 RPA
Facility Name: | Newberg STP |  |  |  | Attachment #6 |  |  |  | Date: | 2004-03-19
Dilution Values? (Y/N) | Y | calculated |  |  | Summer data |  | Effluent | Stream | Mixed
Low Flow Dilution @ ZID = | 2.4 | * | [6 empty] | ZID | MZ
Low Flow Dilution @ MZ = | 28.5 | * |  |  |  | pH * = | 7.3 | 7.7 | 7.3937 | 7.6404 | ( 6.5-9 )
High Flow Dilution @ ZID = | 2.4 | * |  |  |  | Temp * = | 22.5 | 22 | 22.2083 | 22.0175 | ° C
High Flow Dilution @ MZ = | 28.5 | * |  |  |  | Alkalinity = | 75 | 25
Enter data below if no dilution data is available | [5 empty] | Salmonids Present? (Y/N) |  | y
Data to estimate dilution | Summer | Winter |  |  |  | Fresh Water ? (Y/N) |  | y
7Q10 (CFS) = | * | * |  |  |  | Salinity (ppt) | 0 | 20 | 11.6667 | 19.2982
1Q10 (CFS) = | * | * |  |  | Winter data
% dilution at MZ = | 25 | 25 |  |  |  | pH * = | 7 | 7.6 | 7.1306 | 7.4953 | ( 6.5-9 )
% dilution at ZID = | 10 | 10 |  |  |  | Temp * = | 16 | 12.8 | 14.1333 | 12.9123 | ° C |  | CALCULATIONS
Effluent Flow (mgd) = | * | * |  |  |  | Alkalinity = | 75 | 25
[6 empty] | Salmonids Present? (Y/N) |  | y | [6 empty] | M |  | AMMONIA | [10 empty] | R | R
Confidence Level = | 99% |  |  |  |  | Fresh Water ? (Y/N) |  | y | [6 empty] | F | T | T | T | T | [8 empty] | A | A
Probability Basis = | 95% |  |  |  |  | Salinity (ppt) | 0 | 20 | 11.6667 | 19.2982 |  |  | % | s | a | C | C | C | C | F | F | F | F |  |  |  |  | T | T
[13 empty] | t | I | c | A | A | A | A | P | P | P | P | F | F | F | F | I | I
[13 empty] | I | g | t | P | P | P | P | H | H | H | H | T | T | T | T | O | O
|  |  |  | Maximum |  | Maximum | Maximum | WQ CRITERIA |  | REASONABLE |  |  | l | m | o | a | c | a | c | l | l | h | h | a | c | a | c | l | h
| # of | Highest | Coef. of | Effluent | Background | Conc. at | Conc. at | 1 Hour | 4 Day | POTENTIAL ? |  |  | e | a | r | l | l | h | h | a | c | a | c | l | l | h | h | c | c
PARAMETER | Samples | Conc. | Variance | Conc. | Conc. | ZID | MZ | (CMC) | (CCC)
|  | mg/l |  | mg/l | mg/l | mg/l | mg/l | mg/l | mg/l | ACUTE | CHRONIC
Low Flow Season
CHLORINE | 5 | 1 | 0.6 | 2.9 | 0 | 1.2083 | 0.10175 | 0.019 | 0.011 | YES | YES |  | 0.39811 | 0.30748 | 2.9
AMMONIA* | 52 | 0.343 | 0.6 | 0.4116 | 0.09 | 0.224 | 0.10128 | 11.6614 | 1.0769 | NO | NO |  | 0.91525 | 0.30748 | 1.2 | 20 | 15 |  |  | l a: 1.6117; l c: 1.26; a l: 1; c l: 1.4125 | 17.4814
High Flow Season
CHLORINE | 5 | 0.5 | 0.6 | 1.45 | 0 | 0.60417 | 0.050877 | 0.019 | 0.011 | YES | YES |  | 0.39811 | 0.30748 | 2.9
AMMONIA* | 44 | 0.793 | 0.6 | 0.9516 | 0.09 | 0.449 | 0.12023 | 18.1166 | 1.8132 | NO | NO |  | 0.90063 | 0.30748 | 1.2 |  |  | 20 | 15 | h a: 2.2877; h c: 1.4424; a h: 1.4997; c h: 1.6317 |  | 21.3277
* -NOTES :
Temperature must be between 0 and 30 ° C
pH must be between 6.5 and 9
Ammonia is total ammonia as NH3
Saltwater Ammonia Criteria |  | (taken from Ambient Water Quality Criteria for Ammonia (Saltwater) 1989
For RPA Spreadsheet | Temp | pH | Salinity | Pressure | Molal Ionic Strength | pKa8 | % Unionized: | Unionized |  | Total NH3 |  | Total NH3 as N
| (deg C) | (su) | (ppt) | (ATM) | (not valid if >0.85): | @ 25 deg C |  | Acute | Chronic | Acute | Chronic | Acute | Chronic
[12 empty] | mg/L | mg/L
Summer ZID | 22.2083 | 7.3937 | 11.6667 | 1 | 0.23524 | #N/A | #N/A | 0.233 | 0.035 | #N/A | #N/A | #N/A | #N/A
Summer MZ | 22.0175 | 7.6404 | 19.2982 | 1 | 0.39217 | #N/A | #N/A | 0.233 | 0.035 | #N/A | #N/A | #N/A | #N/A
Winter ZID | 14.1333 | 7.1306 | 11.6667 | 1 | 0.23524 | #N/A | #N/A | 0.233 | 0.035 | #N/A | #N/A | #N/A | #N/A
Winter MZ | 12.9123 | 7.4953 | 19.2982 | 1 | 0.39217 | #N/A | #N/A | 0.233 | 0.035 | #N/A | #N/A | #N/A | #N/A
Other | 20 | 8.2 | 10 | 1 | 0.2013 | #N/A | #N/A | 0.233 | 0.035 | #N/A | #N/A | #N/A | #N/A
Other | 20 | 8.2 | 10 | 1 | 0.2013 | #N/A | #N/A | 0.233 | 0.035 | #N/A | #N/A | #N/A | #N/A
Calculation of pH of a mixture of two flows.
Based on the procedure in EPA's DESCON program (EPA, 1988. Technical
Guidance on Supplementary Stream Design Conditions for Steady State
Modeling. USEPA Office of Water, Washington D.C.)
|  |  |  | Summer |  | Winter
INPUT |  |  |  | ZID | MZ | ZID | MZ
1. DILUTION FACTOR AT MIXING ZONE/ZID BOUNDARY |  |  |  | 2.4 | 28.5 | 2.4 | 28.5
1. UPSTREAM/BACKGROUND CHARACTERISTICS
Temperature (deg C): |  |  |  | 22 | 22 | 12.8 | 12.8
pH: |  |  |  | 7.7 | 7.7 | 7.6 | 7.6
Alkalinity (mg CaCO3/L): |  |  |  | 25 | 25 | 25 | 25
2. EFFLUENT CHARACTERISTICS
Temperature (deg C): |  |  |  | 22.5 | 22.5 | 16 | 16
pH: |  |  |  | 7.3 | 7.3 | 7 | 7
Alkalinity (mg CaCO3/L): |  |  |  | 75 | 75 | 75 | 75
OUTPUT
1. IONIZATION CONSTANTS
Upstream/Background pKa: |  |  |  | 6.3685 | 6.3685 | 6.4386 | 6.4386
Effluent pKa: |  |  |  | 6.3652 | 6.3652 | 6.4119 | 6.4119
2. IONIZATION FRACTIONS
Upstream/Background Ionization Fraction: |  |  |  | 0.95547 | 0.95547 | 0.93549 | 0.93549
Effluent Ionization Fraction: |  |  |  | 0.89589 | 0.89589 | 0.7948 | 0.7948
3. TOTAL INORGANIC CARBON
Upstream/Background Total Inorganic Carbon (mg CaCO3/L): |  |  |  | 26.1653 | 26.1653 | 26.7241 | 26.7241
Effluent Total Inorganic Carbon (mg CaCO3/L): |  |  |  | 83.7159 | 83.7159 | 94.3634 | 94.3634
4. CONDITIONS AT MIXING ZONE BOUNDARY
Temperature (deg C): |  |  |  | 22.2083 | 22.0175 | 14.1333 | 12.9123
Alkalinity (mg CaCO3/L): |  |  |  | 45.8333 | 26.7544 | 45.8333 | 26.7544
Total Inorganic Carbon (mg CaCO3/L): |  |  |  | 50.1447 | 28.1846 | 54.9071 | 29.0974
pKa: |  |  |  | 6.3671 | 6.3684 | 6.4272 | 6.4376
pH at Mixing Zone/ZID Boundary: |  |  |  | 7.3937 | 7.6404 | 7.1306 | 7.4953
Note on B3: Enter "Y" if dilution is known, and enter dilution values for ZID and MZ. If dilution is not known enter "N" and enter information for 7Q10, 1Q10, % dilution, and effluent flow below.
Note on B10: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on B11: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on B14: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on B16: Percentile may be changed if rationale is provided
Note on B17: Percentile may be changed if rationale is provided
Note on B25: Enter "*" if you are not doing an RPA for this parameter.
Note on B26: Enter "*" if you are not doing an RPA for this parameter.
Note on B29: Enter "*" if you are not doing an RPA for this parameter.
Note on B30: Enter "*" if you are not doing an RPA for this parameter.
Note on C3: This is the calculated dilution based on the 7Q10, 1Q10 etc. data entered below. This calculated dilution will be used when "N" is entered into the adjacent box.
Note on C10: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on C11: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on C14: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on G10: Enter salinity data if you answered "N" to Fresh Water.
Note on G17: Enter salinity data if you answered "N" to Fresh Water.
Note on G48: DEQ: Whitfield model "B"
Note on I48: DEQ: from EPA 440/5-88-004
Note on M48: DEQ: Total as N is what permit limits are based upon

## Metals RPA
Facility Name: | Enter Name Here | [7 empty] | Date:
Dilution Values? (Y/N) | Y | calculated |  |  | Hardness | mg/L CaCO3
Dilution @ ZID | 2.4 | * |  |  | Effluent | 75 | (Hardness values should
Dilution @ MZ | 28.5 | * |  |  | Stream | 25 | be >25 and <400 mg/L)
If no dilution values enter info below |  |  |  |  | Mixed
Facility Effluent Flow | 4 | MGD |  |  | ZID | 45.8333
7Q10 | * | CFS |  |  | MZ | 26.7544
1Q10 | * | CFS | [14 empty] | Calculations |  | M
% dilution at ZID | 10 | % |  |  | Confidence Level |  | 99% | [11 empty] | F
% dilution at MZ | 25 | % |  |  | Probability Basis |  | 95% | [9 empty] | % | s | a
Fresh Water? (Y/N) | y
[13 empty] | PROPOSED CRITERIA |  |  |  | t | I | c
|  |  |  | Maximum |  | Maximum | Maximum | WQ CRITERIA |  | REASONABLE |  |  | Proposed Criteria |  | REASONABLE |  | I | g | t
| # of | Highest | Coef. of | Effluent | Background | Conc. at | Conc. at | 1 Hour | 4 Day | POTENTIAL ? |  |  | 1 Hour | 4 Day | POTENTIAL ? |  | l | m | o
PARAMETER | Samples | Conc. | Varience | Conc. | Conc. | ZID | MZ | (CMC) | (CCC) |  |  |  | (CMC) | (CCC) |  |  | e | a | r
|  | µg/l |  | µg/l | µg/l | µg/l | µg/l | µg/l | µg/l | ACUTE | CHRONIC | ZID | µg/l | µg/l | ACUTE | CHRONIC
ALUMINUM † | 5 | 1 | 0.6 | 2.9 | * | * | * | 750 | 87 | -- | -- |  | 750 | 87 | YES | YES | 0.39811 | 0.55451 | 2.9
ARSENIC V * | 6 | 2.5 | 0.6 | 6.5 | 2.5 | 4.1667 | 2.6404 | 850 | 48 | NO | NO |  | 850 | 48 | NO | NO | 0.46416 | 0.55451 | 2.6
ARSENIC III | 6 | 2.5 | 0.6 | 6.5 | 2.5 | 4.1667 | 2.6404 | 360 | 190 | NO | NO |  | 340 | 150 | NO | NO | 0.46416 | 0.55451 | 2.6
CADMIUM + | 6 | 0.5 | 0.6 | 1.3 | 0.5 | 0.83333 | 0.52807 | 1.6268 | 0.40281 | NO | YES |  | 0.96513 | 0.10189 | NO | YES | 0.46416 | 0.55451 | 2.6
CHROMIUM VI | 5 | 12 | 0.6 | 34.8 | * | * | * | 16 | 11 | -- | -- |  | 16 | 11 | YES | YES | 0.39811 | 0.55451 | 2.9
CHROMIUM III +^ | 5 | 10 | 0.6 | 29 | * | * | * | 916.6122 | 70.3024 | -- | -- |  | 952.1138 | 29.2713 | YES | YES | 0.39811 | 0.55451 | 2.9
TOTAL CHROMIUM † | 6 | 2.35 | 0.6 | 6.11 | 15 | 11.2958 | 14.6881 | 932.6122 | 81.3024 | NO | NO |  | 968.1138 | 40.2713 | NO | NO | 0.46416 | 0.55451 | 2.6
COPPER + | 6 | 6.2 | 0.6 | 16.12 | 10 | 12.55 | 10.2147 | 8.4988 | 3.8324 | YES | YES | ZID | 6.7122 | 3.0237 | YES | YES | 0.46416 | 0.55451 | 2.6
CYANIDE | 6 | 2.5 | 0.6 | 6.5 | 2.5 | 4.1667 | 2.6404 | 22 | 5.2 | NO | NO |  | 22 | 5.2 | NO | NO | 0.46416 | 0.55451 | 2.6
FLUORIDE † | 5 | 12 | 0.6 | 34.8 | * | * | * | 2000 | 1000 | -- | -- |  | 2000 | 1000 | YES | YES | 0.39811 | 0.55451 | 2.9
IRON ‡ | 5 | 12 | 0.6 | 34.8 | * | * | * | 2000 | 1000 | -- | -- |  | 2000 | 1000 | YES | YES | 0.39811 | 0.55451 | 2.9
LEAD + | 6 | 1 | 0.6 | 2.6 | 7 | 5.1667 | 6.8456 | 30.2422 | 0.59391 | NO | YES |  | 30.2422 | 0.59391 | NO | YES | 0.46416 | 0.55451 | 2.6
MERCURY | 6 | 0.005 | 0.6 | 0.013 | 0.25 | 0.15125 | 0.24168 | 2.4 | 0.012 | NO | YES |  | 2.4 | 0.012 | NO | YES | 0.46416 | 0.55451 | 2.6
NICKEL + | 6 | 1 | 0.6 | 2.6 | 20 | 12.75 | 19.3895 | 733.0104 | 51.6788 | NO | NO |  | 242.8611 | 17.0977 | NO | YES | 0.46416 | 0.55451 | 2.6
SELENIUM | 6 | 2.5 | 0.6 | 6.5 | 2.5 | 4.1667 | 2.6404 | 260 | 35 | NO | NO | [5 empty] | 0.46416 | 0.55451 | 2.6
SILVER + | 6 | 3 | 0.6 | 7.8 | 0.5 | 3.5417 | 0.75614 | 1.0608 | 0.12 | YES | YES | ZID | 0.98908 | 0.12 | YES | YES | 0.46416 | 0.55451 | 2.6
ZINC + | 6 | 50 | 0.6 | 130 | 10 | 60 | 14.2105 | 60.4207 | 34.682 | NO | NO | ZID | 61.8636 | 39.2056 | NO | NO | 0.46416 | 0.55451 | 2.6
Custom | * | 7 | 0.21 | * | * | * | * | * | * | -- | -- |  |  |  | * | * | #VALUE! | 0.20774 | #VALUE!
[17 empty] | #DIV/0! | 0 | #DIV/0!
[17 empty] | #DIV/0! | 0 | #DIV/0!
| NOTES : | [15 empty] | #VALUE! | 0 | #VALUE!
Shaded results are based on 1/2 the detection limit
|  | All units in ug/L | [14 empty] | #DIV/0! | 0 | #DIV/0!
* Insufficient data to develop criteria; value presented is the Lowest Observed Effect Level
+ Hardness dependent criteria
‡ - No acute standard. The CMC is estimated as 2X the CCC.
† - Not DEQ Criteria
^ Marine acute criterion has insufficient data to develop criteria; value = LOEL
[21 empty] | Priority |  | Aquatic Life |  |  |  | Human Health
[21 empty] | Priority Pollutant | Carcinogen | Fresh Water |  | Marine Water |  | Water & Fish | Fish Consumption | Drinking
[23 empty] | Acute | Chronic | Acute | Chronic | Ingestion | Only | Water MCL
[20 empty] | ALUMINUM † | N | N | 750 | 87 | -- | -- | -- | -- | --
[20 empty] | ARSENIC V * | Y | Y | 850 | 48 | 2319 | 13 | -- | -- | --
[20 empty] | ARSENIC III | Y | Y | 360 | 190 | 69 | 36 | -- | -- | --
[20 empty] | CADMIUM + | Y | N | 1.6268 | 0.40281 | 43 | 9.3 | 10 | -- | 10
[20 empty] | CHROMIUM VI | Y | N | 16 | 11 | 1100 | 50 | 50 | -- | 50
[20 empty] | CHROMIUM III +^ | N | N | 916.6122 | 70.3024 | 10300 | -- | 170000 | 3433000 | 50
[20 empty] | TOTAL CHROMIUM † | N | N | 932.6122 | 81.3024 | 11400 | -- | 170050 | 3433000 | 100
[20 empty] | COPPER + | Y | N | 8.4988 | 3.8324 | 2.9 | 2.9 | -- | -- | --
[20 empty] | CYANIDE | Y | N | 22 | 5.2 | 1 | 1 | 200 | -- | --
[20 empty] | FLUORIDE † | N | N | 2000 | 1000 | -- | -- | -- | -- | --
[20 empty] | IRON ‡ | N | N | 2000 | 1000 | -- | -- | 300 | -- | --
[20 empty] | LEAD + | Y | N | 30.2422 | 0.59391 | 140 | 5.6 | 50 | -- | 50
[20 empty] | MERCURY | Y | N | 2.4 | 0.012 | 2.1 | 0.025 | 0.144 | 0.146 | 2
[20 empty] | NICKEL + | Y | N | 733.0104 | 51.6788 | 75 | 8.3 | 13.4 | 100 | --
[20 empty] | SILVER + | Y | N | 1.0608 | 0.12 | 2.3 | -- | 50 | -- | 50
[20 empty] | ZINC + | Y | N | 60.4207 | 34.682 | 95 | 86 | -- | --
NOTES :
All units in ug/L
* Insufficient data to develop criteria; value presented is the Lowest Observed Effect Level
‡ - No acute standard. The CMC is estimated as 2X the CCC.
† - Not DEQ Criteria
^ Marine acute criterion has insufficient data to develop criteria; value = LOEL
Note on B3: Enter "Y" if dilution is known, and enter dilution values for ZID and MZ. If dilution is not known enter "N" and enter information for 7Q10, 1Q10, % dilution, and effluent flow below.
Note on B7: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on B8: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on B9: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on B10: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on B11: Enter "*" if you don't want "calculated" dilution values to be displayed above.
Note on B18: Enter "*" if you are not doing an RPA for this parameter.
Note on B19: Enter "*" if you are not doing an RPA for this parameter.
Note on B20: Enter "*" if you are not doing an RPA for this parameter.
Note on B21: Enter "*" if you are not doing an RPA for this parameter.
Note on B22: Enter "*" if you are not doing an RPA for this parameter.
Note on B23: Enter "*" if you are not doing an RPA for this parameter.
Note on B24: Enter "*" if you are not doing an RPA for this parameter.
Note on B25: Enter "*" if you are not doing an RPA for this parameter.
Note on B26: Enter "*" if you are not doing an RPA for this parameter.
Note on B27: Enter "*" if you are not doing an RPA for this parameter.
Note on B28: Enter "*" if you are not doing an RPA for this parameter.
Note on B29: Enter "*" if you are not doing an RPA for this parameter.
Note on B30: Enter "*" if you are not doing an RPA for this parameter.
Note on B31: Enter "*" if you are not doing an RPA for this parameter.
Note on B32: Enter "*" if you are not doing an RPA for this parameter.
Note on B33: Enter "*" if you are not doing an RPA for this parameter.
Note on B34: Enter "*" if you are not doing an RPA for this parameter.
Note on C3: This is the calculated dilution based on the 7Q10, 1Q10 etc. data entered below. This calculated dilution will be used when "N" is entered into the adjacent box.
Note on H10: Percentile may be changed if rationale is provided
Note on H11: Percentile may be changed if rationale is provided