## EF Determination
Table D1-1. Emission Factor Determination
| Pollutant | CAS/DEQ ID | Emission Factor (lbs/1000 gal)
|  |  | Oregon DEQ1 | 2019 ST 2 | 2021 ST 3 | CAT 3516C 2,500 kW 4 | Other Units >560 kW 1
| 1,3-Butadiene | 106-99-0 | 0.2174 | 0 | N/A | 0 | 0.2174
| Acenaphthene - PAH | 83-32-9 | 0.00073461 |  | 0.00056962 | 0.00056962 | 0.00073461
| Acenaphthylene - PAH | 208-96-8 | 0.00080982 |  | 0.00067801 | 0.00067801 | 0.00080982
| Acetaldehyde | 75-07-0 | 0.7833 | 0 | N/A | 0 | 0.7833
| Acrolein | 107-02-8 | 0.0339 |  | N/A | 0.0339 | 0.0339
| Ammonia | 7664-41-7 | 0.8 |  | N/A | 0.8 | 0.8
| Anthracene - PAH | 120-12-7 | 0.00045209 |  | 0.00031409 | 0.00031409 | 0.00045209
| Antimony | 7440-36-0 | 0.00031819 |  | 0.00025439 | 0.00025439 | 0.00031819
| Arsenic | 7440-38-2 | 0.00027685 |  | 0.000194 | 0.000194 | 0.00027685
| Barium | 7440-39-3 | 0.00037389 |  | 0.00069107 | 0.00069107 | 0.00037389
| Benz[a]anthracene - PAH | 56-55-3 | 4.8541e-05 |  | 4.0027e-05 | 4.0027e-05 | 4.8541e-05
| Benzene | 71-43-2 | 0.1863 | 0 | N/A | 0 | 0.1863
| Benzo[a]pyrene - PAH | 50-32-8 | 1.4385e-05 |  | 1.2753e-05 | 1.2753e-05 | 1.4385e-05
| Benzo[b]fluoranthene - PAH | 205-99-2 | 4.4354e-05 |  | 3.3872e-05 | 3.3872e-05 | 4.4354e-05
| Benzo[e]pyrene - PAH | 192-97-2 | 3.2868e-05 |  | 2.5584e-05 | 2.5584e-05 | 3.2868e-05
| Benzo[g,h,i]perylene - PAH | 191-24-2 | 2.1874e-05 |  | 1.9128e-05 | 1.9128e-05 | 2.1874e-05
| Benzo[k]fluoranthene - PAH | 207-08-9 | 1.3054e-05 |  | 1.0142e-05 | 1.0142e-05 | 1.3054e-05
| Beryllium | 7440-41-7 | 4.7708e-06 |  | 0 | 0 | 4.7708e-06
| Cadmium | 7440-43-9 | 8.0778e-05 |  | 0 | 0 | 8.0778e-05
| Chlorobenzene | 108-90-7 | 0.0002 |  | N/A | 0.0002 | 0.0002
| Chrysene - PAH | 218-01-9 | 6.7e-05 |  | 6.3539e-05 | 6.3539e-05 | 6.7e-05
| Cobalt | 7440-48-4 | 1.5751e-05 |  | 0 | 0 | 1.5751e-05
| Copper | 7440-50-8 | 0.00050214 |  | 0 | 0 | 0.00050214
| Dibenz[a,h]anthracene - PAH | 53-70-3 | 1.037e-06 |  | 2.67e-07 | 2.67e-07 | 1.037e-06
| Ethyl Benzene | 100-41-4 | 0.0109 | 0 | N/A | 0 | 0.0109
| Fluoranthene - PAH | 206-44-0 | 0.00036995 |  | 0.00026724 | 0.00026724 | 0.00036995
| Fluorene - PAH | 86-73-7 | 0.0021844 |  | 0.0015662 | 0.0015662 | 0.0021844
| Formaldehyde | 50-00-0 | 2.7131 | 2.2863 | N/A | 2.2863 | 2.7131
| Hexane | 110-54-3 | 0.0269 | 0 | N/A | 0 | 0.0269
| Hexavalent Chromium5 | 18540-29-9 | 6.3144e-05 |  | 0.00033122 | 0.00033122 | 6.3144e-05
| Hydrogen Chloride | 7647-01-0 | 0.1863 |  | N/A | 0.1863 | 0.1863
| Indeno[1,2,3-cd]pyrene - PAH | 193-39-5 | 1.0711e-05 |  | 7.8508e-06 | 7.8508e-06 | 1.0711e-05
| Lead | 7439-92-1 | 0.00036367 |  | 0.000238 | 0.000238 | 0.00036367
| Manganese | 7439-96-5 | 0.00041991 |  | 0.00020767 | 0.00020767 | 0.00041991
| Mercury | 7439-97-6 | 1.5107e-05 |  | 1.28e-05 | 1.28e-05 | 1.5107e-05
| 2-Methyl naphthalene - PAH | 91-57-6 | 0.012298 |  | 0.0087984 | 0.0087984 | 0.012298
| Naphthalene - PAH | 91-20-3 | 0.026352 |  | 0.017002 | 0.017002 | 0.026352
| Nickel | 365 | 0.00018223 |  | 0.00018612 | 0.00018612 | 0.00018223
| Perylene - PAH | 198-55-0 | 1.1782e-06 |  | 3.51e-07 | 3.51e-07 | 1.1782e-06
| Phenanthrene - PAH | 85-01-8 | 0.0045419 |  | 0.0038314 | 0.0038314 | 0.0045419
| Phosphorus | 504 | 0.008404 |  | 0.00549 | 0.00549 | 0.008404
| Propylene | 115-07-1 | 0.47 |  | N/A | 0.47 | 0.47
| Pyrene - PAH | 129-00-0 | 0.00125 |  | 0.00094044 | 0.00094044 | 0.00125
| PAHs (excl. Naphthalene)6 | 401 | N/A |  | N/A
| Selenium | 7782-49-2 | 0.00037638 |  | 0 | 0 | 0.00037638
| Silver | 7440-22-4 | 4.8013e-05 |  | 0 | 0 | 4.8013e-05
| Thallium | 7440-28-0 | 0.00024009 |  | 0 | 0 | 0.00024009
| Toluene | 108-88-3 | 0.1054 |  | N/A | 0.1054 | 0.1054
| Xylenes | 1330-20-7 | 0.0424 |  | N/A | 0.0424 | 0.0424
| Zinc | 7440-66-6 | 0.0052262 |  | 0.0050308 | 0.0050308 | 0.0052262
1 Oregon DEQ emission factors are obtained from Oregon DEQ Toxics Reporting & Air Toxics Emissions Inventory (ATEI) Combustion Emission Factor Search Tool for Post-2006 Tier 2, 3, and 4 Diesel Internal Combustion Engines is used. The emission factor for equipment without SNCR or SCR is used for ammonia.
2 Stack testing was completed for the CAT 3516C 2,500 kW generators on March 5-8, 2019. Stack testing was completed at 10%, 25%, 50%, 75%, and 100% load. If all runs show non-detect values they are reported as zero emissions consistent with the Oregon DEQ guidance document: Recommended Procedures for Toxic Air Contaminant Health Risk Assessments (October 2022). These were previously approved by Oregon DEQ. Non-zero values that were not re-tested in 2021 are detailed in Table D1-5 with the three run results at 10% load and 100% load levels. A safety factor has been added to these emission factors as shown in Table D1-5.
3 Stack testing for diesel particulate matter, metals, and PAHs was completed on September 21, 23-24, and 27-29, 2021 at ADS PDX90 site on a CAT 3516C 2,500 kW generator. The test was completed over a 6 hour time period to ensure enough exhaust volume at low load levels was procured to accurately detect potential pollutants. Oregon DEQ provided CAO approved emission factors in the 1/14/2022 Source Test Review Report Memorandum. A safety factor has been added to these emission factors as shown in Tables C1-3 and C1-4.
4 ADS is preferentially using emission factors resulting from the 2021 stack test. If pollutants were not tested, the 2019 stack test results are used. Additionally, if pollutants were not tested, the Oregon DEQ emission factors are used.
5 Total chromium was tested during the 2021 stack test. The results from this test are being used to describe hexavalent chromium (ODEQ Toxic listed in OAR 340-245-8010 Table 2).
6 Poly aromatic hydrocarbons (PAHs) is a group of toxic pollutants. Since source testing was completed for specific PAHs for the CAT3516HD generator, the PAHs are included individually instead of as a summation for these engines.
Table D1-2. Diesel Particulate Matter Emission Factor Determination
| Pollutant | CAS/DEQ ID | Emission Factor 1,2 (lbs/1000 gal)
|  |  | CAT 27 750 kW | CAT 27 800 kW | CAT 32 1,000 kW | CAT 3516C Trans 1,825 kW | CAT 3516C 2,000 kW | CAT 3516C 2,500 kW | MTU 2250 2,250 kW | CAT C18 750 kW | CAT 3512C 1500 kW
| Diesel Particulate Matter | 200 | 23.38 | 23.38 | 23.38 | 23.38 | 23.38 | 16.9752 | 23.38 | 234.7368 | 23.38
1 | The diesel particulate matter emission factor for the CAT 2500 kW engine is obtained from the 2021 stack test. The 2021 stack test determination is expanded upon in Table 3 below. Diesel particulate matter emission factors for all other engine types are obtained from the manufacturer's PM + HC data (worst-case load). The emission factor included in the manufacturer’s specifications for these units uses Method 1065 to determine PM emissions and only includes filterable particulate matter. In the absence of specific stationary source stack test information (as used for the 2,500 kW stationary generators), a factor of filterable particulate matter plus measured hydrocarbon has been used to account for condensable particulate matter per Oregon DEQ's request.
2 | Oregon DEQ approved emission factor of 23.38 lb/1000 gal for diesel particulate matter for units > 560 kW derived based on statistic evaluation of all engine test data available in Oregon on August 15, 2022. Emission factors for units > 560 kW determined by comparing the Oregon DEQ approved emission factor with Manufacturer's PM + HC data. The lesser of the two values was used for each of these units; unless the manufacturer's specification shows a higher PM value than Oregon DEQ's emission factor at the specified load level (ex. C18 750 kW). The units with an associated DPF use the below control efficiencies applied to each constituent in the PM + HC scenario.

## Screening Emission Calculations
Table D2-1. Screening Annual Emission Summary
| Pollutant | CAS/DEQ ID | Cold Start? 2 | Maximum Projected Emissions (lbs/yr/generator) 1,3
|  |  |  | CAT 27 - 750 kW | CAT 27 - 800 kW | CAT 32 - 1000 kW | CAT 3516C Trans - 1825 kW | CAT 3516C - 2000 kW | CAT 3516C - 2500 kW | MTU 2250 - 2250 kW | CAT C18 - 750 kW | CAT 3512C - 1500 kW
| 1,3-Butadiene | 106-99-0 | Yes | 1.1843 | 1.266 | 1.5886 | 2.837 | 3.069 | 0 | 3.6015 | 1.1843 | 2.2802
| Acenaphthene | 83-32-9 | Yes | 0.0040018 | 0.0042781 | 0.0053681 | 0.0095865 | 0.01037 | 0.010044 | 0.01217 | 0.0040018 | 0.007705
| Acenaphthylene | 208-96-8 | Yes | 0.0044115 | 0.004716 | 0.0059177 | 0.010568 | 0.011432 | 0.011956 | 0.013416 | 0.0044115 | 0.0084938
| Acetaldehyde | 75-07-0 | Yes | 4.2671 | 4.5616 | 5.7239 | 10.2218 | 11.0577 | 0 | 12.9763 | 4.2671 | 8.2157
| Acrolein | 107-02-8 | Yes | 0.18467 | 0.19742 | 0.24772 | 0.44239 | 0.47856 | 0.59777 | 0.5616 | 0.18467 | 0.35556
| Ammonia | 7664-41-7 | No | 4.288 | 4.584 | 5.752 | 10.272 | 11.112 | 13.88 | 13.04 | 4.288 | 8.256
| Anthracene | 120-12-7 | Yes | 0.0024628 | 0.0026328 | 0.0033036 | 0.0058996 | 0.0063821 | 0.0055384 | 0.0074894 | 0.0024628 | 0.0047418
| Antimony | 7440-36-0 | No | 0.0017055 | 0.0018232 | 0.0022878 | 0.0040855 | 0.0044196 | 0.0044136 | 0.0051865 | 0.0017055 | 0.0032837
| Arsenic | 7440-38-2 | No | 0.0014839 | 0.0015864 | 0.0019906 | 0.0035548 | 0.0038455 | 0.0033659 | 0.0045127 | 0.0014839 | 0.0028571
| Barium | 7440-39-3 | No | 0.0020041 | 0.0021424 | 0.0026883 | 0.0048008 | 0.0051934 | 0.01199 | 0.0060945 | 0.0020041 | 0.0038586
| Benz[a]anthracene | 56-55-3 | Yes | 0.00026443 | 0.00028268 | 0.00035471 | 0.00063345 | 0.00068525 | 0.00070582 | 0.00080415 | 0.00026443 | 0.00050913
| Benzene | 71-43-2 | Yes | 1.0149 | 1.0849 | 1.3614 | 2.4312 | 2.63 | 0 | 3.0863 | 1.0149 | 1.954
| Benzo[a]pyrene | 50-32-8 | Yes | 7.8364e-05 | 8.3774e-05 | 0.00010512 | 0.00018772 | 0.00020307 | 0.00022488 | 0.00023831 | 7.8364e-05 | 0.00015088
| Benzo[b]fluoranthene | 205-99-2 | Yes | 0.00024162 | 0.0002583 | 0.00032411 | 0.0005788 | 0.00062613 | 0.00059728 | 0.00073477 | 0.00024162 | 0.00046521
| Benzo[e]pyrene | 192-97-2 | Yes | 0.00017905 | 0.00019141 | 0.00024018 | 0.00042892 | 0.000464 | 0.00045114 | 0.0005445 | 0.00017905 | 0.00034474
| Benzo[g,h,i]perylene | 191-24-2 | Yes | 0.00011916 | 0.00012739 | 0.00015985 | 0.00028545 | 0.0003088 | 0.00033729 | 0.00036237 | 0.00011916 | 0.00022943
| Benzo[k]fluoranthene | 207-08-9 | Yes | 7.1114e-05 | 7.6023e-05 | 9.5394e-05 | 0.00017036 | 0.00018429 | 0.00017884 | 0.00021626 | 7.1114e-05 | 0.00013692
| Beryllium | 7440-41-7 | No | 2.5572e-05 | 2.7337e-05 | 3.4302e-05 | 6.1258e-05 | 6.6267e-05 | 0 | 7.7765e-05 | 2.5572e-05 | 4.9235e-05
| Cadmium | 7440-43-9 | No | 0.00043297 | 0.00046286 | 0.0005808 | 0.0010372 | 0.001122 | 0 | 0.0013167 | 0.00043297 | 0.00083363
| Chlorobenzene | 108-90-7 | Yes | 0.0010895 | 0.0011647 | 0.0014615 | 0.0026099 | 0.0028234 | 0.0035267 | 0.0033132 | 0.0010895 | 0.0020977
| Chrysene | 218-01-9 | Yes | 0.00036499 | 0.00039018 | 0.0004896 | 0.00087433 | 0.00094583 | 0.0011204 | 0.0011099 | 0.00036499 | 0.00070273
| Cobalt | 7440-48-4 | No | 8.4426e-05 | 9.0254e-05 | 0.00011325 | 0.00020224 | 0.00021878 | 0 | 0.00025674 | 8.4426e-05 | 0.00016255
| Copper | 7440-50-8 | No | 0.0026914 | 0.0028772 | 0.0036104 | 0.0064474 | 0.0069747 | 0 | 0.0081848 | 0.0026914 | 0.005182
| Dibenz[a,h]anthracene | 53-70-3 | Yes | 5.649e-06 | 6.039e-06 | 7.5777e-06 | 1.3532e-05 | 1.4639e-05 | 4.7081e-06 | 1.7179e-05 | 5.649e-06 | 1.0876e-05
| Diesel Particulate Matter | 200 | Yes | 127.3636 | 136.1555 | 170.8479 | 305.1025 | 330.0524 | 299.331 | 387.3185 | 1278.7399 | 245.2225
| Ethyl Benzene | 100-41-4 | Yes | 0.059378 | 0.063477 | 0.079651 | 0.14224 | 0.15387 | 0 | 0.18057 | 0.059378 | 0.11433
| Fluoranthene | 206-44-0 | Yes | 0.0020153 | 0.0021545 | 0.0027034 | 0.0048278 | 0.0052226 | 0.0047124 | 0.0061287 | 0.0020153 | 0.0038803
| Fluorene | 86-73-7 | Yes | 0.0119 | 0.012721 | 0.015962 | 0.028506 | 0.030837 | 0.027617 | 0.036187 | 0.0119 | 0.022911
| Formaldehyde | 50-00-0 | Yes | 14.8207 | 15.8438 | 19.8808 | 35.5034 | 38.4067 | 40.4274 | 45.0705 | 14.8207 | 28.5355
| Hexane | 110-54-3 | Yes | 0.14654 | 0.15665 | 0.19657 | 0.35104 | 0.37974 | 0 | 0.44563 | 0.14654 | 0.28214
| Hexavalent chromium | 18540-29-9 | No | 0.00033845 | 0.00036182 | 0.00045401 | 0.00081077 | 0.00087708 | 0.0057466 | 0.0010293 | 0.00033845 | 0.00065165
| Hydrogen Chloride | 7647-01-0 | Yes | 1.0149 | 1.0849 | 1.3614 | 2.4312 | 2.63 | 3.2851 | 3.0863 | 1.0149 | 1.954
| Indeno[1,2,3-cd]pyrene | 193-39-5 | Yes | 5.8349e-05 | 6.2376e-05 | 7.827e-05 | 0.00013978 | 0.00015121 | 0.00013844 | 0.00017744 | 5.8349e-05 | 0.00011234
| Lead | 7439-92-1 | No | 0.0019493 | 0.0020838 | 0.0026148 | 0.0046695 | 0.0050514 | 0.0041293 | 0.0059278 | 0.0019493 | 0.0037531
| Manganese | 7439-96-5 | No | 0.0022507 | 0.0024061 | 0.0030192 | 0.0053917 | 0.0058326 | 0.003603 | 0.0068446 | 0.0022507 | 0.0043335
| Mercury | 7439-97-6 | No | 8.0975e-05 | 8.6565e-05 | 0.00010862 | 0.00019398 | 0.00020984 | 0.00022208 | 0.00024625 | 8.0975e-05 | 0.00015591
| 2-Methyl naphthalene | 91-57-6 | Yes | 0.066993 | 0.071618 | 0.089866 | 0.16048 | 0.17361 | 0.15514 | 0.20373 | 0.066993 | 0.12899
| Naphthalene | 91-20-3 | Yes | 0.14356 | 0.15347 | 0.19257 | 0.34389 | 0.37201 | 0.29979 | 0.43656 | 0.14356 | 0.2764
| Nickel | 365 | No | 0.00097675 | 0.0010442 | 0.0013102 | 0.0023398 | 0.0025312 | 0.0032292 | 0.0029703 | 0.00097675 | 0.0018806
| Perylene | 198-55-0 | Yes | 6.4186e-06 | 6.8616e-06 | 8.61e-06 | 1.5376e-05 | 1.6633e-05 | 6.1893e-06 | 1.9519e-05 | 6.4186e-06 | 1.2358e-05
| Phenanthrene | 85-01-8 | Yes | 0.024742 | 0.02645 | 0.03319 | 0.059271 | 0.064118 | 0.06756 | 0.075243 | 0.024742 | 0.047638
| Phosphorus | 504 | No | 0.045045 | 0.048155 | 0.060425 | 0.10791 | 0.11673 | 0.095252 | 0.13698 | 0.045045 | 0.086729
| Propylene | 115-07-1 | Yes | 2.5603 | 2.7371 | 3.4345 | 6.1334 | 6.6349 | 8.2877 | 7.7861 | 2.5603 | 4.9296
| Pyrene | 129-00-0 | Yes | 0.0068094 | 0.0072795 | 0.0091343 | 0.016312 | 0.017646 | 0.016583 | 0.020708 | 0.0068094 | 0.013111
| PAHs (excluding Naphthalene) | 401 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Selenium | 7782-49-2 | No | 0.0020174 | 0.0021567 | 0.0027062 | 0.0048328 | 0.005228 | 0 | 0.006135 | 0.0020174 | 0.0038843
| Silver | 7440-22-4 | No | 0.00025735 | 0.00027511 | 0.00034521 | 0.00061649 | 0.0006669 | 0 | 0.00078261 | 0.00025735 | 0.00049549
| Thallium | 7440-28-0 | No | 0.0012869 | 0.0013757 | 0.0017263 | 0.0030828 | 0.0033349 | 0 | 0.0039135 | 0.0012869 | 0.0024778
| Toluene | 108-88-3 | Yes | 0.57417 | 0.61381 | 0.7702 | 1.3754 | 1.4879 | 1.8586 | 1.7461 | 0.57417 | 1.1055
| Xylenes | 1330-20-7 | Yes | 0.23098 | 0.24692 | 0.30984 | 0.55331 | 0.59856 | 0.74766 | 0.70241 | 0.23098 | 0.44471
| Zinc | 7440-66-6 | No | 0.028012 | 0.029946 | 0.037576 | 0.067104 | 0.072592 | 0.087285 | 0.085187 | 0.028012 | 0.053934
1 | Estimated fuel throughput for each generator type based on 100 hours of operation at 100% load. The 100% load fuel use for the CAT 3516C 2,500 kW generator has changed with different installation years. ADS has chosen the highest fuel throughput per hour for these calculations.
| CAT 27 - 750 kW | 5360 | gallons/year for | 1 | engine at | 53.6 | gallon per hour per engine at 100% load
| CAT 27 - 800 kW | 5730 | gallons/year for | 1 | engine at | 57.3 | gallon per hour per engine at 100% load
| CAT 32 - 1000 kW | 7190 | gallons/year for | 1 | engine at | 71.9 | gallon per hour per engine at 100% load
| CAT 3516C Trans - 1825 kW | 12840 | gallons/year for | 1 | engine at | 128.4 | gallon per hour per engine at 100% load
| CAT 3516C - 2000 kW | 13890 | gallons/year for | 1 | engine at | 138.9 | gallon per hour per engine at 100% load
| CAT 3516C - 2500 kW | 17350 | gallons/year for | 1 | engine at | 173.5 | gallon per hour per engine at 100% load
| MTU 2250 - 2250 kW | 16300 | gallons/year for | 1 | engine at | 163 | gallon per hour per engine at 100% load
| CAT C18 - 750 kW | 5360 | gallons/year for | 1 | engine at | 53.6 | gallon per hour per engine at 100% load
| CAT 3512C - 1500 kW | 10320 | gallons/year for | 1 | engine at | 103.2 | gallon per hour per engine at 100% load
2 | Diesel PM emission rate also accounts for the cold start emissions. Spike duration, cold-start emission spike, and steady-state (warm) emissions based on data from California Energy Commission (CEC) "Air Quality Implications of Backup Generators in California. The cold-start scaling factor is derived as the ratio of the spike concentration and duration to the steady-state emissions for the initial 60 seconds. Since a cold-start curve was not developed by CEC, it is assumed that the PM will experience the same trend as HC, and formaldehyde will experience the same trend as CO. A cold start event assumes 1 minute of cold start operation with spike in emissions and the remaining 59 minutes in the hour operating steady state. The cold start emission ratio shown below on hourly basis will be applied as: the hourly emission rate with cold start event = normal hourly emission rate x (1+ratio shown below on hourly basis). Consistent with DEQ's guidance on risk assessment for emergency engines, the cold start emissions are accounted for toxics that are organics and DPM. Metal toxics do not have higher emissions during cold start events.
| Pollutant | Spike Duration (seconds) | Cold-Start Emission Spike (ppm) | Steady-State (Warm) Emissions (ppm) | Cold-Start Scaling Factor | Cold Start Emission Ratio on Hourly Basis
| PM and Organics | 14 | 900 | 30 | 4.2667 | 0.054444
| CO and Formaldehyde | 20 | 750 | 30 | 4.8333 | 0.063889
3 | It is assumed that each CAT generator has 28 cold start events per year (accounting for commissioning, load bank testing and bimonthly testing).
| CAT 27 - 750 kW | 30 | cold start events/yr.
| CAT 27 - 800 kW | 30 | cold start events/yr.
| CAT 32 - 1000 kW | 30 | cold start events/yr.
| CAT 3516C Trans - 1825 kW | 30 | cold start events/yr.
| CAT 3516C - 2000 kW | 30 | cold start events/yr.
| CAT 3516C - 2500 kW | 30 | cold start events/yr.
| MTU 2250 - 2250 kW | 30 | cold start events/yr.
| CAT C18 - 750 kW | 30 | cold start events/yr.
| CAT 3512C - 1500 kW | 30 | cold start events/yr.
Table D2-2. Screening Daily Emission Summary
| Pollutant | CAS/DEQ ID | Cold Start? 2 | Maximum Projected Emissions (lbs/day/generator) 1,3
|  |  |  | CAT 27 - 750 kW | CAT 27 - 800 kW | CAT 32 - 1000 kW | CAT 3516C Trans - 1825 kW | CAT 3516C - 2000 kW | CAT 3516C - 2500 kW | MTU 2250 - 2250 kW | CAT C18 - 750 kW | CAT 3512C - 1500 kW
| 1,3-Butadiene | 106-99-0 | Yes | 0.2803 | 0.29965 | 0.376 | 0.67146 | 0.72637 | 0 | 0.8524 | 0.2803 | 0.53968
| Acenaphthene | 83-32-9 | Yes | 0.00094715 | 0.0010125 | 0.0012705 | 0.0022689 | 0.0024545 | 0.0023773 | 0.0028803 | 0.00094715 | 0.0018236
| Acenaphthylene | 208-96-8 | Yes | 0.0010441 | 0.0011162 | 0.0014006 | 0.0025012 | 0.0027057 | 0.0028296 | 0.0031752 | 0.0010441 | 0.0020103
| Acetaldehyde | 75-07-0 | Yes | 1.0099 | 1.0796 | 1.3547 | 2.4193 | 2.6171 | 0 | 3.0712 | 1.0099 | 1.9445
| Acrolein | 107-02-8 | Yes | 0.043708 | 0.046725 | 0.058631 | 0.1047 | 0.11327 | 0.14148 | 0.13292 | 0.043708 | 0.084154
| Ammonia* | 7664-41-7 | No | 1.0291 | 1.1002 | 1.3805 | 2.4653 | 2.6669 | 3.3312 | 3.1296 | 1.0291 | 1.9814
| Anthracene | 120-12-7 | Yes | 0.00058289 | 0.00062312 | 0.0007819 | 0.0013963 | 0.0015105 | 0.0013108 | 0.0017726 | 0.00058289 | 0.0011223
| Antimony | 7440-36-0 | No | 0.00040932 | 0.00043757 | 0.00054906 | 0.00098053 | 0.0010607 | 0.0010593 | 0.0012447 | 0.00040932 | 0.00078809
| Arsenic | 7440-38-2 | No | 0.00035614 | 0.00038073 | 0.00047774 | 0.00085315 | 0.00092292 | 0.00080782 | 0.001083 | 0.00035614 | 0.00068571
| Barium | 7440-39-3 | No | 0.00048098 | 0.00051418 | 0.00064519 | 0.0011522 | 0.0012464 | 0.0028776 | 0.0014627 | 0.00048098 | 0.00092606
| Benz[a]anthracene | 56-55-3 | Yes | 6.2585e-05 | 6.6905e-05 | 8.3953e-05 | 0.00014992 | 0.00016218 | 0.00016705 | 0.00019032 | 6.2585e-05 | 0.0001205
| Benzene | 71-43-2 | Yes | 0.2402 | 0.25678 | 0.32221 | 0.5754 | 0.62246 | 0 | 0.73046 | 0.2402 | 0.46247
| Benzo[a]pyrene | 50-32-8 | Yes | 1.8547e-05 | 1.9827e-05 | 2.4879e-05 | 4.443e-05 | 4.8063e-05 | 5.3224e-05 | 5.6403e-05 | 1.8547e-05 | 3.571e-05
| Benzo[b]fluoranthene | 205-99-2 | Yes | 5.7186e-05 | 6.1133e-05 | 7.671e-05 | 0.00013699 | 0.00014819 | 0.00014136 | 0.0001739 | 5.7186e-05 | 0.0001101
| Benzo[e]pyrene | 192-97-2 | Yes | 4.2378e-05 | 4.5303e-05 | 5.6846e-05 | 0.00010152 | 0.00010982 | 0.00010677 | 0.00012887 | 4.2378e-05 | 8.1593e-05
| Benzo[g,h,i]perylene | 191-24-2 | Yes | 2.8203e-05 | 3.015e-05 | 3.7832e-05 | 6.7561e-05 | 7.3086e-05 | 7.983e-05 | 8.5766e-05 | 2.8203e-05 | 5.4301e-05
| Benzo[k]fluoranthene | 207-08-9 | Yes | 1.6831e-05 | 1.7993e-05 | 2.2578e-05 | 4.032e-05 | 4.3617e-05 | 4.2328e-05 | 5.1185e-05 | 1.6831e-05 | 3.2406e-05
| Beryllium | 7440-41-7 | No | 6.1372e-06 | 6.5609e-06 | 8.2326e-06 | 1.4702e-05 | 1.5904e-05 | 0 | 1.8664e-05 | 6.1372e-06 | 1.1816e-05
| Cadmium | 7440-43-9 | No | 0.00010391 | 0.00011109 | 0.00013939 | 0.00024893 | 0.00026928 | 0 | 0.000316 | 0.00010391 | 0.00020007
| Chlorobenzene | 108-90-7 | Yes | 0.00025786 | 0.00027566 | 0.0003459 | 0.00061772 | 0.00066823 | 0.00083469 | 0.00078417 | 0.00025786 | 0.00049648
| Chrysene | 218-01-9 | Yes | 8.6384e-05 | 9.2347e-05 | 0.00011588 | 0.00020694 | 0.00022386 | 0.00026518 | 0.0002627 | 8.6384e-05 | 0.00016632
| Cobalt | 7440-48-4 | No | 2.0262e-05 | 2.1661e-05 | 2.718e-05 | 4.8539e-05 | 5.2508e-05 | 0 | 6.1618e-05 | 2.0262e-05 | 3.9012e-05
| Copper | 7440-50-8 | No | 0.00064595 | 0.00069054 | 0.00086648 | 0.0015474 | 0.0016739 | 0 | 0.0019644 | 0.00064595 | 0.0012437
| Dibenz[a,h]anthracene | 53-70-3 | Yes | 1.337e-06 | 1.4293e-06 | 1.7935e-06 | 3.2028e-06 | 3.4647e-06 | 1.1143e-06 | 4.0659e-06 | 1.337e-06 | 2.5742e-06
| Diesel Particulate Matter | 200 | Yes | 30.1443 | 32.2251 | 40.4361 | 72.2112 | 78.1164 | 70.8453 | 91.67 | 302.6505 | 58.0389
| Ethyl Benzene | 100-41-4 | Yes | 0.014054 | 0.015024 | 0.018852 | 0.033666 | 0.036419 | 0 | 0.042738 | 0.014054 | 0.027058
| Fluoranthene | 206-44-0 | Yes | 0.00047699 | 0.00050991 | 0.00063984 | 0.0011426 | 0.0012361 | 0.0011153 | 0.0014505 | 0.00047699 | 0.00091838
| Fluorene | 86-73-7 | Yes | 0.0028164 | 0.0030108 | 0.0037779 | 0.0067467 | 0.0072984 | 0.0065363 | 0.0085647 | 0.0028164 | 0.0054226
| Formaldehyde | 50-00-0 | Yes | 3.4994 | 3.7409 | 4.6941 | 8.3828 | 9.0683 | 9.5454 | 10.6418 | 3.4994 | 6.7376
| Hexane | 110-54-3 | Yes | 0.034683 | 0.037077 | 0.046524 | 0.083083 | 0.089877 | 0 | 0.10547 | 0.034683 | 0.066777
| Hexavalent chromium | 18540-29-9 | No | 8.1229e-05 | 8.6836e-05 | 0.00010896 | 0.00019459 | 0.0002105 | 0.0013792 | 0.00024702 | 8.1229e-05 | 0.0001564
| Hydrogen Chloride | 7647-01-0 | Yes | 0.2402 | 0.25678 | 0.32221 | 0.5754 | 0.62246 | 0.77751 | 0.73046 | 0.2402 | 0.46247
| Indeno[1,2,3-cd]pyrene | 193-39-5 | Yes | 1.381e-05 | 1.4763e-05 | 1.8525e-05 | 3.3082e-05 | 3.5787e-05 | 3.2765e-05 | 4.1996e-05 | 1.381e-05 | 2.6589e-05
| Lead | 7439-92-1 | No | 0.00046783 | 0.00050012 | 0.00062755 | 0.0011207 | 0.0012123 | 0.00099103 | 0.0014227 | 0.00046783 | 0.00090074
| Manganese | 7439-96-5 | No | 0.00054018 | 0.00057746 | 0.0007246 | 0.001294 | 0.0013998 | 0.00086473 | 0.0016427 | 0.00054018 | 0.00104
| Mercury | 7439-97-6 | No | 1.9434e-05 | 2.0776e-05 | 2.6069e-05 | 4.6555e-05 | 5.0362e-05 | 5.3299e-05 | 5.91e-05 | 1.9434e-05 | 3.7418e-05
| 2-Methyl naphthalene | 91-57-6 | Yes | 0.015856 | 0.01695 | 0.021269 | 0.037983 | 0.041089 | 0.036719 | 0.048219 | 0.015856 | 0.030529
| Naphthalene | 91-20-3 | Yes | 0.033977 | 0.036322 | 0.045577 | 0.081392 | 0.088048 | 0.070955 | 0.10332 | 0.033977 | 0.065418
| Nickel | 365 | No | 0.00023442 | 0.0002506 | 0.00031445 | 0.00056156 | 0.00060748 | 0.00077502 | 0.00071288 | 0.00023442 | 0.00045135
| Perylene | 198-55-0 | Yes | 1.5191e-06 | 1.624e-06 | 2.0378e-06 | 3.6391e-06 | 3.9367e-06 | 1.4649e-06 | 4.6198e-06 | 1.5191e-06 | 2.9249e-06
| Phenanthrene | 85-01-8 | Yes | 0.005856 | 0.0062603 | 0.0078554 | 0.014028 | 0.015175 | 0.01599 | 0.017808 | 0.005856 | 0.011275
| Phosphorus | 504 | No | 0.010811 | 0.011557 | 0.014502 | 0.025898 | 0.028016 | 0.022861 | 0.032876 | 0.010811 | 0.020815
| Propylene | 115-07-1 | Yes | 0.60598 | 0.64781 | 0.81287 | 1.4516 | 1.5703 | 1.9615 | 1.8428 | 0.60598 | 1.1667
| Pyrene | 129-00-0 | Yes | 0.0016116 | 0.0017229 | 0.0021619 | 0.0038607 | 0.0041765 | 0.0039249 | 0.0049011 | 0.0016116 | 0.003103
| PAHs (excluding Naphthalene) | 401 | Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Selenium | 7782-49-2 | No | 0.00048418 | 0.0005176 | 0.00064949 | 0.0011599 | 0.0012547 | 0 | 0.0014724 | 0.00048418 | 0.00093222
| Silver | 7440-22-4 | No | 6.1764e-05 | 6.6027e-05 | 8.2851e-05 | 0.00014796 | 0.00016006 | 0 | 0.00018783 | 6.1764e-05 | 0.00011892
| Thallium | 7440-28-0 | No | 0.00030886 | 0.00033018 | 0.00041431 | 0.00073987 | 0.00080038 | 0 | 0.00093925 | 0.00030886 | 0.00059466
| Toluene | 108-88-3 | Yes | 0.13589 | 0.14527 | 0.18229 | 0.32554 | 0.35216 | 0.43988 | 0.41326 | 0.13589 | 0.26165
| Xylenes | 1330-20-7 | Yes | 0.054667 | 0.058441 | 0.073331 | 0.13096 | 0.14167 | 0.17695 | 0.16625 | 0.054667 | 0.10525
| Zinc | 7440-66-6 | No | 0.006723 | 0.007187 | 0.0090183 | 0.016105 | 0.017422 | 0.020948 | 0.020445 | 0.006723 | 0.012944
1 | Estimated fuel throughput for each generator type based on 100 hours of operation at 100% load. The 100% load fuel use for the CAT 3516C 2,500 kW generator has changed with different installation years. ADS has chosen the highest fuel throughput per hour for these calculations.
| CAT 27 - 750 kW | 24 | hrs/day = | 1286.4 | gallons/day with | 53.6 | gallon per hour per engine at 100% load
| CAT 27 - 800 kW | 24 | hrs/day = | 1375.2 | gallons/day with | 57.3 | gallon per hour per engine at 100% load
| CAT 32 - 1000 kW | 24 | hrs/day = | 1725.6 | gallons/day with | 71.9 | gallon per hour per engine at 100% load
| CAT 3516C Trans - 1825 kW | 24 | hrs/day = | 3081.6 | gallons/day with | 128.4 | gallon per hour per engine at 100% load
| CAT 3516C - 2000 kW | 24 | hrs/day = | 3333.6 | gallons/day with | 138.9 | gallon per hour per engine at 100% load
| CAT 3516C - 2500 kW | 24 | hrs/day = | 4164 | gallons/day with | 173.5 | gallon per hour per engine at 100% load
| MTU 2250 - 2250 kW | 24 | hrs/day = | 3912 | gallons/day with | 163 | gallon per hour per engine at 100% load
| CAT C18 - 750 kW | 24 | hrs/day = | 1286.4 | gallons/day with | 53.6 | gallon per hour per engine at 100% load
| CAT 3512C - 1500 kW | 24 | hrs/day = | 2476.8 | gallons/day with | 103.2 | gallon per hour per engine at 100% load
2 | Diesel PM emission rate also accounts for the cold start emissions. Spike duration, cold-start emission spike, and steady-state (warm) emissions based on data from California Energy Commission (CEC) "Air Quality Implications of Backup Generators in California. The cold-start scaling factor is derived as the ratio of the spike concentration and duration to the steady-state emissions for the initial 60 seconds. Since a cold-start curve was not developed by CEC, it is assumed that the PM will experience the same trend as HC, and formaldehyde will experience the same trend as CO. A cold start event assumes 1 minute of cold start operation with spike in emissions and the remaining 59 minutes in the hour operating steady state. The cold start emission ratio shown below on hourly basis will be applied as: the hourly emission rate with cold start event = normal hourly emission rate x (1+ratio shown below on hourly basis). Consistent with DEQ's guidance on risk assessment for emergency engines, the cold start emissions are accounted for toxics that are organics and DPM. Metal toxics do not have higher emissions during cold start events.
| Pollutant | Spike Duration (seconds) | Cold-Start Emission Spike (ppm) | Steady-State (Warm) Emissions (ppm) | Cold-Start Scaling Factor | Cold Start Emission Ratio on Hourly Basis
| PM and Organics | 14 | 900 | 30 | 4.2667 | 0.054444
| CO and Formaldehyde | 20 | 750 | 30 | 4.8333 | 0.063889
3 | Number of cold start events assumes 1 startup for each engine.
| CAT 27 - 750 kW | 1 | cold start events/day
| CAT 27 - 800 kW | 1 | cold start events/day
| CAT 32 - 1000 kW | 1 | cold start events/day
| CAT 3516C Trans - 1825 kW | 1 | cold start events/day
| CAT 3516C - 2000 kW | 1 | cold start events/day
| CAT 3516C - 2500 kW | 1 | cold start events/day
| MTU 2250 - 2250 kW | 1 | cold start events/day
| CAT C18 - 750 kW | 1 | cold start events/day
| CAT 3512C - 1500 kW | 1 | cold start events/day

## Screening REER
Table F1-1. ODEQ Risk Based Concentrations
| Pollutant | CAS/DEQ ID | Toxic Pollutant has an RBC? 1 | Non-cancer Class | Risk-Based Concentrations ( µg/m3 )
[5 empty] | Residential Chronic |  | Non-residential Chronic |  |  |  | Acute Non-cancer
[5 empty] | Chronic Cancer | Chronic Non-cancer | Child Cancer | Child Non-cancer | Worker Cancer | Worker Non-cancer
| 1,3-Butadiene | 106-99-0 | Yes | HI3 | 0.033 | 2 | 0.86 | 8.8 | 0.4 | 8.8 | 660
| Acenaphthene | 83-32-9 | No
| Acenaphthylene | 208-96-8 | No
| Acetaldehyde | 75-07-0 | Yes | HI3 | 0.45 | 140 | 12 | 620 | 5.5 | 620 | 470
| Acrolein | 107-02-8 | Yes | HI5 |  | 0.35 |  | 1.5 |  | 1.5 | 6.9
| Ammonia | 7664-41-7 | Yes | HI3 |  | 500 |  | 2200 |  | 2200 | 1200
| Anthracene | 120-12-7 | No
| Antimony | 7440-36-0 | Yes | HI3 |  | 0.3 |  | 1.3 |  | 1.3 | 1
| Arsenic | 7440-38-2 | Yes | HI3 | 2.4e-05 | 0.00017 | 0.0013 | 0.0024 | 0.00062 | 0.0024 | 0.2
| Barium | 7440-39-3 | No
| Benz[a]anthracene | 56-55-3 | Yes | -- | 0.00021 |  | 0.0078 |  | 0.015
| Benzene | 71-43-2 | Yes | HI3 | 0.13 | 3 | 3.3 | 13 | 1.5 | 13 | 29
| Benzo[a]pyrene 2 | 50-32-8 | Yes | HI3 | 4.3e-05 | 0.002 | 0.0016 | 0.0088 | 0.003 | 0.0088 | 0.002
| Benzo[b]fluoranthene | 205-99-2 | Yes | -- | 5.3e-05 |  | 0.002 |  | 0.0038
| Benzo[e]pyrene | 192-97-2 | No
| Benzo[g,h,i]perylene | 191-24-2 | Yes | -- | 0.0047 |  | 0.17 |  | 0.34
| Benzo[k]fluoranthene | 207-08-9 | Yes | -- | 0.0014 |  | 0.052 |  | 0.1
| Beryllium | 7440-41-7 | Yes | HI3 | 0.00042 | 0.007 | 0.011 | 0.031 | 0.005 | 0.031 | 0.02
| Cadmium | 7440-43-9 | Yes | HI3 | 0.00056 | 0.005 | 0.014 | 0.037 | 0.0067 | 0.037 | 0.03
| Chlorobenzene | 108-90-7 | Yes | HI3 |  | 50 |  | 220 |  | 220
| Chrysene | 218-01-9 | Yes | -- | 0.00043 |  | 0.016 |  | 0.03
| Cobalt | 7440-48-4 | Yes | HI3 |  | 0.1 |  | 0.44 |  | 0.44
| Copper | 7440-50-8 | Yes | HI3 | [6 empty] | 100
| Dibenz[a,h]anthracene | 53-70-3 | Yes | -- | 4.3e-06 |  | 0.00016 |  | 0.0003
| Diesel exhaust particulates | 200 | Yes | HI3 | 0.1 | 5 | 2.6 | 22 | 1.2 | 22
| Ethyl Benzene | 100-41-4 | Yes | HI3 | 0.4 | 260 | 10 | 1100 | 4.8 | 1100 | 22000
| Fluoranthene | 206-44-0 | Yes | -- | 0.00053 |  | 0.02 |  | 0.038
| Fluorene | 86-73-7 | No
| Formaldehyde | 50-00-0 | Yes | HI3 | 0.17 | 9 | 4.3 | 40 | 2 | 40 | 49
| Hexane | 110-54-3 | Yes | HI3 |  | 700 |  | 3100 |  | 3100
| Hexavalent chromium | 18540-29-9 | Yes | HI3 | 3.1e-05 | 0.083 | 0.00052 | 0.88 | 0.001 | 0.88 | 0.3
| Hydrogen Chloride | 7647-01-0 | Yes | HI3 |  | 20 |  | 88 |  | 88 | 2100
| Indeno[1,2,3-cd]pyrene | 193-39-5 | Yes | -- | 0.00061 |  | 0.022 |  | 0.043
| Lead | 7439-92-1 | Yes | HI3 |  | 0.15 |  | 0.66 |  | 0.66 | 0.15
| Manganese | 7439-96-5 | Yes | HI3 |  | 0.09 |  | 0.4 |  | 0.4 | 0.3
| Mercury | 7439-97-6 | Yes | HI3 |  | 0.077 |  | 0.63 |  | 0.63 | 0.6
| 2-Methyl naphthalene | 91-57-6 | No
| Naphthalene | 91-20-3 | Yes | HI3 | 0.029 | 3.7 | 0.76 | 16 | 0.35 | 16 | 200
| Nickel | 365 | Yes | HI3 | 0.0038 | 0.014 | 0.1 | 0.062 | 0.046 | 0.062 | 0.2
| Perylene | 198-55-0 | No
| Phenanthrene | 85-01-8 | No
| Phosphorus | 504 | No
| Propylene | 115-07-1 | Yes | HI5 |  | 3000 |  | 13000 |  | 13000
| Pyrene | 129-00-0 | No
| PAHs (excluding Naphthalene) | 401 | Yes | -- | 4.3e-05 |  | 0.0016 |  | 0.003
| Selenium | 7782-49-2 | Yes | HI3 | [6 empty] | 2
| Silver | 7440-22-4 | No
| Thallium | 7440-28-0 | No
| Toluene | 108-88-3 | Yes | HI3 |  | 5000 |  | 22000 |  | 22000 | 7500
| Xylenes | 1330-20-7 | Yes | HI3 |  | 220 |  | 970 |  | 970 | 8700
| Zinc | 7440-66-6 | No
1 | If the toxic is listed in the Risk-Based Concentrations (Table 2) in OAR Chapter 340-245-8010, then it's considered a permitted toxic.
2 | For emission units that are using total PAHs, RBCs for benzo(a)pyrene are only included for non-cancer risk categories because the chronic cancer risks are accounted for under PAHs.
Table F2-1. Screening Risk Equivalent Emission Rate - CAT 27 - 750 kW
| Pollutant | CAS/DEQ ID | Long-Term Emission Rate (g/s/gen) 1 | Short-Term Emission Rate (g/s/gen) | REER Used for Modeling with Unit Emission Rate
[5 empty] | Residential Chronic |  | Non-residential Chronic |  |  |  | Acute Non-cancer
[5 empty] | Chronic Cancer | Chronic Non-cancer | Child Cancer | Child Non-cancer | Worker Cancer | Worker Non-cancer
| 1,3-Butadiene | 106-99-0 | 1.7034e-05 | 0.0014715 | 0.00051619 | 8.5171e-06 | 1.9807e-05 | 1.9357e-06 | 4.2585e-05 | 1.9357e-06 | 2.2296e-06
| Acenaphthene | 83-32-9 | 5.756e-08 | 4.9725e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Acenaphthylene | 208-96-8 | 6.3452e-08 | 5.4815e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Acetaldehyde | 75-07-0 | 6.1375e-05 | 0.005302 | 0.00013639 | 4.3839e-07 | 5.1145e-06 | 9.8991e-08 | 1.1159e-05 | 9.8991e-08 | 1.1281e-05
| Acrolein | 107-02-8 | 2.6562e-06 | 0.00022946 | 0 | 7.5891e-06 | 0 | 1.7708e-06 | 0 | 1.7708e-06 | 3.3255e-05
| Ammonia | 7664-41-7 | 6.1676e-05 | 0.0054028 | 0 | 1.2335e-07 | 0 | 2.8034e-08 | 0 | 2.8034e-08 | 4.5023e-06
| Anthracene | 120-12-7 | 3.5423e-08 | 3.0601e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Antimony | 7440-36-0 | 2.4531e-08 | 2.1489e-06 | 0 | 8.1768e-08 | 0 | 1.887e-08 | 0 | 1.887e-08 | 2.1489e-06
| Arsenic | 7440-38-2 | 2.1344e-08 | 1.8697e-06 | 0.00088933 | 0.00012555 | 1.6418e-05 | 8.8933e-06 | 3.4426e-05 | 8.8933e-06 | 9.3486e-06
| Barium | 7440-39-3 | 2.8825e-08 | 2.5251e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Benz[a]anthracene | 56-55-3 | 3.8034e-09 | 3.2857e-07 | 1.8111e-05 | 0 | 4.8762e-07 | 0 | 2.5356e-07 | 0 | 0
| Benzene | 71-43-2 | 1.4597e-05 | 0.001261 | 0.00011229 | 4.8658e-06 | 4.4234e-06 | 1.1229e-06 | 9.7315e-06 | 1.1229e-06 | 4.3484e-05
| Benzo[a]pyrene 2 | 50-32-8 | 1.1271e-09 | 9.7371e-08 | 2.6213e-05 | 5.6357e-07 | 7.0446e-07 | 1.2808e-07 | 3.7571e-07 | 1.2808e-07 | 4.8685e-05
| Benzo[b]fluoranthene | 205-99-2 | 3.4753e-09 | 3.0022e-07 | 6.5571e-05 | 0 | 1.7376e-06 | 0 | 9.1455e-07 | 0 | 0
| Benzo[e]pyrene | 192-97-2 | 2.5754e-09 | 2.2248e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Benzo[g,h,i]perylene | 191-24-2 | 1.7139e-09 | 1.4806e-07 | 3.6467e-07 | 0 | 1.0082e-08 | 0 | 5.041e-09 | 0 | 0
| Benzo[k]fluoranthene | 207-08-9 | 1.0229e-09 | 8.8362e-08 | 7.3061e-07 | 0 | 1.967e-08 | 0 | 1.0229e-08 | 0 | 0
| Beryllium | 7440-41-7 | 3.6781e-10 | 3.222e-08 | 8.7573e-07 | 5.2544e-08 | 3.3437e-08 | 1.1865e-08 | 7.3561e-08 | 1.1865e-08 | 1.611e-06
| Cadmium | 7440-43-9 | 6.2276e-09 | 5.4554e-07 | 1.1121e-05 | 1.2455e-06 | 4.4483e-07 | 1.6831e-07 | 9.2949e-07 | 1.6831e-07 | 1.8185e-05
| Chlorobenzene | 108-90-7 | 1.5671e-08 | 1.3538e-06 | 0 | 3.1342e-10 | 0 | 7.1231e-11 | 0 | 7.1231e-11 | 0
| Chrysene | 218-01-9 | 5.2497e-09 | 4.5351e-07 | 1.2209e-05 | 0 | 3.2811e-07 | 0 | 1.7499e-07 | 0 | 0
| Cobalt | 7440-48-4 | 1.2143e-09 | 1.0638e-07 | 0 | 1.2143e-08 | 0 | 2.7598e-09 | 0 | 2.7598e-09 | 0
| Copper | 7440-50-8 | 3.8712e-08 | 3.3912e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3912e-08
| Dibenz[a,h]anthracene | 53-70-3 | 8.1252e-11 | 7.0192e-09 | 1.8896e-05 | 0 | 5.0782e-07 | 0 | 2.7084e-07 | 0 | 0
| Diesel exhaust particulates | 200 | 0.0018319 | 0.15825 | 0.018319 | 0.00036638 | 0.00070458 | 8.3269e-05 | 0.0015266 | 8.3269e-05 | 0
| Ethyl Benzene | 100-41-4 | 8.5406e-07 | 7.378e-05 | 2.1351e-06 | 3.2848e-09 | 8.5406e-08 | 7.7641e-10 | 1.7793e-07 | 7.7641e-10 | 3.3536e-09
| Fluoranthene | 206-44-0 | 2.8987e-08 | 2.5041e-06 | 5.4693e-05 | 0 | 1.4494e-06 | 0 | 7.6282e-07 | 0 | 0
| Fluorene | 86-73-7 | 1.7116e-07 | 1.4786e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Formaldehyde | 50-00-0 | 0.00021317 | 0.018371 | 0.0012539 | 2.3686e-05 | 4.9575e-05 | 5.3293e-06 | 0.00010659 | 5.3293e-06 | 0.00037493
| Hexane | 110-54-3 | 2.1077e-06 | 0.00018208 | 0 | 3.011e-09 | 0 | 6.7991e-10 | 0 | 6.7991e-10 | 0
| Hexavalent chromium | 18540-29-9 | 4.8681e-09 | 4.2645e-07 | 0.00015704 | 5.8652e-08 | 9.3617e-06 | 5.5319e-09 | 4.8681e-06 | 5.5319e-09 | 1.4215e-06
| Hydrogen Chloride | 7647-01-0 | 1.4597e-05 | 0.001261 | 0 | 7.2987e-07 | 0 | 1.6588e-07 | 0 | 1.6588e-07 | 6.0049e-07
| Indeno[1,2,3-cd]pyrene | 193-39-5 | 8.3925e-10 | 7.2501e-08 | 1.3758e-06 | 0 | 3.8148e-08 | 0 | 1.9517e-08 | 0 | 0
| Lead | 7439-92-1 | 2.8037e-08 | 2.4561e-06 | 0 | 1.8691e-07 | 0 | 4.248e-08 | 0 | 4.248e-08 | 1.6374e-05
| Manganese | 7439-96-5 | 3.2373e-08 | 2.8359e-06 | 0 | 3.597e-07 | 0 | 8.0932e-08 | 0 | 8.0932e-08 | 9.4529e-06
| Mercury | 7439-97-6 | 1.1647e-09 | 1.0203e-07 | 0 | 1.5126e-08 | 0 | 1.8487e-09 | 0 | 1.8487e-09 | 1.7005e-07
| 2-Methyl naphthalene | 91-57-6 | 9.6359e-07 | 8.3242e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Naphthalene | 91-20-3 | 2.0648e-06 | 0.00017837 | 7.12e-05 | 5.5806e-07 | 2.7169e-06 | 1.2905e-07 | 5.8995e-06 | 1.2905e-07 | 8.9187e-07
| Nickel | 365 | 1.4049e-08 | 1.2307e-06 | 3.6971e-06 | 1.0035e-06 | 1.4049e-07 | 2.266e-07 | 3.0541e-07 | 2.266e-07 | 6.1534e-06
| Perylene | 198-55-0 | 9.232e-11 | 7.9753e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Phenanthrene | 85-01-8 | 3.5588e-07 | 3.0744e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Phosphorus | 504 | 6.479e-07 | 5.6756e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Propylene | 115-07-1 | 3.6826e-05 | 0.0031813 | 0 | 1.2275e-08 | 0 | 2.8328e-09 | 0 | 2.8328e-09 | 0
| Pyrene | 129-00-0 | 9.7942e-08 | 8.461e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PAHs (excluding Naphthalene) | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Selenium | 7782-49-2 | 2.9017e-08 | 2.5419e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2709e-06
| Silver | 7440-22-4 | 3.7015e-09 | 3.2426e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Thallium | 7440-28-0 | 1.851e-08 | 1.6215e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Toluene | 108-88-3 | 8.2585e-06 | 0.00071343 | 0 | 1.6517e-09 | 0 | 3.7539e-10 | 0 | 3.7539e-10 | 9.5124e-08
| Xylenes | 1330-20-7 | 3.3222e-06 | 0.000287 | 0 | 1.5101e-08 | 0 | 3.4249e-09 | 0 | 3.4249e-09 | 3.2988e-08
| Zinc | 7440-66-6 | 4.0291e-07 | 3.5295e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL REER for 750 kW Units (g/s per µg/m3) |  |  |  | 0.021671 | 0.00054206 | 0.00081799 | 0.00010344 | 0.0017461 | 0.00010344 | 0.00058616
If the toxic is listed in the Risk-Based Concentrations (Table 2) in OAR Chapter 340-245-8010, then it's considered a permitted toxic. Emission rate is normalized based on operational hours of 8,760 hrs/yr or 24 hrs/day.
Table F2-2. Screening Risk Equivalent Emission Rate - CAT 27 - 800 kW
| Pollutant | CAS/DEQ ID | Long-Term Emission Rate (g/s/gen) 1 | Short-Term Emission Rate (g/s/gen) | REER Used for Modeling with Unit Emission Rate
[5 empty] | Residential Chronic |  | Non-residential Chronic |  |  |  | Acute Non-cancer
[5 empty] | Chronic Cancer | Chronic Non-cancer | Child Cancer | Child Non-cancer | Worker Cancer | Worker Non-cancer
| 1,3-Butadiene | 106-99-0 | 1.821e-05 | 0.0015731 | 0.00055182 | 9.105e-06 | 2.1174e-05 | 2.0693e-06 | 4.5525e-05 | 2.0693e-06 | 2.3835e-06
| Acenaphthene | 83-32-9 | 6.1533e-08 | 5.3157e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Acenaphthylene | 208-96-8 | 6.7832e-08 | 5.8599e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Acetaldehyde | 75-07-0 | 6.5611e-05 | 0.005668 | 0.0001458 | 4.6865e-07 | 5.4676e-06 | 1.0582e-07 | 1.1929e-05 | 1.0582e-07 | 1.206e-05
| Acrolein | 107-02-8 | 2.8396e-06 | 0.0002453 | 0 | 8.113e-06 | 0 | 1.893e-06 | 0 | 1.893e-06 | 3.5551e-05
| Ammonia | 7664-41-7 | 6.5933e-05 | 0.0057757 | 0 | 1.3187e-07 | 0 | 2.997e-08 | 0 | 2.997e-08 | 4.8131e-06
| Anthracene | 120-12-7 | 3.7868e-08 | 3.2713e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Antimony | 7440-36-0 | 2.6224e-08 | 2.2972e-06 | 0 | 8.7413e-08 | 0 | 2.0172e-08 | 0 | 2.0172e-08 | 2.2972e-06
| Arsenic | 7440-38-2 | 2.2817e-08 | 1.9988e-06 | 0.00095072 | 0.00013422 | 1.7552e-05 | 9.5072e-06 | 3.6802e-05 | 9.5072e-06 | 9.9939e-06
| Barium | 7440-39-3 | 3.0815e-08 | 2.6994e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Benz[a]anthracene | 56-55-3 | 4.0659e-09 | 3.5125e-07 | 1.9362e-05 | 0 | 5.2128e-07 | 0 | 2.7106e-07 | 0 | 0
| Benzene | 71-43-2 | 1.5605e-05 | 0.0013481 | 0.00012004 | 5.2017e-06 | 4.7288e-06 | 1.2004e-06 | 1.0403e-05 | 1.2004e-06 | 4.6485e-05
| Benzo[a]pyrene 2 | 50-32-8 | 1.2049e-09 | 1.0409e-07 | 2.8022e-05 | 6.0247e-07 | 7.5309e-07 | 1.3693e-07 | 4.0165e-07 | 1.3693e-07 | 5.2046e-05
| Benzo[b]fluoranthene | 205-99-2 | 3.7152e-09 | 3.2094e-07 | 7.0098e-05 | 0 | 1.8576e-06 | 0 | 9.7768e-07 | 0 | 0
| Benzo[e]pyrene | 192-97-2 | 2.7531e-09 | 2.3784e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Benzo[g,h,i]perylene | 191-24-2 | 1.8322e-09 | 1.5828e-07 | 3.8984e-07 | 0 | 1.0778e-08 | 0 | 5.389e-09 | 0 | 0
| Benzo[k]fluoranthene | 207-08-9 | 1.0935e-09 | 9.4462e-08 | 7.8105e-07 | 0 | 2.1028e-08 | 0 | 1.0935e-08 | 0 | 0
| Beryllium | 7440-41-7 | 3.932e-10 | 3.4444e-08 | 9.3618e-07 | 5.6171e-08 | 3.5745e-08 | 1.2684e-08 | 7.8639e-08 | 1.2684e-08 | 1.7222e-06
| Cadmium | 7440-43-9 | 6.6575e-09 | 5.8319e-07 | 1.1888e-05 | 1.3315e-06 | 4.7553e-07 | 1.7993e-07 | 9.9365e-07 | 1.7993e-07 | 1.944e-05
| Chlorobenzene | 108-90-7 | 1.6753e-08 | 1.4472e-06 | 0 | 3.3505e-10 | 0 | 7.6148e-11 | 0 | 7.6148e-11 | 0
| Chrysene | 218-01-9 | 5.6121e-09 | 4.8482e-07 | 1.3051e-05 | 0 | 3.5076e-07 | 0 | 1.8707e-07 | 0 | 0
| Cobalt | 7440-48-4 | 1.2982e-09 | 1.1372e-07 | 0 | 1.2982e-08 | 0 | 2.9503e-09 | 0 | 2.9503e-09 | 0
| Copper | 7440-50-8 | 4.1384e-08 | 3.6253e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6253e-08
| Dibenz[a,h]anthracene | 53-70-3 | 8.6861e-11 | 7.5037e-09 | 2.02e-05 | 0 | 5.4288e-07 | 0 | 2.8954e-07 | 0 | 0
| Diesel exhaust particulates | 200 | 0.0019584 | 0.16918 | 0.019584 | 0.00039167 | 0.00075322 | 8.9017e-05 | 0.001632 | 8.9017e-05 | 0
| Ethyl Benzene | 100-41-4 | 9.1301e-07 | 7.8873e-05 | 2.2825e-06 | 3.5116e-09 | 9.1301e-08 | 8.3001e-10 | 1.9021e-07 | 8.3001e-10 | 3.5851e-09
| Fluoranthene | 206-44-0 | 3.0988e-08 | 2.677e-06 | 5.8468e-05 | 0 | 1.5494e-06 | 0 | 8.1548e-07 | 0 | 0
| Fluorene | 86-73-7 | 1.8297e-07 | 1.5806e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Formaldehyde | 50-00-0 | 0.00022789 | 0.01964 | 0.0013405 | 2.5321e-05 | 5.2997e-05 | 5.6972e-06 | 0.00011394 | 5.6972e-06 | 0.00040081
| Hexane | 110-54-3 | 2.2532e-06 | 0.00019465 | 0 | 3.2189e-09 | 0 | 7.2684e-10 | 0 | 7.2684e-10 | 0
| Hexavalent chromium | 18540-29-9 | 5.2041e-09 | 4.5588e-07 | 0.00016788 | 6.27e-08 | 1.0008e-05 | 5.9138e-09 | 5.2041e-06 | 5.9138e-09 | 1.5196e-06
| Hydrogen Chloride | 7647-01-0 | 1.5605e-05 | 0.0013481 | 0 | 7.8025e-07 | 0 | 1.7733e-07 | 0 | 1.7733e-07 | 6.4194e-07
| Indeno[1,2,3-cd]pyrene | 193-39-5 | 8.9718e-10 | 7.7505e-08 | 1.4708e-06 | 0 | 4.0781e-08 | 0 | 2.0865e-08 | 0 | 0
| Lead | 7439-92-1 | 2.9973e-08 | 2.6256e-06 | 0 | 1.9982e-07 | 0 | 4.5413e-08 | 0 | 4.5413e-08 | 1.7504e-05
| Manganese | 7439-96-5 | 3.4608e-08 | 3.0316e-06 | 0 | 3.8453e-07 | 0 | 8.6519e-08 | 0 | 8.6519e-08 | 1.0105e-05
| Mercury | 7439-97-6 | 1.2451e-09 | 1.0907e-07 | 0 | 1.617e-08 | 0 | 1.9763e-09 | 0 | 1.9763e-09 | 1.8178e-07
| 2-Methyl naphthalene | 91-57-6 | 1.0301e-06 | 8.8988e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Naphthalene | 91-20-3 | 2.2073e-06 | 0.00019069 | 7.6115e-05 | 5.9658e-07 | 2.9044e-06 | 1.3796e-07 | 6.3067e-06 | 1.3796e-07 | 9.5344e-07
| Nickel | 365 | 1.5019e-08 | 1.3156e-06 | 3.9523e-06 | 1.0728e-06 | 1.5019e-07 | 2.4224e-07 | 3.2649e-07 | 2.4224e-07 | 6.5782e-06
| Perylene | 198-55-0 | 9.8693e-11 | 8.5259e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Phenanthrene | 85-01-8 | 3.8045e-07 | 3.2866e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Phosphorus | 504 | 6.9263e-07 | 6.0674e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Propylene | 115-07-1 | 3.9368e-05 | 0.0034009 | 0 | 1.3123e-08 | 0 | 3.0283e-09 | 0 | 3.0283e-09 | 0
| Pyrene | 129-00-0 | 1.047e-07 | 9.0451e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PAHs (excluding Naphthalene) | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Selenium | 7782-49-2 | 3.102e-08 | 2.7174e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3587e-06
| Silver | 7440-22-4 | 3.9571e-09 | 3.4664e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Thallium | 7440-28-0 | 1.9788e-08 | 1.7334e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Toluene | 108-88-3 | 8.8286e-06 | 0.00076268 | 0 | 1.7657e-09 | 0 | 4.013e-10 | 0 | 4.013e-10 | 1.0169e-07
| Xylenes | 1330-20-7 | 3.5515e-06 | 0.00030681 | 0 | 1.6143e-08 | 0 | 3.6614e-09 | 0 | 3.6614e-09 | 3.5265e-08
| Zinc | 7440-66-6 | 4.3072e-07 | 3.7731e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL REER for 800 kW Units (g/s per µg/m3) |  |  |  | 0.023167 | 0.00057947 | 0.00087445 | 0.00011058 | 0.0018667 | 0.00011058 | 0.00062662
1 | If the toxic is listed in the Risk-Based Concentrations (Table 2) in OAR Chapter 340-245-8010, then it's considered a permitted toxic. Emission rate is normalized based on operational hours of 8,760 hrs/yr or 24 hrs/day.
Table F2-3. Screening Risk Equivalent Emission Rate - CAT 32 - 1,000 kW
| Pollutant | CAS/DEQ ID | Long-Term Emission Rate (g/s) | Short-Term Emission Rate (g/s) | REER Used for Modeling with Unit Emission Rate
[5 empty] | Residential Chronic |  | Non-residential Chronic |  |  |  | Acute Non-cancer
[5 empty] | Chronic Cancer | Chronic Non-cancer | Child Cancer | Child Non-cancer | Worker Cancer | Worker Non-cancer
| 1,3-Butadiene | 106-99-0 | 2.285e-05 | 0.0019739 | 0.00069242 | 1.1425e-05 | 2.657e-05 | 2.5966e-06 | 5.7125e-05 | 2.5966e-06 | 2.9908e-06
| Acenaphthene | 83-32-9 | 7.7212e-08 | 6.6702e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Acenaphthylene | 208-96-8 | 8.5116e-08 | 7.353e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Acetaldehyde | 75-07-0 | 8.2329e-05 | 0.0071122 | 0.00018295 | 5.8806e-07 | 6.8607e-06 | 1.3279e-07 | 1.4969e-05 | 1.3279e-07 | 1.5132e-05
| Acrolein | 107-02-8 | 3.5631e-06 | 0.00030781 | 0 | 1.018e-05 | 0 | 2.3754e-06 | 0 | 2.3754e-06 | 4.4609e-05
| Ammonia | 7664-41-7 | 8.2733e-05 | 0.0072474 | 0 | 1.6547e-07 | 0 | 3.7606e-08 | 0 | 3.7606e-08 | 6.0395e-06
| Anthracene | 120-12-7 | 4.7517e-08 | 4.1049e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Antimony | 7440-36-0 | 3.2906e-08 | 2.8825e-06 | 0 | 1.0969e-07 | 0 | 2.5312e-08 | 0 | 2.5312e-08 | 2.8825e-06
| Arsenic | 7440-38-2 | 2.8631e-08 | 2.5081e-06 | 0.001193 | 0.00016842 | 2.2024e-05 | 1.193e-05 | 4.6179e-05 | 1.193e-05 | 1.254e-05
| Barium | 7440-39-3 | 3.8667e-08 | 3.3872e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Benz[a]anthracene | 56-55-3 | 5.1019e-09 | 4.4075e-07 | 2.4295e-05 | 0 | 6.541e-07 | 0 | 3.4013e-07 | 0 | 0
| Benzene | 71-43-2 | 1.9581e-05 | 0.0016916 | 0.00015062 | 6.527e-06 | 5.9337e-06 | 1.5062e-06 | 1.3054e-05 | 1.5062e-06 | 5.833e-05
| Benzo[a]pyrene 2 | 50-32-8 | 1.512e-09 | 1.3062e-07 | 3.5162e-05 | 7.5598e-07 | 9.4498e-07 | 1.7181e-07 | 5.0399e-07 | 1.7181e-07 | 6.5308e-05
| Benzo[b]fluoranthene | 205-99-2 | 4.6618e-09 | 4.0272e-07 | 8.7958e-05 | 0 | 2.3309e-06 | 0 | 1.2268e-06 | 0 | 0
| Benzo[e]pyrene | 192-97-2 | 3.4546e-09 | 2.9844e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Benzo[g,h,i]perylene | 191-24-2 | 2.2991e-09 | 1.9861e-07 | 4.8917e-07 | 0 | 1.3524e-08 | 0 | 6.7621e-09 | 0 | 0
| Benzo[k]fluoranthene | 207-08-9 | 1.3721e-09 | 1.1853e-07 | 9.8006e-07 | 0 | 2.6386e-08 | 0 | 1.3721e-08 | 0 | 0
| Beryllium | 7440-41-7 | 4.9338e-10 | 4.322e-08 | 1.1747e-06 | 7.0483e-08 | 4.4853e-08 | 1.5916e-08 | 9.8676e-08 | 1.5916e-08 | 2.161e-06
| Cadmium | 7440-43-9 | 8.3538e-09 | 7.3179e-07 | 1.4917e-05 | 1.6708e-06 | 5.967e-07 | 2.2578e-07 | 1.2468e-06 | 2.2578e-07 | 2.4393e-05
| Chlorobenzene | 108-90-7 | 2.1021e-08 | 1.816e-06 | 0 | 4.2042e-10 | 0 | 9.555e-11 | 0 | 9.555e-11 | 0
| Chrysene | 218-01-9 | 7.042e-09 | 6.0835e-07 | 1.6377e-05 | 0 | 4.4013e-07 | 0 | 2.3473e-07 | 0 | 0
| Cobalt | 7440-48-4 | 1.6289e-09 | 1.4269e-07 | 0 | 1.6289e-08 | 0 | 3.7021e-09 | 0 | 3.7021e-09 | 0
| Copper | 7440-50-8 | 5.1929e-08 | 4.549e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 4.549e-08
| Dibenz[a,h]anthracene | 53-70-3 | 1.0899e-10 | 9.4156e-09 | 2.5347e-05 | 0 | 6.812e-07 | 0 | 3.6331e-07 | 0 | 0
| Diesel exhaust particulates | 200 | 0.0024574 | 0.21229 | 0.024574 | 0.00049147 | 0.00094514 | 0.0001117 | 0.0020478 | 0.0001117 | 0
| Ethyl Benzene | 100-41-4 | 1.1456e-06 | 9.897e-05 | 2.8641e-06 | 4.4063e-09 | 1.1456e-07 | 1.0415e-09 | 2.3868e-07 | 1.0415e-09 | 4.4986e-09
| Fluoranthene | 206-44-0 | 3.8884e-08 | 3.3591e-06 | 7.3366e-05 | 0 | 1.9442e-06 | 0 | 1.0233e-06 | 0 | 0
| Fluorene | 86-73-7 | 2.2959e-07 | 1.9834e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Formaldehyde | 50-00-0 | 0.00028595 | 0.024644 | 0.0016821 | 3.1772e-05 | 6.65e-05 | 7.1488e-06 | 0.00014298 | 7.1488e-06 | 0.00050293
| Hexane | 110-54-3 | 2.8273e-06 | 0.00024425 | 0 | 4.039e-09 | 0 | 9.1204e-10 | 0 | 9.1204e-10 | 0
| Hexavalent chromium | 18540-29-9 | 6.5302e-09 | 5.7204e-07 | 0.00021065 | 7.8677e-08 | 1.2558e-05 | 7.4206e-09 | 6.5302e-06 | 7.4206e-09 | 1.9068e-06
| Hydrogen Chloride | 7647-01-0 | 1.9581e-05 | 0.0016916 | 0 | 9.7905e-07 | 0 | 2.2251e-07 | 0 | 2.2251e-07 | 8.0551e-07
| Indeno[1,2,3-cd]pyrene | 193-39-5 | 1.1258e-09 | 9.7253e-08 | 1.8455e-06 | 0 | 5.1172e-08 | 0 | 2.6181e-08 | 0 | 0
| Lead | 7439-92-1 | 3.7609e-08 | 3.2946e-06 | 0 | 2.5073e-07 | 0 | 5.6984e-08 | 0 | 5.6984e-08 | 2.1964e-05
| Manganese | 7439-96-5 | 4.3426e-08 | 3.8041e-06 | 0 | 4.8251e-07 | 0 | 1.0856e-07 | 0 | 1.0856e-07 | 1.268e-05
| Mercury | 7439-97-6 | 1.5623e-09 | 1.3686e-07 | 0 | 2.029e-08 | 0 | 2.4799e-09 | 0 | 2.4799e-09 | 2.281e-07
| 2-Methyl naphthalene | 91-57-6 | 1.2926e-06 | 0.00011166 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Naphthalene | 91-20-3 | 2.7698e-06 | 0.00023927 | 9.5509e-05 | 7.4859e-07 | 3.6444e-06 | 1.7311e-07 | 7.9136e-06 | 1.7311e-07 | 1.1964e-06
| Nickel | 365 | 1.8845e-08 | 1.6509e-06 | 4.9593e-06 | 1.3461e-06 | 1.8845e-07 | 3.0396e-07 | 4.0968e-07 | 3.0396e-07 | 8.2543e-06
| Perylene | 198-55-0 | 1.2384e-10 | 1.0698e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Phenanthrene | 85-01-8 | 4.7738e-07 | 4.124e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Phosphorus | 504 | 8.6911e-07 | 7.6134e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Propylene | 115-07-1 | 4.9399e-05 | 0.0042675 | 0 | 1.6466e-08 | 0 | 3.8e-09 | 0 | 3.8e-09 | 0
| Pyrene | 129-00-0 | 1.3138e-07 | 1.135e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PAHs (excluding Naphthalene) | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Selenium | 7782-49-2 | 3.8924e-08 | 3.4097e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7049e-06
| Silver | 7440-22-4 | 4.9653e-09 | 4.3496e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Thallium | 7440-28-0 | 2.483e-08 | 2.1751e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Toluene | 108-88-3 | 1.1078e-05 | 0.00095701 | 0 | 2.2156e-09 | 0 | 5.0355e-10 | 0 | 5.0355e-10 | 1.276e-07
| Xylenes | 1330-20-7 | 4.4565e-06 | 0.00038498 | 0 | 2.0257e-08 | 0 | 4.5943e-09 | 0 | 4.5943e-09 | 4.4251e-08
| Zinc | 7440-66-6 | 5.4047e-07 | 4.7345e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL REER for 1,000 kW Unit (g/s per µg/m3) |  |  |  | 0.029071 | 0.00072712 | 0.0010973 | 0.00013875 | 0.0023423 | 0.00013875 | 0.00078628
1 | If the toxic is listed in the Risk-Based Concentrations (Table 2) in OAR Chapter 340-245-8010, then it's considered a permitted toxic. Emission rate is normalized based on operational hours of 8,760 hrs/yr or 24 hrs/day.
Table F2-4. Screening Risk Equivalent Emission Rate - CAT 3516C Trans - 1,825 kW
| Pollutant | CAS/DEQ ID | Long-Term Emission Rate (g/s) | Short-Term Emission Rate (g/s) | REER Used for Modeling with Unit Emission Rate
[5 empty] | Residential Chronic |  | Non-residential Chronic |  |  |  | Acute Non-cancer
[5 empty] | Chronic Cancer | Chronic Non-cancer | Child Cancer | Child Non-cancer | Worker Cancer | Worker Non-cancer
| 1,3-Butadiene | 106-99-0 | 4.0806e-05 | 0.0035251 | 0.0012365 | 2.0403e-05 | 4.7448e-05 | 4.637e-06 | 0.00010201 | 4.637e-06 | 5.3411e-06
| Acenaphthene | 83-32-9 | 1.3789e-07 | 1.1912e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Acenaphthylene | 208-96-8 | 1.52e-07 | 1.3131e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Acetaldehyde | 75-07-0 | 0.00014702 | 0.012701 | 0.00032672 | 1.0502e-06 | 1.2252e-05 | 2.3714e-07 | 2.6732e-05 | 2.3714e-07 | 2.7024e-05
| Acrolein | 107-02-8 | 6.363e-06 | 0.00054968 | 0 | 1.818e-05 | 0 | 4.242e-06 | 0 | 4.242e-06 | 7.9664e-05
| Ammonia | 7664-41-7 | 0.00014775 | 0.012943 | 0 | 2.9549e-07 | 0 | 6.7157e-08 | 0 | 6.7157e-08 | 1.0785e-05
| Anthracene | 120-12-7 | 8.4857e-08 | 7.3306e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Antimony | 7440-36-0 | 5.8763e-08 | 5.1477e-06 | 0 | 1.9588e-07 | 0 | 4.5203e-08 | 0 | 4.5203e-08 | 5.1477e-06
| Arsenic | 7440-38-2 | 5.113e-08 | 4.479e-06 | 0.0021304 | 0.00030076 | 3.9331e-05 | 2.1304e-05 | 8.2467e-05 | 2.1304e-05 | 2.2395e-05
| Barium | 7440-39-3 | 6.9051e-08 | 6.0489e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Benz[a]anthracene | 56-55-3 | 9.1111e-09 | 7.8709e-07 | 4.3386e-05 | 0 | 1.1681e-06 | 0 | 6.0741e-07 | 0 | 0
| Benzene | 71-43-2 | 3.4968e-05 | 0.0030208 | 0.00026899 | 1.1656e-05 | 1.0596e-05 | 2.6899e-06 | 2.3312e-05 | 2.6899e-06 | 0.00010417
| Benzo[a]pyrene 2 | 50-32-8 | 2.7001e-09 | 2.3325e-07 | 6.2793e-05 | 1.35e-06 | 1.6876e-06 | 3.0683e-07 | 9.0003e-07 | 3.0683e-07 | 0.00011663
| Benzo[b]fluoranthene | 205-99-2 | 8.3251e-09 | 7.1919e-07 | 0.00015708 | 0 | 4.1625e-06 | 0 | 2.1908e-06 | 0 | 0
| Benzo[e]pyrene | 192-97-2 | 6.1693e-09 | 5.3295e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Benzo[g,h,i]perylene | 191-24-2 | 4.1058e-09 | 3.5469e-07 | 8.7357e-07 | 0 | 2.4152e-08 | 0 | 1.2076e-08 | 0 | 0
| Benzo[k]fluoranthene | 207-08-9 | 2.4503e-09 | 2.1167e-07 | 1.7502e-06 | 0 | 4.7121e-08 | 0 | 2.4503e-08 | 0 | 0
| Beryllium | 7440-41-7 | 8.8109e-10 | 7.7183e-08 | 2.0978e-06 | 1.2587e-07 | 8.0099e-08 | 2.8422e-08 | 1.7622e-07 | 2.8422e-08 | 3.8592e-06
| Cadmium | 7440-43-9 | 1.4918e-08 | 1.3068e-06 | 2.664e-05 | 2.9837e-06 | 1.0656e-06 | 4.032e-07 | 2.2266e-06 | 4.032e-07 | 4.3561e-05
| Chlorobenzene | 108-90-7 | 3.754e-08 | 3.243e-06 | 0 | 7.5079e-10 | 0 | 1.7063e-10 | 0 | 1.7063e-10 | 0
| Chrysene | 218-01-9 | 1.2576e-08 | 1.0864e-06 | 2.9246e-05 | 0 | 7.8599e-07 | 0 | 4.1919e-07 | 0 | 0
| Cobalt | 7440-48-4 | 2.9089e-09 | 2.5482e-07 | 0 | 2.9089e-08 | 0 | 6.6112e-09 | 0 | 6.6112e-09 | 0
| Copper | 7440-50-8 | 9.2735e-08 | 8.1236e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1236e-08
| Dibenz[a,h]anthracene | 53-70-3 | 1.9464e-10 | 1.6815e-08 | 4.5265e-05 | 0 | 1.2165e-06 | 0 | 6.488e-07 | 0 | 0
| Diesel exhaust particulates | 200 | 0.0043884 | 0.3791 | 0.043884 | 0.00087768 | 0.0016878 | 0.00019947 | 0.003657 | 0.00019947 | 0
| Ethyl Benzene | 100-41-4 | 2.0459e-06 | 0.00017674 | 5.1148e-06 | 7.8689e-09 | 2.0459e-07 | 1.8599e-09 | 4.2623e-07 | 1.8599e-09 | 8.0337e-09
| Fluoranthene | 206-44-0 | 6.944e-08 | 5.9987e-06 | 0.00013102 | 0 | 3.472e-06 | 0 | 1.8274e-06 | 0 | 0
| Fluorene | 86-73-7 | 4.1001e-07 | 3.542e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Formaldehyde | 50-00-0 | 0.00051066 | 0.044009 | 0.0030039 | 5.674e-05 | 0.00011876 | 1.2766e-05 | 0.00025533 | 1.2766e-05 | 0.00089815
| Hexane | 110-54-3 | 5.0491e-06 | 0.00043618 | 0 | 7.213e-09 | 0 | 1.6287e-09 | 0 | 1.6287e-09 | 0
| Hexavalent chromium | 18540-29-9 | 1.1662e-08 | 1.0216e-06 | 0.00037618 | 1.405e-07 | 2.2426e-05 | 1.3252e-08 | 1.1662e-05 | 1.3252e-08 | 3.4052e-06
| Hydrogen Chloride | 7647-01-0 | 3.4968e-05 | 0.0030208 | 0 | 1.7484e-06 | 0 | 3.9737e-07 | 0 | 3.9737e-07 | 1.4385e-06
| Indeno[1,2,3-cd]pyrene | 193-39-5 | 2.0104e-09 | 1.7368e-07 | 3.2958e-06 | 0 | 9.1383e-08 | 0 | 4.6754e-08 | 0 | 0
| Lead | 7439-92-1 | 6.7164e-08 | 5.8835e-06 | 0 | 4.4776e-07 | 0 | 1.0176e-07 | 0 | 1.0176e-07 | 3.9223e-05
| Manganese | 7439-96-5 | 7.755e-08 | 6.7934e-06 | 0 | 8.6167e-07 | 0 | 1.9388e-07 | 0 | 1.9388e-07 | 2.2645e-05
| Mercury | 7439-97-6 | 2.7901e-09 | 2.4441e-07 | 0 | 3.6234e-08 | 0 | 4.4287e-09 | 0 | 4.4287e-09 | 4.0735e-07
| 2-Methyl naphthalene | 91-57-6 | 2.3083e-06 | 0.00019941 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Naphthalene | 91-20-3 | 4.9463e-06 | 0.0004273 | 0.00017056 | 1.3368e-06 | 6.5083e-06 | 3.0914e-07 | 1.4132e-05 | 3.0914e-07 | 2.1365e-06
| Nickel | 365 | 3.3654e-08 | 2.9481e-06 | 8.8564e-06 | 2.4039e-06 | 3.3654e-07 | 5.4281e-07 | 7.3162e-07 | 5.4281e-07 | 1.4741e-05
| Perylene | 198-55-0 | 2.2115e-10 | 1.9105e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Phenanthrene | 85-01-8 | 8.5252e-07 | 7.3647e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Phosphorus | 504 | 1.5521e-06 | 0.00013596 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Propylene | 115-07-1 | 8.8218e-05 | 0.007621 | 0 | 2.9406e-08 | 0 | 6.786e-09 | 0 | 6.786e-09 | 0
| Pyrene | 129-00-0 | 2.3462e-07 | 2.0269e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PAHs (excluding Naphthalene) | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Selenium | 7782-49-2 | 6.9511e-08 | 6.0892e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0446e-06
| Silver | 7440-22-4 | 8.8671e-09 | 7.7676e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Thallium | 7440-28-0 | 4.4341e-08 | 3.8843e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Toluene | 108-88-3 | 1.9783e-05 | 0.001709 | 0 | 3.9567e-09 | 0 | 8.9925e-10 | 0 | 8.9925e-10 | 2.2787e-07
| Xylenes | 1330-20-7 | 7.9584e-06 | 0.00068751 | 0 | 3.6175e-08 | 0 | 8.2045e-09 | 0 | 8.2045e-09 | 7.9024e-08
| Zinc | 7440-66-6 | 9.6518e-07 | 8.455e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL REER for 1,825 kW (g/s per µg/m3) |  |  |  | 0.051915 | 0.0012985 | 0.0019595 | 0.00024779 | 0.0041829 | 0.00024779 | 0.0014042
1 | If the toxic is listed in the Risk-Based Concentrations (Table 2) in OAR Chapter 340-245-8010, then it's considered a permitted toxic. Emission rate is normalized based on operational hours of 8,760 hrs/yr or 24 hrs/day.
Table F2-5. Screening Risk Equivalent Emission Rate - CAT 3516C - 2,000 kW
| Pollutant | CAS/DEQ ID | Long-Term Emission Rate (g/s/gen) 1 | Short-Term Emission Rate (g/s/gen) | REER Used for Modeling with Unit Emission Rate
[5 empty] | Residential Chronic |  | Non-residential Chronic |  |  |  | Acute Non-cancer
[5 empty] | Chronic Cancer | Chronic Non-cancer | Child Cancer | Child Non-cancer | Worker Cancer | Worker Non-cancer
| 1,3-Butadiene | 106-99-0 | 4.4143e-05 | 0.0038134 | 0.0013377 | 2.2071e-05 | 5.1329e-05 | 5.0162e-06 | 0.00011036 | 5.0162e-06 | 5.7778e-06
| Acenaphthene | 83-32-9 | 1.4916e-07 | 1.2886e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Acenaphthylene | 208-96-8 | 1.6443e-07 | 1.4205e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Acetaldehyde | 75-07-0 | 0.00015905 | 0.01374 | 0.00035344 | 1.1361e-06 | 1.3254e-05 | 2.5653e-07 | 2.8918e-05 | 2.5653e-07 | 2.9233e-05
| Acrolein | 107-02-8 | 6.8833e-06 | 0.00059463 | 0 | 1.9667e-05 | 0 | 4.5889e-06 | 0 | 4.5889e-06 | 8.6179e-05
| Ammonia | 7664-41-7 | 0.00015983 | 0.014001 | 0 | 3.1965e-07 | 0 | 7.2649e-08 | 0 | 7.2649e-08 | 1.1667e-05
| Anthracene | 120-12-7 | 9.1796e-08 | 7.93e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Antimony | 7440-36-0 | 6.3569e-08 | 5.5686e-06 | 0 | 2.119e-07 | 0 | 4.8899e-08 | 0 | 4.8899e-08 | 5.5686e-06
| Arsenic | 7440-38-2 | 5.5311e-08 | 4.8452e-06 | 0.0023046 | 0.00032536 | 4.2547e-05 | 2.3046e-05 | 8.9211e-05 | 2.3046e-05 | 2.4226e-05
| Barium | 7440-39-3 | 7.4698e-08 | 6.5435e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Benz[a]anthracene | 56-55-3 | 9.8562e-09 | 8.5145e-07 | 4.6934e-05 | 0 | 1.2636e-06 | 0 | 6.5708e-07 | 0 | 0
| Benzene | 71-43-2 | 3.7828e-05 | 0.0032679 | 0.00029098 | 1.2609e-05 | 1.1463e-05 | 2.9098e-06 | 2.5218e-05 | 2.9098e-06 | 0.00011268
| Benzo[a]pyrene 2 | 50-32-8 | 2.9209e-09 | 2.5233e-07 | 6.7928e-05 | 1.4604e-06 | 1.8256e-06 | 3.3192e-07 | 9.7363e-07 | 3.3192e-07 | 0.00012616
| Benzo[b]fluoranthene | 205-99-2 | 9.0059e-09 | 7.78e-07 | 0.00016992 | 0 | 4.5029e-06 | 0 | 2.37e-06 | 0 | 0
| Benzo[e]pyrene | 192-97-2 | 6.6738e-09 | 5.7654e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Benzo[g,h,i]perylene | 191-24-2 | 4.4415e-09 | 3.8369e-07 | 9.45e-07 | 0 | 2.6127e-08 | 0 | 1.3063e-08 | 0 | 0
| Benzo[k]fluoranthene | 207-08-9 | 2.6507e-09 | 2.2898e-07 | 1.8933e-06 | 0 | 5.0974e-08 | 0 | 2.6507e-08 | 0 | 0
| Beryllium | 7440-41-7 | 9.5314e-10 | 8.3495e-08 | 2.2694e-06 | 1.3616e-07 | 8.6649e-08 | 3.0746e-08 | 1.9063e-07 | 3.0746e-08 | 4.1748e-06
| Cadmium | 7440-43-9 | 1.6138e-08 | 1.4137e-06 | 2.8818e-05 | 3.2276e-06 | 1.1527e-06 | 4.3617e-07 | 2.4087e-06 | 4.3617e-07 | 4.7124e-05
| Chlorobenzene | 108-90-7 | 4.0609e-08 | 3.5082e-06 | 0 | 8.1219e-10 | 0 | 1.8459e-10 | 0 | 1.8459e-10 | 0
| Chrysene | 218-01-9 | 1.3604e-08 | 1.1752e-06 | 3.1638e-05 | 0 | 8.5026e-07 | 0 | 4.5347e-07 | 0 | 0
| Cobalt | 7440-48-4 | 3.1468e-09 | 2.7566e-07 | 0 | 3.1468e-08 | 0 | 7.1519e-09 | 0 | 7.1519e-09 | 0
| Copper | 7440-50-8 | 1.0032e-07 | 8.7879e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7879e-08
| Dibenz[a,h]anthracene | 53-70-3 | 2.1056e-10 | 1.819e-08 | 4.8967e-05 | 0 | 1.316e-06 | 0 | 7.0186e-07 | 0 | 0
| Diesel exhaust particulates | 200 | 0.0047472 | 0.4101 | 0.047472 | 0.00094945 | 0.0018259 | 0.00021578 | 0.003956 | 0.00021578 | 0
| Ethyl Benzene | 100-41-4 | 2.2132e-06 | 0.00019119 | 5.533e-06 | 8.5124e-09 | 2.2132e-07 | 2.012e-09 | 4.6109e-07 | 2.012e-09 | 8.6907e-09
| Fluoranthene | 206-44-0 | 7.5118e-08 | 6.4893e-06 | 0.00014173 | 0 | 3.7559e-06 | 0 | 1.9768e-06 | 0 | 0
| Fluorene | 86-73-7 | 4.4354e-07 | 3.8316e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Formaldehyde | 50-00-0 | 0.00055242 | 0.047608 | 0.0032495 | 6.138e-05 | 0.00012847 | 1.381e-05 | 0.00027621 | 1.381e-05 | 0.00097159
| Hexane | 110-54-3 | 5.462e-06 | 0.00047185 | 0 | 7.8028e-09 | 0 | 1.7619e-09 | 0 | 1.7619e-09 | 0
| Hexavalent chromium | 18540-29-9 | 1.2615e-08 | 1.1051e-06 | 0.00040694 | 1.5199e-07 | 2.426e-05 | 1.4336e-08 | 1.2615e-05 | 1.4336e-08 | 3.6837e-06
| Hydrogen Chloride | 7647-01-0 | 3.7828e-05 | 0.0032679 | 0 | 1.8914e-06 | 0 | 4.2986e-07 | 0 | 4.2986e-07 | 1.5561e-06
| Indeno[1,2,3-cd]pyrene | 193-39-5 | 2.1748e-09 | 1.8788e-07 | 3.5653e-06 | 0 | 9.8856e-08 | 0 | 5.0578e-08 | 0 | 0
| Lead | 7439-92-1 | 7.2656e-08 | 6.3647e-06 | 0 | 4.8437e-07 | 0 | 1.1008e-07 | 0 | 1.1008e-07 | 4.2431e-05
| Manganese | 7439-96-5 | 8.3892e-08 | 7.3489e-06 | 0 | 9.3213e-07 | 0 | 2.0973e-07 | 0 | 2.0973e-07 | 2.4496e-05
| Mercury | 7439-97-6 | 3.0182e-09 | 2.644e-07 | 0 | 3.9198e-08 | 0 | 4.7908e-09 | 0 | 4.7908e-09 | 4.4066e-07
| 2-Methyl naphthalene | 91-57-6 | 2.4971e-06 | 0.00021572 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Naphthalene | 91-20-3 | 5.3508e-06 | 0.00046224 | 0.00018451 | 1.4462e-06 | 7.0405e-06 | 3.3442e-07 | 1.5288e-05 | 3.3442e-07 | 2.3112e-06
| Nickel | 365 | 3.6407e-08 | 3.1892e-06 | 9.5807e-06 | 2.6005e-06 | 3.6407e-07 | 5.872e-07 | 7.9145e-07 | 5.872e-07 | 1.5946e-05
| Perylene | 198-55-0 | 2.3924e-10 | 2.0667e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Phenanthrene | 85-01-8 | 9.2223e-07 | 7.9669e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Phosphorus | 504 | 1.679e-06 | 0.00014708 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Propylene | 115-07-1 | 9.5432e-05 | 0.0082442 | 0 | 3.1811e-08 | 0 | 7.3409e-09 | 0 | 7.3409e-09 | 0
| Pyrene | 129-00-0 | 2.5381e-07 | 2.1926e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PAHs (excluding Naphthalene) | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Selenium | 7782-49-2 | 7.5195e-08 | 6.5871e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2936e-06
| Silver | 7440-22-4 | 9.5922e-09 | 8.4028e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Thallium | 7440-28-0 | 4.7967e-08 | 4.2019e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Toluene | 108-88-3 | 2.1401e-05 | 0.0018488 | 0 | 4.2802e-09 | 0 | 9.7278e-10 | 0 | 9.7278e-10 | 2.4651e-07
| Xylenes | 1330-20-7 | 8.6092e-06 | 0.00074373 | 0 | 3.9133e-08 | 0 | 8.8755e-09 | 0 | 8.8755e-09 | 8.5486e-08
| Zinc | 7440-66-6 | 1.0441e-06 | 9.1464e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL REER for 2,000 kW (g/s per µg/m3) |  |  |  | 0.05616 | 0.0014047 | 0.0021197 | 0.00026805 | 0.0045249 | 0.00026805 | 0.001519
1 | If the toxic is listed in the Risk-Based Concentrations (Table 2) in OAR Chapter 340-245-8010, then it's considered a permitted toxic. Emission rate is normalized based on operational hours of 8,760 hrs/yr or 24 hrs/day.
Table F2-6. Screening Risk Equivalent Emission Rate - CAT 3516C - 2,500 kW
| Pollutant | CAS/DEQ ID | Long-Term Emission Rate (g/s/gen) 1 | Short-Term Emission Rate (g/s/gen) | REER Used for Modeling with Unit Emission Rate
[5 empty] | Residential Chronic |  | Non-residential Chronic |  |  |  | Acute Non-cancer
[5 empty] | Chronic Cancer | Chronic Non-cancer | Child Cancer | Child Non-cancer | Worker Cancer | Worker Non-cancer
| 1,3-Butadiene | 106-99-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Acenaphthene | 83-32-9 | 1.4447e-07 | 1.2481e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Acenaphthylene | 208-96-8 | 1.7196e-07 | 1.4855e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Acetaldehyde | 75-07-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Acrolein | 107-02-8 | 8.5979e-06 | 0.00074276 | 0 | 2.4566e-05 | 0 | 5.732e-06 | 0 | 5.732e-06 | 0.00010765
| Ammonia | 7664-41-7 | 0.00019964 | 0.017489 | 0 | 3.9928e-07 | 0 | 9.0746e-08 | 0 | 9.0746e-08 | 1.4574e-05
| Anthracene | 120-12-7 | 7.966e-08 | 6.8817e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Antimony | 7440-36-0 | 6.3482e-08 | 5.561e-06 | 0 | 2.1161e-07 | 0 | 4.8832e-08 | 0 | 4.8832e-08 | 5.561e-06
| Arsenic | 7440-38-2 | 4.8413e-08 | 4.241e-06 | 0.0020172 | 0.00028478 | 3.7241e-05 | 2.0172e-05 | 7.8085e-05 | 2.0172e-05 | 2.1205e-05
| Barium | 7440-39-3 | 1.7246e-07 | 1.5107e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Benz[a]anthracene | 56-55-3 | 1.0152e-08 | 8.7701e-07 | 4.8343e-05 | 0 | 1.3015e-06 | 0 | 6.768e-07 | 0 | 0
| Benzene | 71-43-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Benzo[a]pyrene 2 | 50-32-8 | 3.2345e-09 | 2.7942e-07 | 7.5221e-05 | 1.6172e-06 | 2.0216e-06 | 3.6756e-07 | 1.0782e-06 | 3.6756e-07 | 0.00013971
| Benzo[b]fluoranthene | 205-99-2 | 8.5909e-09 | 7.4215e-07 | 0.00016209 | 0 | 4.2955e-06 | 0 | 2.2608e-06 | 0 | 0
| Benzo[e]pyrene | 192-97-2 | 6.4888e-09 | 5.6056e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Benzo[g,h,i]perylene | 191-24-2 | 4.8514e-09 | 4.191e-07 | 1.0322e-06 | 0 | 2.8537e-08 | 0 | 1.4269e-08 | 0 | 0
| Benzo[k]fluoranthene | 207-08-9 | 2.5723e-09 | 2.2222e-07 | 1.8374e-06 | 0 | 4.9468e-08 | 0 | 2.5723e-08 | 0 | 0
| Beryllium | 7440-41-7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cadmium | 7440-43-9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Chlorobenzene | 108-90-7 | 5.0725e-08 | 4.382e-06 | 0 | 1.0145e-09 | 0 | 2.3057e-10 | 0 | 2.3057e-10 | 0
| Chrysene | 218-01-9 | 1.6115e-08 | 1.3921e-06 | 3.7477e-05 | 0 | 1.0072e-06 | 0 | 5.3717e-07 | 0 | 0
| Cobalt | 7440-48-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Copper | 7440-50-8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Dibenz[a,h]anthracene | 53-70-3 | 6.7718e-11 | 5.85e-09 | 1.5748e-05 | 0 | 4.2324e-07 | 0 | 2.2573e-07 | 0 | 0
| Diesel exhaust particulates | 200 | 0.0043054 | 0.37193 | 0.043054 | 0.00086107 | 0.0016559 | 0.0001957 | 0.0035878 | 0.0001957 | 0
| Ethyl Benzene | 100-41-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fluoranthene | 206-44-0 | 6.778e-08 | 5.8554e-06 | 0.00012789 | 0 | 3.389e-06 | 0 | 1.7837e-06 | 0 | 0
| Fluorene | 86-73-7 | 3.9722e-07 | 3.4315e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Formaldehyde | 50-00-0 | 0.00058148 | 0.050113 | 0.0034205 | 6.4609e-05 | 0.00013523 | 1.4537e-05 | 0.00029074 | 1.4537e-05 | 0.0010227
| Hexane | 110-54-3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hexavalent chromium | 18540-29-9 | 8.2656e-08 | 7.2406e-06 | 0.0026663 | 9.9585e-07 | 0.00015895 | 9.3927e-08 | 8.2656e-05 | 9.3927e-08 | 2.4135e-05
| Hydrogen Chloride | 7647-01-0 | 4.7251e-05 | 0.0040819 | 0 | 2.3625e-06 | 0 | 5.3694e-07 | 0 | 5.3694e-07 | 1.9437e-06
| Indeno[1,2,3-cd]pyrene | 193-39-5 | 1.9912e-09 | 1.7201e-07 | 3.2642e-06 | 0 | 9.0508e-08 | 0 | 4.6306e-08 | 0 | 0
| Lead | 7439-92-1 | 5.9393e-08 | 5.2028e-06 | 0 | 3.9595e-07 | 0 | 8.9989e-08 | 0 | 8.9989e-08 | 3.4686e-05
| Manganese | 7439-96-5 | 5.1823e-08 | 4.5397e-06 | 0 | 5.7582e-07 | 0 | 1.2956e-07 | 0 | 1.2956e-07 | 1.5132e-05
| Mercury | 7439-97-6 | 3.1942e-09 | 2.7982e-07 | 0 | 4.1484e-08 | 0 | 5.0702e-09 | 0 | 5.0702e-09 | 4.6636e-07
| 2-Methyl naphthalene | 91-57-6 | 2.2315e-06 | 0.00019277 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Naphthalene | 91-20-3 | 4.312e-06 | 0.00037251 | 0.00014869 | 1.1654e-06 | 5.6737e-06 | 2.695e-07 | 1.232e-05 | 2.695e-07 | 1.8625e-06
| Nickel | 365 | 4.6447e-08 | 4.0688e-06 | 1.2223e-05 | 3.3177e-06 | 4.6447e-07 | 7.4915e-07 | 1.0097e-06 | 7.4915e-07 | 2.0344e-05
| Perylene | 198-55-0 | 8.9023e-11 | 7.6905e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Phenanthrene | 85-01-8 | 9.7174e-07 | 8.3946e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Phosphorus | 504 | 1.37e-06 | 0.00012002 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Propylene | 115-07-1 | 0.0001192 | 0.010298 | 0 | 3.9735e-08 | 0 | 9.1696e-09 | 0 | 9.1696e-09 | 0
| Pyrene | 129-00-0 | 2.3852e-07 | 2.0605e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PAHs (excluding Naphthalene) | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Selenium | 7782-49-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Silver | 7440-22-4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Thallium | 7440-28-0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Toluene | 108-88-3 | 2.6732e-05 | 0.0023093 | 0 | 5.3464e-09 | 0 | 1.2151e-09 | 0 | 1.2151e-09 | 3.0791e-07
| Xylenes | 1330-20-7 | 1.0754e-05 | 0.00092899 | 0 | 4.8881e-08 | 0 | 1.1086e-08 | 0 | 1.1086e-08 | 1.0678e-07
| Zinc | 7440-66-6 | 1.2554e-06 | 0.00010998 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL REER for 2,500 kW (g/s per µg/m3) |  |  |  | 0.051792 | 0.0012462 | 0.0020061 | 0.00023854 | 0.0040593 | 0.00023854 | 0.0014104
1 | If the toxic is listed in the Risk-Based Concentrations (Table 2) in OAR Chapter 340-245-8010, then it's considered a permitted toxic. Emission rate is normalized based on operational hours of 8,760 hrs/yr or 24 hrs/day.
Table F2-7. Screening Risk Equivalent Emission Rate - MTU 2250 - 2,250 kW
| Pollutant | CAS/DEQ ID | Long-Term Emission Rate (g/s) | Short-Term Emission Rate (g/s) | REER Used for Modeling with Unit Emission Rate
[5 empty] | Residential Chronic |  | Non-residential Chronic |  |  |  | Acute Non-cancer
[5 empty] | Chronic Cancer | Chronic Non-cancer | Child Cancer | Child Non-cancer | Worker Cancer | Worker Non-cancer
| 1,3-Butadiene | 106-99-0 | 5.1802e-05 | 0.004475 | 0.0015697 | 2.5901e-05 | 6.0234e-05 | 5.8865e-06 | 0.0001295 | 5.8865e-06 | 6.7803e-06
| Acenaphthene | 83-32-9 | 1.7504e-07 | 1.5121e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Acenaphthylene | 208-96-8 | 1.9296e-07 | 1.6669e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Acetaldehyde | 75-07-0 | 0.00018664 | 0.016124 | 0.00041476 | 1.3332e-06 | 1.5554e-05 | 3.0104e-07 | 3.3935e-05 | 3.0104e-07 | 3.4306e-05
| Acrolein | 107-02-8 | 8.0776e-06 | 0.00069781 | 0 | 2.3079e-05 | 0 | 5.3851e-06 | 0 | 5.3851e-06 | 0.00010113
| Ammonia | 7664-41-7 | 0.00018756 | 0.01643 | 0 | 3.7512e-07 | 0 | 8.5254e-08 | 0 | 8.5254e-08 | 1.3692e-05
| Anthracene | 120-12-7 | 1.0772e-07 | 9.3059e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Antimony | 7440-36-0 | 7.4598e-08 | 6.5348e-06 | 0 | 2.4866e-07 | 0 | 5.7383e-08 | 0 | 5.7383e-08 | 6.5348e-06
| Arsenic | 7440-38-2 | 6.4908e-08 | 5.6859e-06 | 0.0027045 | 0.00038181 | 4.9929e-05 | 2.7045e-05 | 0.00010469 | 2.7045e-05 | 2.843e-05
| Barium | 7440-39-3 | 8.7659e-08 | 7.6789e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Benz[a]anthracene | 56-55-3 | 1.1566e-08 | 9.9919e-07 | 5.5078e-05 | 0 | 1.4829e-06 | 0 | 7.7109e-07 | 0 | 0
| Benzene | 71-43-2 | 4.4391e-05 | 0.0038348 | 0.00034147 | 1.4797e-05 | 1.3452e-05 | 3.4147e-06 | 2.9594e-05 | 3.4147e-06 | 0.00013224
| Benzo[a]pyrene 2 | 50-32-8 | 3.4277e-09 | 2.9611e-07 | 7.9713e-05 | 1.7138e-06 | 2.1423e-06 | 3.8951e-07 | 1.1426e-06 | 3.8951e-07 | 0.00014805
| Benzo[b]fluoranthene | 205-99-2 | 1.0568e-08 | 9.1298e-07 | 0.0001994 | 0 | 5.2842e-06 | 0 | 2.7812e-06 | 0 | 0
| Benzo[e]pyrene | 192-97-2 | 7.8318e-09 | 6.7657e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Benzo[g,h,i]perylene | 191-24-2 | 5.2122e-09 | 4.5027e-07 | 1.109e-06 | 0 | 3.066e-08 | 0 | 1.533e-08 | 0 | 0
| Benzo[k]fluoranthene | 207-08-9 | 3.1106e-09 | 2.6871e-07 | 2.2218e-06 | 0 | 5.9818e-08 | 0 | 3.1106e-08 | 0 | 0
| Beryllium | 7440-41-7 | 1.1185e-09 | 9.7982e-08 | 2.6631e-06 | 1.5979e-07 | 1.0168e-07 | 3.6081e-08 | 2.237e-07 | 3.6081e-08 | 4.8991e-06
| Cadmium | 7440-43-9 | 1.8938e-08 | 1.659e-06 | 3.3818e-05 | 3.7877e-06 | 1.3527e-06 | 5.1185e-07 | 2.8266e-06 | 5.1185e-07 | 5.53e-05
| Chlorobenzene | 108-90-7 | 4.7655e-08 | 4.1168e-06 | 0 | 9.5311e-10 | 0 | 2.1662e-10 | 0 | 2.1662e-10 | 0
| Chrysene | 218-01-9 | 1.5965e-08 | 1.3791e-06 | 3.7127e-05 | 0 | 9.9779e-07 | 0 | 5.3215e-07 | 0 | 0
| Cobalt | 7440-48-4 | 3.6928e-09 | 3.2349e-07 | 0 | 3.6928e-08 | 0 | 8.3928e-09 | 0 | 8.3928e-09 | 0
| Copper | 7440-50-8 | 1.1772e-07 | 1.0313e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0313e-07
| Dibenz[a,h]anthracene | 53-70-3 | 2.4709e-10 | 2.1346e-08 | 5.7463e-05 | 0 | 1.5443e-06 | 0 | 8.2364e-07 | 0 | 0
| Diesel exhaust particulates | 200 | 0.0055709 | 0.48126 | 0.055709 | 0.0011142 | 0.0021427 | 0.00025322 | 0.0046424 | 0.00025322 | 0
| Ethyl Benzene | 100-41-4 | 2.5972e-06 | 0.00022437 | 6.4931e-06 | 9.9893e-09 | 2.5972e-07 | 2.3611e-09 | 5.4109e-07 | 2.3611e-09 | 1.0199e-08
| Fluoranthene | 206-44-0 | 8.8152e-08 | 7.6152e-06 | 0.00016632 | 0 | 4.4076e-06 | 0 | 2.3198e-06 | 0 | 0
| Fluorene | 86-73-7 | 5.2049e-07 | 4.4964e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Formaldehyde | 50-00-0 | 0.00064826 | 0.055868 | 0.0038133 | 7.2029e-05 | 0.00015076 | 1.6207e-05 | 0.00032413 | 1.6207e-05 | 0.0011402
| Hexane | 110-54-3 | 6.4097e-06 | 0.00055372 | 0 | 9.1567e-09 | 0 | 2.0676e-09 | 0 | 2.0676e-09 | 0
| Hexavalent chromium | 18540-29-9 | 1.4804e-08 | 1.2968e-06 | 0.00047755 | 1.7836e-07 | 2.8469e-05 | 1.6823e-08 | 1.4804e-05 | 1.6823e-08 | 4.3228e-06
| Hydrogen Chloride | 7647-01-0 | 4.4391e-05 | 0.0038348 | 0 | 2.2196e-06 | 0 | 5.0444e-07 | 0 | 5.0444e-07 | 1.8261e-06
| Indeno[1,2,3-cd]pyrene | 193-39-5 | 2.5522e-09 | 2.2048e-07 | 4.1839e-06 | 0 | 1.1601e-07 | 0 | 5.9353e-08 | 0 | 0
| Lead | 7439-92-1 | 8.5262e-08 | 7.469e-06 | 0 | 5.6841e-07 | 0 | 1.2919e-07 | 0 | 1.2919e-07 | 4.9793e-05
| Manganese | 7439-96-5 | 9.8448e-08 | 8.624e-06 | 0 | 1.0939e-06 | 0 | 2.4612e-07 | 0 | 2.4612e-07 | 2.8747e-05
| Mercury | 7439-97-6 | 3.5419e-09 | 3.1027e-07 | 0 | 4.5999e-08 | 0 | 5.622e-09 | 0 | 5.622e-09 | 5.1712e-07
| 2-Methyl naphthalene | 91-57-6 | 2.9303e-06 | 0.00025314 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Naphthalene | 91-20-3 | 6.2792e-06 | 0.00054244 | 0.00021652 | 1.6971e-06 | 8.2621e-06 | 3.9245e-07 | 1.7941e-05 | 3.9245e-07 | 2.7122e-06
| Nickel | 365 | 4.2723e-08 | 3.7426e-06 | 1.1243e-05 | 3.0517e-06 | 4.2723e-07 | 6.8909e-07 | 9.2877e-07 | 6.8909e-07 | 1.8713e-05
| Perylene | 198-55-0 | 2.8075e-10 | 2.4253e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Phenanthrene | 85-01-8 | 1.0822e-06 | 9.3493e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Phosphorus | 504 | 1.9703e-06 | 0.0001726 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Propylene | 115-07-1 | 0.00011199 | 0.0096746 | 0 | 3.733e-08 | 0 | 8.6146e-09 | 0 | 8.6146e-09 | 0
| Pyrene | 129-00-0 | 2.9785e-07 | 2.573e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PAHs (excluding Naphthalene) | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Selenium | 7782-49-2 | 8.8242e-08 | 7.73e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 3.865e-06
| Silver | 7440-22-4 | 1.1257e-08 | 9.8607e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Thallium | 7440-28-0 | 5.629e-08 | 4.931e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Toluene | 108-88-3 | 2.5114e-05 | 0.0021696 | 0 | 5.0229e-09 | 0 | 1.1416e-09 | 0 | 1.1416e-09 | 2.8928e-07
| Xylenes | 1330-20-7 | 1.0103e-05 | 0.00087277 | 0 | 4.5923e-08 | 0 | 1.0415e-08 | 0 | 1.0415e-08 | 1.0032e-07
| Zinc | 7440-66-6 | 1.2253e-06 | 0.00010733 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL REER for 2,250 kW (g/s per µg/m3) |  |  |  | 0.065904 | 0.0016484 | 0.0024875 | 0.00031456 | 0.00531 | 0.00031456 | 0.0017825
1 | If the toxic is listed in the Risk-Based Concentrations (Table 2) in OAR Chapter 340-245-8010, then it's considered a permitted toxic. Emission rate is normalized based on operational hours of 8,760 hrs/yr or 24 hrs/day.
Table F2-8. Screening Risk Equivalent Emission Rate - CAT C18 - 750 kW
| Pollutant | CAS/DEQ ID | Long-Term Emission Rate (g/s) | Short-Term Emission Rate (g/s) | REER Used for Modeling with Unit Emission Rate
[5 empty] | Residential Chronic |  | Non-residential Chronic |  |  |  | Acute Non-cancer
[5 empty] | Chronic Cancer | Chronic Non-cancer | Child Cancer | Child Non-cancer | Worker Cancer | Worker Non-cancer
| 1,3-Butadiene | 106-99-0 | 1.7034e-05 | 0.0014715 | 0.00051619 | 8.5171e-06 | 1.9807e-05 | 1.9357e-06 | 4.2585e-05 | 1.9357e-06 | 2.2296e-06
| Acenaphthene | 83-32-9 | 5.756e-08 | 4.9725e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Acenaphthylene | 208-96-8 | 6.3452e-08 | 5.4815e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Acetaldehyde | 75-07-0 | 6.1375e-05 | 0.005302 | 0.00013639 | 4.3839e-07 | 5.1145e-06 | 9.8991e-08 | 1.1159e-05 | 9.8991e-08 | 1.1281e-05
| Acrolein | 107-02-8 | 2.6562e-06 | 0.00022946 | 0 | 7.5891e-06 | 0 | 1.7708e-06 | 0 | 1.7708e-06 | 3.3255e-05
| Ammonia | 7664-41-7 | 6.1676e-05 | 0.0054028 | 0 | 1.2335e-07 | 0 | 2.8034e-08 | 0 | 2.8034e-08 | 4.5023e-06
| Anthracene | 120-12-7 | 3.5423e-08 | 3.0601e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Antimony | 7440-36-0 | 2.4531e-08 | 2.1489e-06 | 0 | 8.1768e-08 | 0 | 1.887e-08 | 0 | 1.887e-08 | 2.1489e-06
| Arsenic | 7440-38-2 | 2.1344e-08 | 1.8697e-06 | 0.00088933 | 0.00012555 | 1.6418e-05 | 8.8933e-06 | 3.4426e-05 | 8.8933e-06 | 9.3486e-06
| Barium | 7440-39-3 | 2.8825e-08 | 2.5251e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Benz[a]anthracene | 56-55-3 | 3.8034e-09 | 3.2857e-07 | 1.8111e-05 | 0 | 4.8762e-07 | 0 | 2.5356e-07 | 0 | 0
| Benzene | 71-43-2 | 1.4597e-05 | 0.001261 | 0.00011229 | 4.8658e-06 | 4.4234e-06 | 1.1229e-06 | 9.7315e-06 | 1.1229e-06 | 4.3484e-05
| Benzo[a]pyrene 2 | 50-32-8 | 1.1271e-09 | 9.7371e-08 | 2.6213e-05 | 5.6357e-07 | 7.0446e-07 | 1.2808e-07 | 3.7571e-07 | 1.2808e-07 | 4.8685e-05
| Benzo[b]fluoranthene | 205-99-2 | 3.4753e-09 | 3.0022e-07 | 6.5571e-05 | 0 | 1.7376e-06 | 0 | 9.1455e-07 | 0 | 0
| Benzo[e]pyrene | 192-97-2 | 2.5754e-09 | 2.2248e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Benzo[g,h,i]perylene | 191-24-2 | 1.7139e-09 | 1.4806e-07 | 3.6467e-07 | 0 | 1.0082e-08 | 0 | 5.041e-09 | 0 | 0
| Benzo[k]fluoranthene | 207-08-9 | 1.0229e-09 | 8.8362e-08 | 7.3061e-07 | 0 | 1.967e-08 | 0 | 1.0229e-08 | 0 | 0
| Beryllium | 7440-41-7 | 3.6781e-10 | 3.222e-08 | 8.7573e-07 | 5.2544e-08 | 3.3437e-08 | 1.1865e-08 | 7.3561e-08 | 1.1865e-08 | 1.611e-06
| Cadmium | 7440-43-9 | 6.2276e-09 | 5.4554e-07 | 1.1121e-05 | 1.2455e-06 | 4.4483e-07 | 1.6831e-07 | 9.2949e-07 | 1.6831e-07 | 1.8185e-05
| Chlorobenzene | 108-90-7 | 1.5671e-08 | 1.3538e-06 | 0 | 3.1342e-10 | 0 | 7.1231e-11 | 0 | 7.1231e-11 | 0
| Chrysene | 218-01-9 | 5.2497e-09 | 4.5351e-07 | 1.2209e-05 | 0 | 3.2811e-07 | 0 | 1.7499e-07 | 0 | 0
| Cobalt | 7440-48-4 | 1.2143e-09 | 1.0638e-07 | 0 | 1.2143e-08 | 0 | 2.7598e-09 | 0 | 2.7598e-09 | 0
| Copper | 7440-50-8 | 3.8712e-08 | 3.3912e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3912e-08
| Dibenz[a,h]anthracene | 53-70-3 | 8.1252e-11 | 7.0192e-09 | 1.8896e-05 | 0 | 5.0782e-07 | 0 | 2.7084e-07 | 0 | 0
| Diesel exhaust particulates | 200 | 0.018393 | 1.5889 | 0.18393 | 0.0036785 | 0.007074 | 0.00083602 | 0.015327 | 0.00083602 | 0
| Ethyl Benzene | 100-41-4 | 8.5406e-07 | 7.378e-05 | 2.1351e-06 | 3.2848e-09 | 8.5406e-08 | 7.7641e-10 | 1.7793e-07 | 7.7641e-10 | 3.3536e-09
| Fluoranthene | 206-44-0 | 2.8987e-08 | 2.5041e-06 | 5.4693e-05 | 0 | 1.4494e-06 | 0 | 7.6282e-07 | 0 | 0
| Fluorene | 86-73-7 | 1.7116e-07 | 1.4786e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Formaldehyde | 50-00-0 | 0.00021317 | 0.018371 | 0.0012539 | 2.3686e-05 | 4.9575e-05 | 5.3293e-06 | 0.00010659 | 5.3293e-06 | 0.00037493
| Hexane | 110-54-3 | 2.1077e-06 | 0.00018208 | 0 | 3.011e-09 | 0 | 6.7991e-10 | 0 | 6.7991e-10 | 0
| Hexavalent chromium | 18540-29-9 | 4.8681e-09 | 4.2645e-07 | 0.00015704 | 5.8652e-08 | 9.3617e-06 | 5.5319e-09 | 4.8681e-06 | 5.5319e-09 | 1.4215e-06
| Hydrogen Chloride | 7647-01-0 | 1.4597e-05 | 0.001261 | 0 | 7.2987e-07 | 0 | 1.6588e-07 | 0 | 1.6588e-07 | 6.0049e-07
| Indeno[1,2,3-cd]pyrene | 193-39-5 | 8.3925e-10 | 7.2501e-08 | 1.3758e-06 | 0 | 3.8148e-08 | 0 | 1.9517e-08 | 0 | 0
| Lead | 7439-92-1 | 2.8037e-08 | 2.4561e-06 | 0 | 1.8691e-07 | 0 | 4.248e-08 | 0 | 4.248e-08 | 1.6374e-05
| Manganese | 7439-96-5 | 3.2373e-08 | 2.8359e-06 | 0 | 3.597e-07 | 0 | 8.0932e-08 | 0 | 8.0932e-08 | 9.4529e-06
| Mercury | 7439-97-6 | 1.1647e-09 | 1.0203e-07 | 0 | 1.5126e-08 | 0 | 1.8487e-09 | 0 | 1.8487e-09 | 1.7005e-07
| 2-Methyl naphthalene | 91-57-6 | 9.6359e-07 | 8.3242e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Naphthalene | 91-20-3 | 2.0648e-06 | 0.00017837 | 7.12e-05 | 5.5806e-07 | 2.7169e-06 | 1.2905e-07 | 5.8995e-06 | 1.2905e-07 | 8.9187e-07
| Nickel | 365 | 1.4049e-08 | 1.2307e-06 | 3.6971e-06 | 1.0035e-06 | 1.4049e-07 | 2.266e-07 | 3.0541e-07 | 2.266e-07 | 6.1534e-06
| Perylene | 198-55-0 | 9.232e-11 | 7.9753e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Phenanthrene | 85-01-8 | 3.5588e-07 | 3.0744e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Phosphorus | 504 | 6.479e-07 | 5.6756e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Propylene | 115-07-1 | 3.6826e-05 | 0.0031813 | 0 | 1.2275e-08 | 0 | 2.8328e-09 | 0 | 2.8328e-09 | 0
| Pyrene | 129-00-0 | 9.7942e-08 | 8.461e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PAHs (excluding Naphthalene) | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Selenium | 7782-49-2 | 2.9017e-08 | 2.5419e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2709e-06
| Silver | 7440-22-4 | 3.7015e-09 | 3.2426e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Thallium | 7440-28-0 | 1.851e-08 | 1.6215e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Toluene | 108-88-3 | 8.2585e-06 | 0.00071343 | 0 | 1.6517e-09 | 0 | 3.7539e-10 | 0 | 3.7539e-10 | 9.5124e-08
| Xylenes | 1330-20-7 | 3.3222e-06 | 0.000287 | 0 | 1.5101e-08 | 0 | 3.4249e-09 | 0 | 3.4249e-09 | 3.2988e-08
| Zinc | 7440-66-6 | 4.0291e-07 | 3.5295e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL REER for 750 kW (g/s per µg/m3) |  |  |  | 0.18728 | 0.0038542 | 0.0071875 | 0.00085619 | 0.015547 | 0.00085619 | 0.00058616
1 | If the toxic is listed in the Risk-Based Concentrations (Table 2) in OAR Chapter 340-245-8010, then it's considered a permitted toxic. Emission rate is normalized based on operational hours of 8,760 hrs/yr or 24 hrs/day.
Table F2-9. Screening Risk Equivalent Emission Rate - CAT 3512C - 1,500 kW
| Pollutant | CAS/DEQ ID | Long-Term Emission Rate (g/s) | Short-Term Emission Rate (g/s) | REER Used for Modeling with Unit Emission Rate
[5 empty] | Residential Chronic |  | Non-residential Chronic |  |  |  | Acute Non-cancer
[5 empty] | Chronic Cancer | Chronic Non-cancer | Child Cancer | Child Non-cancer | Worker Cancer | Worker Non-cancer
| 1,3-Butadiene | 106-99-0 | 3.2797e-05 | 0.0028333 | 0.00099385 | 1.6399e-05 | 3.8136e-05 | 3.7269e-06 | 8.1993e-05 | 3.7269e-06 | 4.2928e-06
| Acenaphthene | 83-32-9 | 1.1082e-07 | 9.5738e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Acenaphthylene | 208-96-8 | 1.2217e-07 | 1.0554e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Acetaldehyde | 75-07-0 | 0.00011817 | 0.010208 | 0.0002626 | 8.4406e-07 | 9.8474e-06 | 1.9059e-07 | 2.1485e-05 | 1.9059e-07 | 2.172e-05
| Acrolein | 107-02-8 | 5.1142e-06 | 0.0004418 | 0 | 1.4612e-05 | 0 | 3.4094e-06 | 0 | 3.4094e-06 | 6.4029e-05
| Ammonia | 7664-41-7 | 0.00011875 | 0.010402 | 0 | 2.375e-07 | 0 | 5.3977e-08 | 0 | 5.3977e-08 | 8.6687e-06
| Anthracene | 120-12-7 | 6.8202e-08 | 5.8919e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Antimony | 7440-36-0 | 4.723e-08 | 4.1374e-06 | 0 | 1.5743e-07 | 0 | 3.6331e-08 | 0 | 3.6331e-08 | 4.1374e-06
| Arsenic | 7440-38-2 | 4.1095e-08 | 3.5999e-06 | 0.0017123 | 0.00024173 | 3.1611e-05 | 1.7123e-05 | 6.6282e-05 | 1.7123e-05 | 1.8e-05
| Barium | 7440-39-3 | 5.5499e-08 | 4.8617e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Benz[a]anthracene | 56-55-3 | 7.323e-09 | 6.3261e-07 | 3.4871e-05 | 0 | 9.3884e-07 | 0 | 4.882e-07 | 0 | 0
| Benzene | 71-43-2 | 2.8105e-05 | 0.002428 | 0.00021619 | 9.3684e-06 | 8.5168e-06 | 2.1619e-06 | 1.8737e-05 | 2.1619e-06 | 8.3722e-05
| Benzo[a]pyrene 2 | 50-32-8 | 2.1702e-09 | 1.8748e-07 | 5.0469e-05 | 1.0851e-06 | 1.3564e-06 | 2.4661e-07 | 7.2339e-07 | 2.4661e-07 | 9.3738e-05
| Benzo[b]fluoranthene | 205-99-2 | 6.6912e-09 | 5.7804e-07 | 0.00012625 | 0 | 3.3456e-06 | 0 | 1.7608e-06 | 0 | 0
| Benzo[e]pyrene | 192-97-2 | 4.9585e-09 | 4.2836e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Benzo[g,h,i]perylene | 191-24-2 | 3.3e-09 | 2.8508e-07 | 7.0212e-07 | 0 | 1.9412e-08 | 0 | 9.7058e-09 | 0 | 0
| Benzo[k]fluoranthene | 207-08-9 | 1.9694e-09 | 1.7013e-07 | 1.4067e-06 | 0 | 3.7873e-08 | 0 | 1.9694e-08 | 0 | 0
| Beryllium | 7440-41-7 | 7.0816e-10 | 6.2035e-08 | 1.6861e-06 | 1.0117e-07 | 6.4379e-08 | 2.2844e-08 | 1.4163e-07 | 2.2844e-08 | 3.1018e-06
| Cadmium | 7440-43-9 | 1.199e-08 | 1.0504e-06 | 2.1411e-05 | 2.3981e-06 | 8.5646e-07 | 3.2406e-07 | 1.7896e-06 | 3.2406e-07 | 3.5012e-05
| Chlorobenzene | 108-90-7 | 3.0172e-08 | 2.6065e-06 | 0 | 6.0344e-10 | 0 | 1.3715e-10 | 0 | 1.3715e-10 | 0
| Chrysene | 218-01-9 | 1.0108e-08 | 8.7317e-07 | 2.3506e-05 | 0 | 6.3173e-07 | 0 | 3.3692e-07 | 0 | 0
| Cobalt | 7440-48-4 | 2.338e-09 | 2.0481e-07 | 0 | 2.338e-08 | 0 | 5.3137e-09 | 0 | 5.3137e-09 | 0
| Copper | 7440-50-8 | 7.4535e-08 | 6.5293e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5293e-08
| Dibenz[a,h]anthracene | 53-70-3 | 1.5644e-10 | 1.3515e-08 | 3.6381e-05 | 0 | 9.7775e-07 | 0 | 5.2147e-07 | 0 | 0
| Diesel exhaust particulates | 200 | 0.0035271 | 0.3047 | 0.035271 | 0.00070542 | 0.0013566 | 0.00016032 | 0.0029393 | 0.00016032 | 0
| Ethyl Benzene | 100-41-4 | 1.6444e-06 | 0.00014205 | 4.1109e-06 | 6.3245e-09 | 1.6444e-07 | 1.4949e-09 | 3.4258e-07 | 1.4949e-09 | 6.457e-09
| Fluoranthene | 206-44-0 | 5.5811e-08 | 4.8214e-06 | 0.0001053 | 0 | 2.7906e-06 | 0 | 1.4687e-06 | 0 | 0
| Fluorene | 86-73-7 | 3.2954e-07 | 2.8468e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Formaldehyde | 50-00-0 | 0.00041043 | 0.035372 | 0.0024143 | 4.5604e-05 | 9.545e-05 | 1.0261e-05 | 0.00020522 | 1.0261e-05 | 0.00072187
| Hexane | 110-54-3 | 4.0581e-06 | 0.00035057 | 0 | 5.7973e-09 | 0 | 1.3091e-09 | 0 | 1.3091e-09 | 0
| Hexavalent chromium | 18540-29-9 | 9.3729e-09 | 8.2107e-07 | 0.00030235 | 1.1293e-07 | 1.8025e-05 | 1.0651e-08 | 9.3729e-06 | 1.0651e-08 | 2.7369e-06
| Hydrogen Chloride | 7647-01-0 | 2.8105e-05 | 0.002428 | 0 | 1.4053e-06 | 0 | 3.1938e-07 | 0 | 3.1938e-07 | 1.1562e-06
| Indeno[1,2,3-cd]pyrene | 193-39-5 | 1.6159e-09 | 1.3959e-07 | 2.649e-06 | 0 | 7.3448e-08 | 0 | 3.7578e-08 | 0 | 0
| Lead | 7439-92-1 | 5.3982e-08 | 4.7288e-06 | 0 | 3.5988e-07 | 0 | 8.1791e-08 | 0 | 8.1791e-08 | 3.1525e-05
| Manganese | 7439-96-5 | 6.233e-08 | 5.4601e-06 | 0 | 6.9256e-07 | 0 | 1.5583e-07 | 0 | 1.5583e-07 | 1.82e-05
| Mercury | 7439-97-6 | 2.2425e-09 | 1.9644e-07 | 0 | 2.9123e-08 | 0 | 3.5595e-09 | 0 | 3.5595e-09 | 3.274e-07
| 2-Methyl naphthalene | 91-57-6 | 1.8553e-06 | 0.00016027 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Naphthalene | 91-20-3 | 3.9755e-06 | 0.00034344 | 0.00013709 | 1.0745e-06 | 5.231e-06 | 2.4847e-07 | 1.1359e-05 | 2.4847e-07 | 1.7172e-06
| Nickel | 365 | 2.7049e-08 | 2.3695e-06 | 7.1183e-06 | 1.9321e-06 | 2.7049e-07 | 4.3628e-07 | 5.8803e-07 | 4.3628e-07 | 1.1848e-05
| Perylene | 198-55-0 | 1.7775e-10 | 1.5355e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Phenanthrene | 85-01-8 | 6.852e-07 | 5.9193e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Phosphorus | 504 | 1.2475e-06 | 0.00010928 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Propylene | 115-07-1 | 7.0904e-05 | 0.0061253 | 0 | 2.3635e-08 | 0 | 5.4542e-09 | 0 | 5.4542e-09 | 0
| Pyrene | 129-00-0 | 1.8858e-07 | 1.6291e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| PAHs (excluding Naphthalene) | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Selenium | 7782-49-2 | 5.5869e-08 | 4.8941e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 2.447e-06
| Silver | 7440-22-4 | 7.1269e-09 | 6.2431e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Thallium | 7440-28-0 | 3.5639e-08 | 3.1219e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Toluene | 108-88-3 | 1.5901e-05 | 0.0013736 | 0 | 3.1801e-09 | 0 | 7.2276e-10 | 0 | 7.2276e-10 | 1.8315e-07
| Xylenes | 1330-20-7 | 6.3965e-06 | 0.00055258 | 0 | 2.9075e-08 | 0 | 6.5943e-09 | 0 | 6.5943e-09 | 6.3515e-08
| Zinc | 7440-66-6 | 7.7575e-07 | 6.7956e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL REER for 1,500 kW (g/s per µg/m3) |  |  |  | 0.041726 | 0.0010437 | 0.0015749 | 0.00019916 | 0.0033619 | 0.00019916 | 0.0011286
1 | If the toxic is listed in the Risk-Based Concentrations (Table 2) in OAR Chapter 340-245-8010, then it's considered a permitted toxic. Emission rate is normalized based on operational hours of 8,760 hrs/yr or 24 hrs/day.
Table F3-1. Screening Risk Equivalent Emission Rate - Summary Table
| Generator | Type | Residential Cancer | Residential Non-Cancer | Child Cancer | Child Non-Cancer | Worker Cancer | Worker Non-Cancer | Acute Non-Cancer |  |  | Reference
| CAT 27 - 750 kW | Type A | 0.021671 | 0.00054206 | 0.00081799 | 0.00010344 | 0.0017461 | 0.00010344 | 0.00058616 |  |  | Type A
| CAT 27 - 800 kW | Type B | 0.023167 | 0.00057947 | 0.00087445 | 0.00011058 | 0.0018667 | 0.00011058 | 0.00062662 |  |  | Type B
| CAT 32 - 1,000 kW | Type C | 0.029071 | 0.00072712 | 0.0010973 | 0.00013875 | 0.0023423 | 0.00013875 | 0.00078628 |  |  | Type C
| CAT 3516C Trans - 1,825 kW | Type D | 0.051915 | 0.0012985 | 0.0019595 | 0.00024779 | 0.0041829 | 0.00024779 | 0.0014042 |  |  | Type D
| CAT 3516C - 2,000 kW | Type E | 0.05616 | 0.0014047 | 0.0021197 | 0.00026805 | 0.0045249 | 0.00026805 | 0.001519 |  |  | Type E
| CAT 3516C - 2,500 kW | Type F | 0.051792 | 0.0012462 | 0.0020061 | 0.00023854 | 0.0040593 | 0.00023854 | 0.0014104 |  |  | Type F
| MTU 2250 - 2,250 kW | Type G | 0.065904 | 0.0016484 | 0.0024875 | 0.00031456 | 0.00531 | 0.00031456 | 0.0017825 |  |  | Type G
| CAT C18 - 750 kW | Type H | 0.18728 | 0.0038542 | 0.0071875 | 0.00085619 | 0.015547 | 0.00085619 | 0.00058616 |  |  | Type H
| CAT 3512C - 1,500 kW | Type I | 0.041726 | 0.0010437 | 0.0015749 | 0.00019916 | 0.0033619 | 0.00019916 | 0.0011286 |  |  | Type I
Table F3-2 Screening REER Rankings by Generator Type
| REER Rankings | Residential Cancer | Residential Non-Cancer | Child Cancer | Child Non-Cancer | Worker Cancer | Worker Non-Cancer
| 1 | Type H | Type H | Type H | Type H | Type H | Type H
| 2 | Type G | Type G | Type G | Type G | Type G | Type G
| 3 | Type E | Type E | Type E | Type E | Type E | Type E
| 4 | Type D | Type D | Type F | Type D | Type D | Type D
| 5 | Type F | Type F | Type D | Type F | Type F | Type F
| 6 | Type I | Type I | Type I | Type I | Type I | Type I
| 7 | Type C | Type C | Type C | Type C | Type C | Type C
| 8 | Type B | Type B | Type B | Type B | Type B | Type B
| 9 | Type A | Type A | Type A | Type A | Type A | Type A
Note on C598: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Verifying that the logic of using residential risk ranking accounts for highest non-cancer risk.
Note on F601: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Portable generator is included in child risk, not concerned.

## ChiCanF
Gen | X | Y | AveConc | EL | ChiCan | Lookup
B04_G13A | 291600 | 5080100 | 0.066933 | Child | 0.0001419 | 291600_5080100
B04_G13B | 291600 | 5080100 | 0.067006 | Child | 0.00014205 | 291600_5080100
B04_G14A | 291600 | 5080100 | 0.067076 | Child | 0.0001422 | 291600_5080100
B04_G14B | 291600 | 5080100 | 0.067178 | Child | 0.00014242 | 291600_5080100
B04_G15A | 291600 | 5080100 | 0.067491 | Child | 0.00014308 | 291600_5080100
B04_G15B | 291600 | 5080100 | 0.067371 | Child | 0.00014283 | 291600_5080100
B04_G15C | 291600 | 5080100 | 0.048608 | Child | 9.7703e-05 | 291600_5080100
B04_G16A | 291600 | 5080100 | 0.04876 | Child | 9.8007e-05 | 291600_5080100
B04_G16B | 291600 | 5080100 | 0.048845 | Child | 9.8179e-05 | 291600_5080100
B04_G17A | 291600 | 5080100 | 0.049587 | Child | 0.00012347 | 291600_5080100
B04_G17B | 291600 | 5080100 | 0.049665 | Child | 0.00012367 | 291600_5080100
B04_G17C | 291600 | 5080100 | 0.049727 | Child | 0.00012382 | 291600_5080100
B04_G18A | 291600 | 5080100 | 0.049499 | Child | 9.9493e-05 | 291600_5080100
B04_G18B | 291600 | 5080100 | 0.049632 | Child | 9.976e-05 | 291600_5080100
B04_G19A | 291600 | 5080100 | 0.049719 | Child | 9.9934e-05 | 291600_5080100
B04_G19B | 291600 | 5080100 | 0.049861 | Child | 0.00010022 | 291600_5080100
B04_G20A | 291600 | 5080100 | 0.049928 | Child | 0.00010036 | 291600_5080100
B04_G20B | 291600 | 5080100 | 0.050079 | Child | 0.00010066 | 291600_5080100
B52_G01A | 291600 | 5080100 | 0.049881 | Child | 0.00010026 | 291600_5080100
B52_G01B | 291600 | 5080100 | 0.049871 | Child | 0.00010024 | 291600_5080100
B52_G02A | 291600 | 5080100 | 0.04998 | Child | 0.00010046 | 291600_5080100
B52_G02B | 291600 | 5080100 | 0.049963 | Child | 0.00010043 | 291600_5080100
B52_G03A | 291600 | 5080100 | 0.050004 | Child | 0.00010051 | 291600_5080100
B52_G03B | 291600 | 5080100 | 0.050018 | Child | 0.00010054 | 291600_5080100
B52_G04A | 291600 | 5080100 | 0.050049 | Child | 0.0001006 | 291600_5080100
B52_G04B | 291600 | 5080100 | 0.050038 | Child | 0.00010058 | 291600_5080100
B52_G04C | 291600 | 5080100 | 0.050068 | Child | 0.00010064 | 291600_5080100
B52_G05A | 291600 | 5080100 | 0.050131 | Child | 0.00010076 | 291600_5080100
B52_G05B | 291600 | 5080100 | 0.050137 | Child | 0.00010077 | 291600_5080100
B52_G05C | 291600 | 5080100 | 0.050126 | Child | 0.00010075 | 291600_5080100
B52_G06A | 291600 | 5080100 | 0.050152 | Child | 0.0001008 | 291600_5080100
B52_G06B | 291600 | 5080100 | 0.050147 | Child | 0.0001008 | 291600_5080100
B52_G07A | 291600 | 5080100 | 0.05016 | Child | 0.00010082 | 291600_5080100
B52_G07B | 291600 | 5080100 | 0.050163 | Child | 0.00010083 | 291600_5080100
B52_G08A | 291600 | 5080100 | 0.050165 | Child | 0.00010083 | 291600_5080100
B52_G08B | 291600 | 5080100 | 0.050164 | Child | 0.00010083 | 291600_5080100
B55_G01A | 291600 | 5080100 | 0.048441 | Child | 9.7367e-05 | 291600_5080100
B55_G01B | 291600 | 5080100 | 0.048448 | Child | 9.738e-05 | 291600_5080100
B55_G02A | 291600 | 5080100 | 0.048418 | Child | 9.732e-05 | 291600_5080100
B55_G02B | 291600 | 5080100 | 0.04843 | Child | 9.7344e-05 | 291600_5080100
B55_G03A | 291600 | 5080100 | 0.048592 | Child | 9.7671e-05 | 291600_5080100
B55_G03B | 291600 | 5080100 | 0.048599 | Child | 9.7685e-05 | 291600_5080100
B55_G04A | 291600 | 5080100 | 0.04857 | Child | 9.7626e-05 | 291600_5080100
B55_G04B | 291600 | 5080100 | 0.048587 | Child | 9.766e-05 | 291600_5080100
B55_G04C | 291600 | 5080100 | 0.048558 | Child | 9.7602e-05 | 291600_5080100
B55_G05A | 291600 | 5080100 | 0.048391 | Child | 9.7266e-05 | 291600_5080100
B55_G05B | 291600 | 5080100 | 0.048427 | Child | 9.7339e-05 | 291600_5080100
B55_G05C | 291600 | 5080100 | 0.048446 | Child | 9.7376e-05 | 291600_5080100
B55_G06A | 291600 | 5080100 | 0.048324 | Child | 9.7131e-05 | 291600_5080100
B55_G06B | 291600 | 5080100 | 0.04837 | Child | 9.7223e-05 | 291600_5080100
B55_G07A | 291600 | 5080100 | 0.04824 | Child | 9.6962e-05 | 291600_5080100
B55_G07B | 291600 | 5080100 | 0.048266 | Child | 9.7016e-05 | 291600_5080100
B58_G01A | 291600 | 5080100 | 0.047971 | Child | 9.6422e-05 | 291600_5080100
B58_G01B | 291600 | 5080100 | 0.048062 | Child | 9.6605e-05 | 291600_5080100
B58_G02A | 291600 | 5080100 | 0.047863 | Child | 9.6204e-05 | 291600_5080100
B58_G02B | 291600 | 5080100 | 0.047925 | Child | 9.6329e-05 | 291600_5080100
B58_G03A | 291600 | 5080100 | 0.047804 | Child | 9.6087e-05 | 291600_5080100
B58_G03B | 291600 | 5080100 | 0.047834 | Child | 9.6147e-05 | 291600_5080100
B58_G04A | 291600 | 5080100 | 0.047802 | Child | 9.6081e-05 | 291600_5080100
B58_G04B | 291600 | 5080100 | 0.047797 | Child | 9.6072e-05 | 291600_5080100
B58_G04C | 291600 | 5080100 | 0.047815 | Child | 9.6107e-05 | 291600_5080100
B58_G05A | 291600 | 5080100 | 0.048302 | Child | 9.7087e-05 | 291600_5080100
B58_G05B | 291600 | 5080100 | 0.048185 | Child | 9.6851e-05 | 291600_5080100
B58_G05C | 291600 | 5080100 | 0.048101 | Child | 9.6682e-05 | 291600_5080100
B58_G06A | 291600 | 5080100 | 0.048518 | Child | 9.7521e-05 | 291600_5080100
B58_G06B | 291600 | 5080100 | 0.048381 | Child | 9.7245e-05 | 291600_5080100
B58_G07A | 291600 | 5080100 | 0.048756 | Child | 9.8e-05 | 291600_5080100
B58_G07B | 291600 | 5080100 | 0.048605 | Child | 9.7695e-05 | 291600_5080100
B58_G08A | 291600 | 5080100 | 0.049016 | Child | 9.8522e-05 | 291600_5080100
B58_G08B | 291600 | 5080100 | 0.048853 | Child | 9.8194e-05 | 291600_5080100
B61_G01A | 291600 | 5080100 | 0.049038 | Child | 9.8566e-05 | 291600_5080100
B61_G01B | 291600 | 5080100 | 0.04919 | Child | 9.8872e-05 | 291600_5080100
B61_G02A | 291600 | 5080100 | 0.048789 | Child | 9.8066e-05 | 291600_5080100
B61_G02B | 291600 | 5080100 | 0.048934 | Child | 9.8357e-05 | 291600_5080100
B61_G03A | 291600 | 5080100 | 0.048576 | Child | 9.7638e-05 | 291600_5080100
B61_G03B | 291600 | 5080100 | 0.048709 | Child | 9.7905e-05 | 291600_5080100
B61_G04A | 291600 | 5080100 | 0.048386 | Child | 9.7256e-05 | 291600_5080100
B61_G04B | 291600 | 5080100 | 0.048501 | Child | 9.7487e-05 | 291600_5080100
B61_G04C | 291600 | 5080100 | 0.048317 | Child | 9.7117e-05 | 291600_5080100
B61_G05A | 291600 | 5080100 | 0.048001 | Child | 9.6482e-05 | 291600_5080100
B61_G05B | 291600 | 5080100 | 0.04801 | Child | 9.6501e-05 | 291600_5080100
B61_G05C | 291600 | 5080100 | 0.048022 | Child | 9.6524e-05 | 291600_5080100
B61_G06A | 291600 | 5080100 | 0.048023 | Child | 9.6526e-05 | 291600_5080100
B61_G06B | 291600 | 5080100 | 0.048003 | Child | 9.6487e-05 | 291600_5080100
B61_G07A | 291600 | 5080100 | 0.048093 | Child | 9.6666e-05 | 291600_5080100
B61_G07B | 291600 | 5080100 | 0.048043 | Child | 9.6565e-05 | 291600_5080100
B61_G08A | 291600 | 5080100 | 0.048194 | Child | 9.6869e-05 | 291600_5080100
B61_G08B | 291600 | 5080100 | 0.048126 | Child | 9.6733e-05 | 291600_5080100
P04_GEN1 | 291600 | 5080100 | 0.18714 | Child | 0.00015308 | 291600_5080100
P04_GEN2 | 291600 | 5080100 | 0.18709 | Child | 0.00016352 | 291600_5080100
P04_GEN3 | 291600 | 5080100 | 0.17703 | Child | 0.00015472 | 291600_5080100
P04_GEN4 | 291600 | 5080100 | 0.19703 | Child | 0.00016117 | 291600_5080100
P04_GEN5 | 291600 | 5080100 | 0.17782 | Child | 0.00015541 | 291600_5080100
P04_GEN6 | 291600 | 5080100 | 0.19597 | Child | 0.0001603 | 291600_5080100
P04_GENC | 291600 | 5080100 | 0.13777 | Child | 0.00015155 | 291600_5080100
SKILODG1 | 291600 | 5080100 | 0.20622 | Child | 0.0014827 | 291600_5080100
SKILODG2 | 291600 | 5080100 | 0.074886 | Child | 0.00011757 | 291600_5080100
PORTABLE | 291600 | 5080100 | 0.083465 | Child | 0.00016359 | 291600_5080100

## WorCanF
Gen | X | Y | AveConc | EL | WorCan | Lookup
SKILODG1 | 293903.2 | 5079885.1 | 11.8263 | Worker | 0.18331 | 293903.2_5079885.1
P04_GENC | 293903.2 | 5079885.1 | 44.9688 | Worker | 0.10523 | 293903.2_5079885.1
B55_G02A | 293903.2 | 5079885.1 | 21.1522 | Worker | 0.085878 | 293903.2_5079885.1
B55_G03B | 293903.2 | 5079885.1 | 21.0669 | Worker | 0.085532 | 293903.2_5079885.1
B55_G03A | 293903.2 | 5079885.1 | 19.9985 | Worker | 0.081194 | 293903.2_5079885.1
B55_G02B | 293903.2 | 5079885.1 | 19.1391 | Worker | 0.077705 | 293903.2_5079885.1
B55_G04B | 293903.2 | 5079885.1 | 18.6563 | Worker | 0.075745 | 293903.2_5079885.1
B55_G04A | 293903.2 | 5079885.1 | 16.3372 | Worker | 0.066329 | 293903.2_5079885.1
B55_G04C | 293903.2 | 5079885.1 | 14.576 | Worker | 0.059179 | 293903.2_5079885.1
B04_G17C | 293903.2 | 5079885.1 | 11.0882 | Worker | 0.058878 | 293903.2_5079885.1
B04_G17B | 293903.2 | 5079885.1 | 10.6797 | Worker | 0.056709 | 293903.2_5079885.1
B04_G17A | 293903.2 | 5079885.1 | 9.9144 | Worker | 0.052646 | 293903.2_5079885.1
B55_G01A | 293903.2 | 5079885.1 | 11.82 | Worker | 0.047989 | 293903.2_5079885.1
B52_G06A | 293903.2 | 5079885.1 | 10.9219 | Worker | 0.044343 | 293903.2_5079885.1
B52_G07A | 293903.2 | 5079885.1 | 10.5623 | Worker | 0.042883 | 293903.2_5079885.1
B52_G06B | 293903.2 | 5079885.1 | 10.2344 | Worker | 0.041552 | 293903.2_5079885.1
B52_G07B | 293903.2 | 5079885.1 | 9.475 | Worker | 0.038468 | 293903.2_5079885.1
B04_G18A | 293903.2 | 5079885.1 | 8.1805 | Worker | 0.033213 | 293903.2_5079885.1
B04_G18B | 293903.2 | 5079885.1 | 7.9626 | Worker | 0.032328 | 293903.2_5079885.1
B04_G19A | 293903.2 | 5079885.1 | 7.7184 | Worker | 0.031337 | 293903.2_5079885.1
B52_G01B | 293903.2 | 5079885.1 | 7.5265 | Worker | 0.030558 | 293903.2_5079885.1
B52_G01A | 293903.2 | 5079885.1 | 7.392 | Worker | 0.030012 | 293903.2_5079885.1
B04_G19B | 293903.2 | 5079885.1 | 7.3829 | Worker | 0.029975 | 293903.2_5079885.1
B55_G01B | 293903.2 | 5079885.1 | 7.1841 | Worker | 0.029168 | 293903.2_5079885.1
B55_G05C | 293903.2 | 5079885.1 | 7.1275 | Worker | 0.028938 | 293903.2_5079885.1
B52_G02B | 293903.2 | 5079885.1 | 7.1059 | Worker | 0.02885 | 293903.2_5079885.1
B04_G20A | 293903.2 | 5079885.1 | 7.0709 | Worker | 0.028708 | 293903.2_5079885.1
B52_G08B | 293903.2 | 5079885.1 | 6.9674 | Worker | 0.028288 | 293903.2_5079885.1
B52_G02A | 293903.2 | 5079885.1 | 6.8956 | Worker | 0.027996 | 293903.2_5079885.1
PORTABLE | 293903.2 | 5079885.1 | 6.6304 | Worker | 0.027715 | 293903.2_5079885.1
B55_G05B | 293903.2 | 5079885.1 | 6.6993 | Worker | 0.027199 | 293903.2_5079885.1
B52_G03A | 293903.2 | 5079885.1 | 6.5579 | Worker | 0.026625 | 293903.2_5079885.1
B52_G03B | 293903.2 | 5079885.1 | 6.3599 | Worker | 0.025821 | 293903.2_5079885.1
B52_G04B | 293903.2 | 5079885.1 | 6.0484 | Worker | 0.024557 | 293903.2_5079885.1
B55_G05A | 293903.2 | 5079885.1 | 6.0363 | Worker | 0.024507 | 293903.2_5079885.1
B52_G08A | 293903.2 | 5079885.1 | 6.0256 | Worker | 0.024464 | 293903.2_5079885.1
B04_G15A | 293903.2 | 5079885.1 | 5.3539 | Worker | 0.0242 | 293903.2_5079885.1
B04_G20B | 293903.2 | 5079885.1 | 5.9276 | Worker | 0.024066 | 293903.2_5079885.1
P04_GEN5 | 293903.2 | 5079885.1 | 12.7946 | Worker | 0.023926 | 293903.2_5079885.1
P04_GEN3 | 293903.2 | 5079885.1 | 12.7928 | Worker | 0.023923 | 293903.2_5079885.1
B52_G04A | 293903.2 | 5079885.1 | 5.8719 | Worker | 0.02384 | 293903.2_5079885.1
B61_G04A | 293903.2 | 5079885.1 | 5.8005 | Worker | 0.02355 | 293903.2_5079885.1
P04_GEN6 | 293903.2 | 5079885.1 | 13.3675 | Worker | 0.023393 | 293903.2_5079885.1
B55_G06B | 293903.2 | 5079885.1 | 5.6995 | Worker | 0.02314 | 293903.2_5079885.1
B52_G04C | 293903.2 | 5079885.1 | 5.622 | Worker | 0.022825 | 293903.2_5079885.1
B61_G04B | 293903.2 | 5079885.1 | 5.5901 | Worker | 0.022696 | 293903.2_5079885.1
B04_G15B | 293903.2 | 5079885.1 | 4.9158 | Worker | 0.022219 | 293903.2_5079885.1
B61_G03B | 293903.2 | 5079885.1 | 5.0999 | Worker | 0.020706 | 293903.2_5079885.1
B61_G02A | 293903.2 | 5079885.1 | 5.0857 | Worker | 0.020648 | 293903.2_5079885.1
B04_G16B | 293903.2 | 5079885.1 | 5.0819 | Worker | 0.020632 | 293903.2_5079885.1
B61_G02B | 293903.2 | 5079885.1 | 5.0235 | Worker | 0.020395 | 293903.2_5079885.1
B61_G03A | 293903.2 | 5079885.1 | 4.9971 | Worker | 0.020288 | 293903.2_5079885.1
B61_G01A | 293903.2 | 5079885.1 | 4.9662 | Worker | 0.020163 | 293903.2_5079885.1
B61_G04C | 293903.2 | 5079885.1 | 4.8662 | Worker | 0.019757 | 293903.2_5079885.1
B52_G05C | 293903.2 | 5079885.1 | 4.8565 | Worker | 0.019717 | 293903.2_5079885.1
B04_G14B | 293903.2 | 5079885.1 | 4.3534 | Worker | 0.019678 | 293903.2_5079885.1
B61_G01B | 293903.2 | 5079885.1 | 4.8238 | Worker | 0.019585 | 293903.2_5079885.1
B04_G14A | 293903.2 | 5079885.1 | 4.2308 | Worker | 0.019123 | 293903.2_5079885.1
B04_G13B | 293903.2 | 5079885.1 | 3.9889 | Worker | 0.01803 | 293903.2_5079885.1
B04_G16A | 293903.2 | 5079885.1 | 4.4175 | Worker | 0.017935 | 293903.2_5079885.1
B55_G06A | 293903.2 | 5079885.1 | 4.2666 | Worker | 0.017322 | 293903.2_5079885.1
B52_G05A | 293903.2 | 5079885.1 | 3.9075 | Worker | 0.015864 | 293903.2_5079885.1
P04_GEN4 | 293903.2 | 5079885.1 | 8.9271 | Worker | 0.015622 | 293903.2_5079885.1
B04_G13A | 293903.2 | 5079885.1 | 3.419 | Worker | 0.015454 | 293903.2_5079885.1
B58_G08A | 293903.2 | 5079885.1 | 3.3321 | Worker | 0.013528 | 293903.2_5079885.1
B04_G15C | 293903.2 | 5079885.1 | 3.3189 | Worker | 0.013475 | 293903.2_5079885.1
B58_G08B | 293903.2 | 5079885.1 | 3.2513 | Worker | 0.0132 | 293903.2_5079885.1
B58_G07A | 293903.2 | 5079885.1 | 3.2128 | Worker | 0.013044 | 293903.2_5079885.1
B58_G07B | 293903.2 | 5079885.1 | 3.1202 | Worker | 0.012668 | 293903.2_5079885.1
B58_G06A | 293903.2 | 5079885.1 | 3.0548 | Worker | 0.012402 | 293903.2_5079885.1
B58_G06B | 293903.2 | 5079885.1 | 2.9221 | Worker | 0.011864 | 293903.2_5079885.1
B58_G05A | 293903.2 | 5079885.1 | 2.8273 | Worker | 0.011479 | 293903.2_5079885.1
P04_GEN2 | 293903.2 | 5079885.1 | 5.9801 | Worker | 0.011183 | 293903.2_5079885.1
B58_G05B | 293903.2 | 5079885.1 | 2.6572 | Worker | 0.010788 | 293903.2_5079885.1
B55_G07A | 293903.2 | 5079885.1 | 2.6488 | Worker | 0.010754 | 293903.2_5079885.1
B58_G05C | 293903.2 | 5079885.1 | 2.5178 | Worker | 0.010222 | 293903.2_5079885.1
B55_G07B | 293903.2 | 5079885.1 | 2.5111 | Worker | 0.010195 | 293903.2_5079885.1
B58_G04C | 293903.2 | 5079885.1 | 1.8164 | Worker | 0.0073744 | 293903.2_5079885.1
B58_G04A | 293903.2 | 5079885.1 | 1.7362 | Worker | 0.007049 | 293903.2_5079885.1
B61_G05C | 293903.2 | 5079885.1 | 1.7085 | Worker | 0.0069367 | 293903.2_5079885.1
B58_G04B | 293903.2 | 5079885.1 | 1.6051 | Worker | 0.0065166 | 293903.2_5079885.1
B61_G05B | 293903.2 | 5079885.1 | 1.5884 | Worker | 0.0064489 | 293903.2_5079885.1
B58_G03A | 293903.2 | 5079885.1 | 1.5333 | Worker | 0.0062252 | 293903.2_5079885.1
B61_G05A | 293903.2 | 5079885.1 | 1.4643 | Worker | 0.0059451 | 293903.2_5079885.1
B61_G06B | 293903.2 | 5079885.1 | 1.4183 | Worker | 0.0057585 | 293903.2_5079885.1
B58_G03B | 293903.2 | 5079885.1 | 1.4169 | Worker | 0.0057525 | 293903.2_5079885.1
B61_G06A | 293903.2 | 5079885.1 | 1.369 | Worker | 0.0055581 | 293903.2_5079885.1
SKILODG2 | 293903.2 | 5079885.1 | 1.6532 | Worker | 0.0055546 | 293903.2_5079885.1
B61_G07B | 293903.2 | 5079885.1 | 1.3492 | Worker | 0.0054776 | 293903.2_5079885.1
B58_G02A | 293903.2 | 5079885.1 | 1.3415 | Worker | 0.0054467 | 293903.2_5079885.1
B61_G07A | 293903.2 | 5079885.1 | 1.3074 | Worker | 0.0053078 | 293903.2_5079885.1
B61_G08B | 293903.2 | 5079885.1 | 1.278 | Worker | 0.0051889 | 293903.2_5079885.1
B61_G08A | 293903.2 | 5079885.1 | 1.259 | Worker | 0.0051116 | 293903.2_5079885.1
B58_G02B | 293903.2 | 5079885.1 | 1.227 | Worker | 0.0049815 | 293903.2_5079885.1
B58_G01A | 293903.2 | 5079885.1 | 1.165 | Worker | 0.0047298 | 293903.2_5079885.1
P04_GEN1 | 293903.2 | 5079885.1 | 2.6327 | Worker | 0.0046072 | 293903.2_5079885.1
B58_G01B | 293903.2 | 5079885.1 | 1.0516 | Worker | 0.0042694 | 293903.2_5079885.1
B52_G05B | 293903.2 | 5079885.1 | 1.0272 | Worker | 0.0041705 | 293903.2_5079885.1

## ResCanF
Gen | X | Y | AveConc | EL | ResCan | Lookup
B04_G13A | 293875 | 5079550 | 1.4854 | Residential | 0.083481 | 293875_5079550
B04_G13B | 293875 | 5079550 | 1.5928 | Residential | 0.089515 | 293875_5079550
B04_G14A | 293875 | 5079550 | 1.6612 | Residential | 0.093359 | 293875_5079550
B04_G14B | 293875 | 5079550 | 1.7484 | Residential | 0.098261 | 293875_5079550
B04_G15A | 293875 | 5079550 | 1.9481 | Residential | 0.10948 | 293875_5079550
B04_G15B | 293875 | 5079550 | 1.8823 | Residential | 0.10578 | 293875_5079550
B04_G15C | 293875 | 5079550 | 1.5058 | Residential | 0.077999 | 293875_5079550
B04_G16A | 293875 | 5079550 | 1.6685 | Residential | 0.086429 | 293875_5079550
B04_G16B | 293875 | 5079550 | 1.7286 | Residential | 0.08954 | 293875_5079550
B04_G17A | 293875 | 5079550 | 2.0675 | Residential | 0.13625 | 293875_5079550
B04_G17B | 293875 | 5079550 | 2.1017 | Residential | 0.1385 | 293875_5079550
B04_G17C | 293875 | 5079550 | 2.1249 | Residential | 0.14003 | 293875_5079550
B04_G18A | 293875 | 5079550 | 1.8747 | Residential | 0.09711 | 293875_5079550
B04_G18B | 293875 | 5079550 | 1.8403 | Residential | 0.095329 | 293875_5079550
B04_G19A | 293875 | 5079550 | 1.8031 | Residential | 0.093403 | 293875_5079550
B04_G19B | 293875 | 5079550 | 1.7491 | Residential | 0.090604 | 293875_5079550
B04_G20A | 293875 | 5079550 | 1.7178 | Residential | 0.088984 | 293875_5079550
B04_G20B | 293875 | 5079550 | 1.284 | Residential | 0.066512 | 293875_5079550
B52_G01A | 293875 | 5079550 | 1.3119 | Residential | 0.067955 | 293875_5079550
B52_G01B | 293875 | 5079550 | 1.268 | Residential | 0.065681 | 293875_5079550
B52_G02A | 293875 | 5079550 | 1.3844 | Residential | 0.071711 | 293875_5079550
B52_G02B | 293875 | 5079550 | 1.3582 | Residential | 0.070356 | 293875_5079550
B52_G03A | 293875 | 5079550 | 1.4259 | Residential | 0.073859 | 293875_5079550
B52_G03B | 293875 | 5079550 | 1.4464 | Residential | 0.074922 | 293875_5079550
B52_G04A | 293875 | 5079550 | 1.4447 | Residential | 0.074838 | 293875_5079550
B52_G04B | 293875 | 5079550 | 1.4577 | Residential | 0.075508 | 293875_5079550
B52_G04C | 293875 | 5079550 | 1.3826 | Residential | 0.071618 | 293875_5079550
B52_G05A | 293875 | 5079550 | 0.97856 | Residential | 0.050689 | 293875_5079550
B52_G05B | 293875 | 5079550 | 1.2933 | Residential | 0.066992 | 293875_5079550
B52_G05C | 293875 | 5079550 | 0.94189 | Residential | 0.04879 | 293875_5079550
B52_G06A | 293875 | 5079550 | 1.7752 | Residential | 0.091953 | 293875_5079550
B52_G06B | 293875 | 5079550 | 1.5136 | Residential | 0.078403 | 293875_5079550
B52_G07A | 293875 | 5079550 | 2.2236 | Residential | 0.11518 | 293875_5079550
B52_G07B | 293875 | 5079550 | 2.3933 | Residential | 0.12398 | 293875_5079550
B52_G08A | 293875 | 5079550 | 2.652 | Residential | 0.13738 | 293875_5079550
B52_G08B | 293875 | 5079550 | 2.4661 | Residential | 0.12774 | 293875_5079550
B55_G01A | 293875 | 5079550 | 1.1041 | Residential | 0.057193 | 293875_5079550
B55_G01B | 293875 | 5079550 | 1.1031 | Residential | 0.057142 | 293875_5079550
B55_G02A | 293875 | 5079550 | 1.0973 | Residential | 0.05684 | 293875_5079550
B55_G02B | 293875 | 5079550 | 1.1114 | Residential | 0.057568 | 293875_5079550
B55_G03A | 293875 | 5079550 | 1.073 | Residential | 0.055581 | 293875_5079550
B55_G03B | 293875 | 5079550 | 1.0885 | Residential | 0.056384 | 293875_5079550
B55_G04A | 293875 | 5079550 | 1.041 | Residential | 0.053924 | 293875_5079550
B55_G04B | 293875 | 5079550 | 1.0608 | Residential | 0.05495 | 293875_5079550
B55_G04C | 293875 | 5079550 | 1.0257 | Residential | 0.053133 | 293875_5079550
B55_G05A | 293875 | 5079550 | 0.90044 | Residential | 0.046643 | 293875_5079550
B55_G05B | 293875 | 5079550 | 0.92723 | Residential | 0.048031 | 293875_5079550
B55_G05C | 293875 | 5079550 | 0.94143 | Residential | 0.048766 | 293875_5079550
B55_G06A | 293875 | 5079550 | 0.84166 | Residential | 0.043598 | 293875_5079550
B55_G06B | 293875 | 5079550 | 0.88126 | Residential | 0.045649 | 293875_5079550
B55_G07A | 293875 | 5079550 | 0.74362 | Residential | 0.038519 | 293875_5079550
B55_G07B | 293875 | 5079550 | 0.79232 | Residential | 0.041042 | 293875_5079550
B58_G01A | 293875 | 5079550 | 0.44614 | Residential | 0.02311 | 293875_5079550
B58_G01B | 293875 | 5079550 | 0.41919 | Residential | 0.021714 | 293875_5079550
B58_G02A | 293875 | 5079550 | 0.47796 | Residential | 0.024759 | 293875_5079550
B58_G02B | 293875 | 5079550 | 0.45839 | Residential | 0.023745 | 293875_5079550
B58_G03A | 293875 | 5079550 | 0.50828 | Residential | 0.026329 | 293875_5079550
B58_G03B | 293875 | 5079550 | 0.48957 | Residential | 0.02536 | 293875_5079550
B58_G04A | 293875 | 5079550 | 0.53729 | Residential | 0.027832 | 293875_5079550
B58_G04B | 293875 | 5079550 | 0.51973 | Residential | 0.026922 | 293875_5079550
B58_G04C | 293875 | 5079550 | 0.548 | Residential | 0.028387 | 293875_5079550
B58_G05A | 293875 | 5079550 | 0.63518 | Residential | 0.032902 | 293875_5079550
B58_G05B | 293875 | 5079550 | 0.62318 | Residential | 0.032281 | 293875_5079550
B58_G05C | 293875 | 5079550 | 0.61329 | Residential | 0.031769 | 293875_5079550
B58_G06A | 293875 | 5079550 | 0.65483 | Residential | 0.03392 | 293875_5079550
B58_G06B | 293875 | 5079550 | 0.6425 | Residential | 0.033282 | 293875_5079550
B58_G07A | 293875 | 5079550 | 0.67402 | Residential | 0.034914 | 293875_5079550
B58_G07B | 293875 | 5079550 | 0.6623 | Residential | 0.034307 | 293875_5079550
B58_G08A | 293875 | 5079550 | 0.69119 | Residential | 0.035803 | 293875_5079550
B58_G08B | 293875 | 5079550 | 0.68114 | Residential | 0.035283 | 293875_5079550
B61_G01A | 293875 | 5079550 | 0.45895 | Residential | 0.023773 | 293875_5079550
B61_G01B | 293875 | 5079550 | 0.3823 | Residential | 0.019803 | 293875_5079550
B61_G02A | 293875 | 5079550 | 0.5436 | Residential | 0.028158 | 293875_5079550
B61_G02B | 293875 | 5079550 | 0.49308 | Residential | 0.025542 | 293875_5079550
B61_G03A | 293875 | 5079550 | 0.61559 | Residential | 0.031888 | 293875_5079550
B61_G03B | 293875 | 5079550 | 0.57304 | Residential | 0.029684 | 293875_5079550
B61_G04A | 293875 | 5079550 | 0.70078 | Residential | 0.0363 | 293875_5079550
B61_G04B | 293875 | 5079550 | 0.62865 | Residential | 0.032564 | 293875_5079550
B61_G04C | 293875 | 5079550 | 0.70012 | Residential | 0.036266 | 293875_5079550
B61_G05A | 293875 | 5079550 | 0.61695 | Residential | 0.031958 | 293875_5079550
B61_G05B | 293875 | 5079550 | 0.63317 | Residential | 0.032798 | 293875_5079550
B61_G05C | 293875 | 5079550 | 0.64229 | Residential | 0.03327 | 293875_5079550
B61_G06A | 293875 | 5079550 | 0.58941 | Residential | 0.030531 | 293875_5079550
B61_G06B | 293875 | 5079550 | 0.60687 | Residential | 0.031436 | 293875_5079550
B61_G07A | 293875 | 5079550 | 0.55512 | Residential | 0.028755 | 293875_5079550
B61_G07B | 293875 | 5079550 | 0.57896 | Residential | 0.02999 | 293875_5079550
B61_G08A | 293875 | 5079550 | 0.21102 | Residential | 0.010931 | 293875_5079550
B61_G08B | 293875 | 5079550 | 0.54061 | Residential | 0.028004 | 293875_5079550
P04_GEN1 | 293875 | 5079550 | 0.79044 | Residential | 0.017153 | 293875_5079550
P04_GEN2 | 293875 | 5079550 | 0.63876 | Residential | 0.014819 | 293875_5079550
P04_GEN3 | 293875 | 5079550 | 0.96528 | Residential | 0.022395 | 293875_5079550
P04_GEN4 | 293875 | 5079550 | 0.62818 | Residential | 0.013631 | 293875_5079550
P04_GEN5 | 293875 | 5079550 | 1.0712 | Residential | 0.024853 | 293875_5079550
P04_GEN6 | 293875 | 5079550 | 0.57315 | Residential | 0.012437 | 293875_5079550
P04_GENC | 293875 | 5079550 | 0.51313 | Residential | 0.014932 | 293875_5079550
SKILODG1 | 293875 | 5079550 | 3.6829 | Residential | 0.68869 | 293875_5079550
SKILODG2 | 293875 | 5079550 | 1.5227 | Residential | 0.063497 | 293875_5079550
PORTABLE | 293875 | 5079550 | 1.3306 | Residential | 0.06906 | 293875_5079550

## AcuteF
Gen | X | Y | 24hr_Conc | AcuteRisk | EL | Lookup
P04_GENC | 293903.2 | 5079885.1 | 796.85 | 0.62632 | Acute | 293903.2_5079885.1
B55_G01A | 293903.2 | 5079885.1 | 167.58 | 0.23629 | Acute | 293903.2_5079885.1
B55_G02B | 293903.2 | 5079885.1 | 121.201 | 0.17089 | Acute | 293903.2_5079885.1
B52_G07A | 293903.2 | 5079885.1 | 111.676 | 0.15746 | Acute | 293903.2_5079885.1
B55_G02A | 293903.2 | 5079885.1 | 108.504 | 0.15299 | Acute | 293903.2_5079885.1
B52_G06A | 293903.2 | 5079885.1 | 106.785 | 0.15057 | Acute | 293903.2_5079885.1
B55_G03B | 293903.2 | 5079885.1 | 106.036 | 0.14951 | Acute | 293903.2_5079885.1
P04_GEN4 | 293903.2 | 5079885.1 | 230.094 | 0.13484 | Acute | 293903.2_5079885.1
B52_G07B | 293903.2 | 5079885.1 | 94.0552 | 0.13262 | Acute | 293903.2_5079885.1
B52_G06B | 293903.2 | 5079885.1 | 93.4264 | 0.13173 | Acute | 293903.2_5079885.1
B55_G03A | 293903.2 | 5079885.1 | 92.0464 | 0.12979 | Acute | 293903.2_5079885.1
B04_G17C | 293903.2 | 5079885.1 | 65.5857 | 0.11674 | Acute | 293903.2_5079885.1
B55_G04B | 293903.2 | 5079885.1 | 82.1634 | 0.11585 | Acute | 293903.2_5079885.1
P04_GEN6 | 293903.2 | 5079885.1 | 191.28 | 0.11209 | Acute | 293903.2_5079885.1
B04_G17B | 293903.2 | 5079885.1 | 62.5288 | 0.1113 | Acute | 293903.2_5079885.1
B04_G17A | 293903.2 | 5079885.1 | 56.89 | 0.10126 | Acute | 293903.2_5079885.1
B55_G04A | 293903.2 | 5079885.1 | 66.8177 | 0.094213 | Acute | 293903.2_5079885.1
B52_G08B | 293903.2 | 5079885.1 | 61.6777 | 0.086966 | Acute | 293903.2_5079885.1
B04_G18B | 293903.2 | 5079885.1 | 58.3333 | 0.08225 | Acute | 293903.2_5079885.1
B55_G04C | 293903.2 | 5079885.1 | 58.0196 | 0.081808 | Acute | 293903.2_5079885.1
B04_G19A | 293903.2 | 5079885.1 | 57.7956 | 0.081492 | Acute | 293903.2_5079885.1
B55_G01B | 293903.2 | 5079885.1 | 57.7844 | 0.081476 | Acute | 293903.2_5079885.1
B04_G19B | 293903.2 | 5079885.1 | 57.3905 | 0.080921 | Acute | 293903.2_5079885.1
B04_G18A | 293903.2 | 5079885.1 | 56.6122 | 0.079823 | Acute | 293903.2_5079885.1
P04_GEN2 | 293903.2 | 5079885.1 | 126.578 | 0.079364 | Acute | 293903.2_5079885.1
B04_G20A | 293903.2 | 5079885.1 | 54.6612 | 0.077072 | Acute | 293903.2_5079885.1
B52_G08A | 293903.2 | 5079885.1 | 52.8957 | 0.074583 | Acute | 293903.2_5079885.1
P04_GEN3 | 293903.2 | 5079885.1 | 111.636 | 0.069996 | Acute | 293903.2_5079885.1
B04_G13B | 293903.2 | 5079885.1 | 44.1482 | 0.067105 | Acute | 293903.2_5079885.1
B04_G14A | 293903.2 | 5079885.1 | 41.6743 | 0.063345 | Acute | 293903.2_5079885.1
B52_G01B | 293903.2 | 5079885.1 | 44.1218 | 0.062212 | Acute | 293903.2_5079885.1
B04_G20B | 293903.2 | 5079885.1 | 43.7423 | 0.061677 | Acute | 293903.2_5079885.1
B52_G01A | 293903.2 | 5079885.1 | 42.6771 | 0.060175 | Acute | 293903.2_5079885.1
B04_G15A | 293903.2 | 5079885.1 | 39.1928 | 0.059573 | Acute | 293903.2_5079885.1
B04_G13A | 293903.2 | 5079885.1 | 38.4594 | 0.058458 | Acute | 293903.2_5079885.1
B04_G15B | 293903.2 | 5079885.1 | 38.3151 | 0.058239 | Acute | 293903.2_5079885.1
SKILODG1 | 293903.2 | 5079885.1 | 99.1232 | 0.058086 | Acute | 293903.2_5079885.1
P04_GEN5 | 293903.2 | 5079885.1 | 91.8091 | 0.057564 | Acute | 293903.2_5079885.1
B04_G14B | 293903.2 | 5079885.1 | 35.3946 | 0.0538 | Acute | 293903.2_5079885.1
B52_G02B | 293903.2 | 5079885.1 | 37.8725 | 0.0534 | Acute | 293903.2_5079885.1
P04_GEN1 | 293903.2 | 5079885.1 | 87.5228 | 0.051288 | Acute | 293903.2_5079885.1
PORTABLE | 293903.2 | 5079885.1 | 35.1192 | 0.049167 | Acute | 293903.2_5079885.1
B52_G02A | 293903.2 | 5079885.1 | 34.0884 | 0.048065 | Acute | 293903.2_5079885.1
B61_G04A | 293903.2 | 5079885.1 | 32.6062 | 0.045975 | Acute | 293903.2_5079885.1
B04_G16A | 293903.2 | 5079885.1 | 32.5545 | 0.045902 | Acute | 293903.2_5079885.1
B55_G05C | 293903.2 | 5079885.1 | 32.2369 | 0.045454 | Acute | 293903.2_5079885.1
B04_G16B | 293903.2 | 5079885.1 | 30.0756 | 0.042407 | Acute | 293903.2_5079885.1
B55_G05B | 293903.2 | 5079885.1 | 29.7517 | 0.04195 | Acute | 293903.2_5079885.1
B52_G03A | 293903.2 | 5079885.1 | 29.706 | 0.041885 | Acute | 293903.2_5079885.1
B52_G04B | 293903.2 | 5079885.1 | 29.6658 | 0.041829 | Acute | 293903.2_5079885.1
B52_G04A | 293903.2 | 5079885.1 | 29.2509 | 0.041244 | Acute | 293903.2_5079885.1
B52_G03B | 293903.2 | 5079885.1 | 28.9919 | 0.040879 | Acute | 293903.2_5079885.1
B52_G04C | 293903.2 | 5079885.1 | 28.0348 | 0.039529 | Acute | 293903.2_5079885.1
B55_G05A | 293903.2 | 5079885.1 | 27.7918 | 0.039186 | Acute | 293903.2_5079885.1
B04_G15C | 293903.2 | 5079885.1 | 27.6516 | 0.038989 | Acute | 293903.2_5079885.1
B52_G05C | 293903.2 | 5079885.1 | 27.3313 | 0.038537 | Acute | 293903.2_5079885.1
B61_G04C | 293903.2 | 5079885.1 | 27.1748 | 0.038316 | Acute | 293903.2_5079885.1
B61_G04B | 293903.2 | 5079885.1 | 26.7141 | 0.037667 | Acute | 293903.2_5079885.1
B61_G03A | 293903.2 | 5079885.1 | 26.4909 | 0.037352 | Acute | 293903.2_5079885.1
B52_G05A | 293903.2 | 5079885.1 | 26.4746 | 0.037329 | Acute | 293903.2_5079885.1
B55_G06B | 293903.2 | 5079885.1 | 26.3587 | 0.037166 | Acute | 293903.2_5079885.1
B61_G03B | 293903.2 | 5079885.1 | 26.214 | 0.036962 | Acute | 293903.2_5079885.1
B61_G02A | 293903.2 | 5079885.1 | 25.0953 | 0.035384 | Acute | 293903.2_5079885.1
B61_G02B | 293903.2 | 5079885.1 | 22.2306 | 0.031345 | Acute | 293903.2_5079885.1
B61_G01A | 293903.2 | 5079885.1 | 21.0464 | 0.029675 | Acute | 293903.2_5079885.1
B58_G02A | 293903.2 | 5079885.1 | 20.5963 | 0.029041 | Acute | 293903.2_5079885.1
B61_G01B | 293903.2 | 5079885.1 | 20.3229 | 0.028655 | Acute | 293903.2_5079885.1
B58_G03B | 293903.2 | 5079885.1 | 20.3176 | 0.028648 | Acute | 293903.2_5079885.1
B58_G05B | 293903.2 | 5079885.1 | 20.2658 | 0.028575 | Acute | 293903.2_5079885.1
B55_G06A | 293903.2 | 5079885.1 | 20.2128 | 0.0285 | Acute | 293903.2_5079885.1
B58_G05C | 293903.2 | 5079885.1 | 20.1788 | 0.028452 | Acute | 293903.2_5079885.1
B58_G08A | 293903.2 | 5079885.1 | 19.9696 | 0.028157 | Acute | 293903.2_5079885.1
B58_G02B | 293903.2 | 5079885.1 | 19.6946 | 0.027769 | Acute | 293903.2_5079885.1
B58_G05A | 293903.2 | 5079885.1 | 19.6519 | 0.027709 | Acute | 293903.2_5079885.1
B58_G03A | 293903.2 | 5079885.1 | 18.9388 | 0.026704 | Acute | 293903.2_5079885.1
B58_G06B | 293903.2 | 5079885.1 | 18.9358 | 0.026699 | Acute | 293903.2_5079885.1
B58_G08B | 293903.2 | 5079885.1 | 18.7959 | 0.026502 | Acute | 293903.2_5079885.1
B58_G04B | 293903.2 | 5079885.1 | 18.1198 | 0.025549 | Acute | 293903.2_5079885.1
B58_G07A | 293903.2 | 5079885.1 | 18.0037 | 0.025385 | Acute | 293903.2_5079885.1
B55_G07A | 293903.2 | 5079885.1 | 17.5836 | 0.024793 | Acute | 293903.2_5079885.1
B58_G06A | 293903.2 | 5079885.1 | 17.4452 | 0.024598 | Acute | 293903.2_5079885.1
B58_G01A | 293903.2 | 5079885.1 | 17.2498 | 0.024322 | Acute | 293903.2_5079885.1
B58_G07B | 293903.2 | 5079885.1 | 17.2223 | 0.024283 | Acute | 293903.2_5079885.1
B58_G04A | 293903.2 | 5079885.1 | 17.0543 | 0.024047 | Acute | 293903.2_5079885.1
B58_G04C | 293903.2 | 5079885.1 | 16.7795 | 0.023659 | Acute | 293903.2_5079885.1
B58_G01B | 293903.2 | 5079885.1 | 15.0226 | 0.021182 | Acute | 293903.2_5079885.1
B61_G05C | 293903.2 | 5079885.1 | 14.6498 | 0.020656 | Acute | 293903.2_5079885.1
B61_G07B | 293903.2 | 5079885.1 | 14.3148 | 0.020184 | Acute | 293903.2_5079885.1
B61_G06A | 293903.2 | 5079885.1 | 13.8041 | 0.019464 | Acute | 293903.2_5079885.1
B61_G07A | 293903.2 | 5079885.1 | 13.6048 | 0.019183 | Acute | 293903.2_5079885.1
B61_G05B | 293903.2 | 5079885.1 | 13.5985 | 0.019174 | Acute | 293903.2_5079885.1
B61_G05A | 293903.2 | 5079885.1 | 13.1774 | 0.01858 | Acute | 293903.2_5079885.1
SKILODG2 | 293903.2 | 5079885.1 | 15.9611 | 0.018036 | Acute | 293903.2_5079885.1
B61_G08B | 293903.2 | 5079885.1 | 12.6861 | 0.017887 | Acute | 293903.2_5079885.1
B55_G07B | 293903.2 | 5079885.1 | 12.4545 | 0.017561 | Acute | 293903.2_5079885.1
B61_G06B | 293903.2 | 5079885.1 | 12.2737 | 0.017306 | Acute | 293903.2_5079885.1
B61_G08A | 293903.2 | 5079885.1 | 11.8724 | 0.01674 | Acute | 293903.2_5079885.1
B52_G05B | 293903.2 | 5079885.1 | 11.4287 | 0.016114 | Acute | 293903.2_5079885.1

## Final Residential Risk
2
Generator Ranking and Risk Calculation - Residential Risk
Generator Rank | Generator ID | Modeled Concentration | Generator Non-Cancer REER | Generator Cancer Risk | Generator Non-Cancer Risk
|  | (μg/m3) | (g/s per μg/m3) |  |  | Reference
1 | SKILODG1 | 3.6829 | 0.0038542 | 0.68869 | 0.014194 | Type H
2 | B04_G17C | 2.1249 | 0.0016484 | 0.14003 | 0.0035027 | Type G
3 | B04_G17B | 2.1017 | 0.0016484 | 0.1385 | 0.0034645 | Type G
4 | B52_G08A | 2.652 | 0.0012462 | 0.13738 | 0.003305 | Type F
1Maximum project emissions are determined by multiplying the emission factor by the projected fuel throughput. Total annual fuel throughput for the facility is determined to ensure that facility wide emissions are less than ODEQ generic plant site emission limits. To develop a conservative model and ensure worst-case risks are represented for Cleaner Air Oregon, the site-wide annual fuel throughput is allocated to the worst-case individual generators based on the screening model results. Units are ranked by the highest contributing risk to the maximum exposure location using the modeled concentrations in a 1 g/s model and scaled for each unit at each receptor by the chronic cancer REER for each exposure type. In the case of this model, SKILODG1, B04_G17C, and B04_G17B have a higher contribution than the the worst-case 2,500 kW main generator (B52_G08A). Therefore, the SKILODG1, B04_G17C, and B04_G17B generators are assumed to have 100 hours of fuel throughput at 100% load (for compliance with requirements in 40 CFR Subpart 60). The remainder of the total proposed facility-wide fuel throughput is assumed to go to B52_G08A, for conservatism. Emissions from the remaining generators are not included in the final model because the screening model indicates B52_G08A will have a higher contribution to modeled risk.
Reference
2Estimated fuel throughput for each generator type based on 100 hours of operation per year at 100% load for one generator. | [5 empty] | Type A
CAT 27 - 750 kW | 5360 | gallons/yr/engine |  |  |  | Type B
CAT 27 - 800 kW | 5730 | gallons/yr/engine |  |  |  | Type C
CAT 32 - 1000 kW | 7190 | gallons/yr/engine |  |  |  | Type D
CAT 3516C Trans - 1825 kW | 12840 | gallons/yr/engine |  |  |  | Type E
CAT 3516C - 2000 kW | 13890 | gallons/yr/engine |  |  |  | Type F
CAT 3516C - 2500 kW | 17350 | gallons/yr/engine |  |  |  | Type G
MTU 2250 - 2250 kW | 16300 | gallons/yr/engine |  |  |  | Type H
CAT C18 - 750 kW | 5360 | gallons/yr/engine |  |  |  | Type I
CAT 3512C - 1500 kW | 10320 | gallons/yr/engine
Final Risk Determination - Residential Risk
Generator ID | Fuel Used (gal)
Facility Wide Annual Fuel Limit | 269504 |  | Maximum Exposure Location, UTM Easting (m) |  | 293875
SKILODG1 | 5360 |  | Maximum Exposure Location, UTM Northing (m) |  | 5079550
B04_G17C | 16300 |  | Calculated Facility Risk - Residential Cancer Risk |  | 2.8006
B04_G17B | 16300 |  | Calculated Facility Risk - Residential Non-Cancer Risk |  | 0.065268
B52_G08A | 231544
Main Gen Fuel Ratio | 13.3455

## Final Child Risk
4
Generator Ranking and Risk Calculation - Child Risk
Generator Rank | Generator ID | Modeled Concentration | Generator Non-Cancer REER | Generator Cancer Risk | Generator Non-Cancer Risk
|  | (μg/m3) | (g/s per μg/m3) |  |  |  |  | Reference
1 | SKILODG1 | 0.20622 | 0.00085619 | 0.0014827 | 0.00017657 | 1 | 1 | Type H
2 | PORTABLE | 0.083465 | 0.00024779 | 0.00016359 | 2.0682e-05 | 2 | 3 | Type D
3 | P04_GEN2 | 0.18709 | 0.00011058 | 0.00016352 | 2.0688e-05 | 3 | 2 | Type B
4 | P04_GEN4 | 0.19703 | 0.00010344 | 0.00016117 | 2.0381e-05 | 4 | 4 | Type A
5 | P04_GEN6 | 0.19597 | 0.00010344 | 0.0001603 | 2.0271e-05 | 5 | 5 | Type A
6 | P04_GEN5 | 0.17782 | 0.00011058 | 0.00015541 | 1.9663e-05 | 6 | 6 | Type B
7 | P04_GEN3 | 0.17703 | 0.00011058 | 0.00015472 | 1.9576e-05 | 7 | 7 | Type B
8 | P04_GEN1 | 0.18714 | 0.00010344 | 0.00015308 | 1.9357e-05 | 8 | 8 | Type A
9 | P04_GENC | 0.13777 | 0.00013875 | 0.00015155 | 1.9116e-05 | 9 | 9 | Type C
10 | B04_G15A | 0.067491 | 0.00026805 | 0.00014308 | 1.8091e-05 | 10 | 10 | Type E
11 | B04_G15B | 0.067371 | 0.00026805 | 0.00014283 | 1.8059e-05 | 11 | 11 | Type E
12 | B04_G14B | 0.067178 | 0.00026805 | 0.00014242 | 1.8007e-05 | 12 | 12 | Type E
13 | B04_G14A | 0.067076 | 0.00026805 | 0.0001422 | 1.798e-05 | 13 | 13 | Type E
14 | B04_G13B | 0.067006 | 0.00026805 | 0.00014205 | 1.7961e-05 | 14 | 14 | Type E
15 | B04_G13A | 0.066933 | 0.00026805 | 0.0001419 | 1.7941e-05 | 15 | 15 | Type E
16 | B04_G17C | 0.049727 | 0.00031456 | 0.00012382 | 1.5642e-05 | 16 | 16 | Type G
17 | B04_G17B | 0.049665 | 0.00031456 | 0.00012367 | 1.5623e-05 | 17 | 17 | Type G
18 | B04_G17A | 0.049587 | 0.00031456 | 0.00012347 | 1.5598e-05 | 18 | 18 | Type G
19 | SKILODG2 | 0.074886 | 0.00019916 | 0.00011757 | 1.4914e-05 | 19 | 19 | Type I
20 | B52_G08A | 0.050165 | 0.00023854 | 0.00010083 | 1.1967e-05 | 20 | 20 | Type F
1Maximum project emissions are determined by multiplying the emission factor by the projected fuel throughput. Total annual fuel throughput for the facility is determined to ensure that facility wide emissions are less than ODEQ generic plant site emission limits. To develop a conservative model and ensure worst-case risks are represented for Cleaner Air Oregon, the site-wide annual fuel throughput is allocated to the worst-case individual generators based on the screening model results. Units are ranked by the highest contributing risk to the maximum exposure location using the modeled concentrations in a 1 g/s model and scaled for each unit at each receptor by the chronic cancer REER for each exposure type. In the case of this model, 19 generators have a higher risk contribution than the worst-case 2,500 kW main generator (B52_G08B). Therefore, each of those 19 generators are assumed to have 100 hours of fuel throughput at 100% load (for compliance with requirements in 40 CFR Subpart 60). The remainder of the total proposed facility-wide fuel throughput is assumed to go to B52_G08B for conservatism. Emissions from the remaining generators are not included in the final model because the screening model indicates B52_G08B will have a higher contribution to modeled risk.
2Estimated fuel throughput for each generator type based on 100 hours of operation per year at 100% load for one generator. | [7 empty] | Reference
CAT 27 - 750 kW | 5360 | gallons/yr/engine | [5 empty] | Type A
CAT 27 - 800 kW | 5730 | gallons/yr/engine | [5 empty] | Type B
CAT 32 - 1000 kW | 7190 | gallons/yr/engine | [5 empty] | Type C
CAT 3516C Trans - 1825 kW | 12840 | gallons/yr/engine | [5 empty] | Type D
CAT 3516C - 2000 kW | 13890 | gallons/yr/engine | [5 empty] | Type E
CAT 3516C - 2500 kW | 17350 | gallons/yr/engine | [5 empty] | Type F
MTU 2250 - 2250 kW | 16300 | gallons/yr/engine | [5 empty] | Type G
CAT C18 - 750 kW | 5360 | gallons/yr/engine | [5 empty] | Type H
CAT 3512C - 1500 kW | 10320 | gallons/yr/engine | [5 empty] | Type I
Final Risk Determination - Child Risk
Generator ID | Fuel Used (gal)
Facility Wide Annual Fuel Limit | 269504
SKILODG1 | 5360
PORTABLE | 12840
P04_GEN2 | 5730
P04_GEN4 | 5360
P04_GEN6 | 5360
P04_GEN5 | 5730
P04_GEN3 | 5730
P04_GEN1 | 5360
P04_GENC | 7190
B04_G15A | 13890
B04_G15B | 13890
B04_G14B | 13890
B04_G14A | 13890
B04_G13B | 13890
B04_G13A | 13890
B04_G17C | 16300
B04_G17B | 16300
B04_G17A | 16300 |  | Maximum Exposure Location, UTM Easting (m) |  | 291600
SKILODG2 | 10320 |  | Maximum Exposure Location, UTM Northing (m) |  | 5080100
B52_G08A | 68284 |  | Calculated Facility Risk - Child Cancer Risk |  | 0.0044859
Main Gen Fuel Ratio | 3.9357 |  | Calculated Facility Risk - Child Non-Cancer Risk |  | 0.00055321

## Final Worker Risk
6
Generator Ranking and Risk Calculation - Worker Risk
Generator Rank | Generator ID | Modeled Concentration | Generator Non-Cancer REER | Generator Cancer Risk | Generator Non-Cancer Risk
|  | (μg/m3) | (g/s per μg/m3) |  |  | Reference
1 | SKILODG1 | 11.8263 | 0.00085619 | 0.18331 | 0.010126 | Type H
2 | P04_GENC | 44.9688 | 0.00013875 | 0.10523 | 0.0062396 | Type C
3 | B55_G02A | 21.1522 | 0.00023854 | 0.085878 | 0.0050457 | Type F
1Maximum project emissions are determined by multiplying the emission factor by the projected fuel throughput. Total annual fuel throughput for the facility is determined to ensure that facility wide emissions are less than ODEQ generic plant site emission limits. To develop a conservative model and ensure worst-case risks are represented for Cleaner Air Oregon, the site-wide annual fuel throughput is allocated to the worst-case individual generators based on the screening model results. Units are ranked by the highest contributing risk to the maximum exposure location using the modeled concentrations in a 1 g/s model and scaled for each unit at each receptor by the chronic cancer REER for each exposure type. In the case of this model, SKILODG1 has a higher contribution has a higher risk contribution than the worst-case 2,500 kW main generator (B55_G02A). Therefore, SKILODG1 generator is assumed to have 100 hours of fuel throughput at 100% load (for compliance with requirements in 40 CFR Subpart 60). The remainder of the total proposed facility-wide fuel throughput is assumed to go to B55_G02A, for conservatism. Emissions from the remaining generators are not included in the final model because the screening model indicates B55_G02A will have a higher contribution to modeled risk.
2Estimated fuel throughput for each generator type based on 100 hours of operation per year at 100% load for one generator. | [5 empty] | Reference
CAT 27 - 750 kW | 5360 | gallons/yr/engine |  |  |  | Type A
CAT 27 - 800 kW | 5730 | gallons/yr/engine |  |  |  | Type B
CAT 32 - 1000 kW | 7190 | gallons/yr/engine |  |  |  | Type C
CAT 3516C Trans - 1825 kW | 12840 | gallons/yr/engine |  |  |  | Type D
CAT 3516C - 2000 kW | 13890 | gallons/yr/engine |  |  |  | Type E
CAT 3516C - 2500 kW | 17350 | gallons/yr/engine |  |  |  | Type F
MTU 2250 - 2250 kW | 16300 | gallons/yr/engine |  |  |  | Type G
CAT C18 - 750 kW | 5360 | gallons/yr/engine |  |  |  | Type H
CAT 3512C - 1500 kW | 10320 | gallons/yr/engine |  |  |  | Type I
Final Risk Determination - Worker Risk
Generator ID | Fuel Used (gal)
Facility Wide Annual Fuel Limit | 269504 |  | Maximum Exposure Location, UTM Easting (m) |  | 293903.2
SKILODG1 | 5360 |  | Maximum Exposure Location, UTM Northing (m) |  | 5079885.1
P04_GENC | 7190 |  | Calculated Facility Risk - Worker Cancer Risk |  | 1.5604
B55_G02A | 256954 |  | Calculated Facility Risk - Worker Non-Cancer Risk |  | 0.091092
Main Gen Fuel Ratio | 14.81

## Final Acute Risk
Generator Ranking and Risk Determination - Acute Risk
Generator Rank | Generator ID | Generator Non-Cancer Risk | Fuel Used (gal)
Reference
1 | P04_GENC | 0.62632 | 1725.6 | Type C
2 | B55_G01A | 0.23629 | 4164 | Type F
3 | B55_G02B | 0.17089 | 4164 | Type F
4 | B52_G07A | 0.15746 | 4164 | Type F
5 | B55_G02A | 0.15299 | 4164 | Type F
6 | B52_G06A | 0.15057 | 1618.4 | Type F
Facility Wide Daily Fuel Limit |  |  | 20000
1Maximum project emissions are determined by multiplying the emission factor by the projected fuel throughput. To develop a conservative model and ensure worst-case risks are represented for Cleaner Air Oregon, the site-wide 24-hr fuel throughput is allocated to the worst-case individual generators based on the screening model results. Units are ranked by the highest contributing risk to the maximum exposure location using the modeled concentrations in a 1 g/s model and scaled for each unit at each receptor by the acute non-cancer REER. In the case of this model, auxiliary generators P04_GENC, has a higher risk contributions than the worst-case main generator, B55_G01A. The next highest risk contributors are all main generators (B55_G02B, B52_G07A, B52_G07A, B55_G02A, and B52_G06A). All modeled units are assumed to operate for 24 hours per day with the exception of B52_G06A, which has a fuel throughput of 1,834 gallons to meet the proposed site-wide daily fuel limit of 20,000 gallons/day.
2Estimated fuel throughput for each generator type based on 24 hours of operation per year at 100% load for one generator.
Reference
CAT 27 - 750 kW | 1286.4 | gallons/yr/engine |  | Type A
CAT 27 - 800 kW | 1375.2 | gallons/yr/engine |  | Type B
CAT 32 - 1000 kW | 1725.6 | gallons/yr/engine |  | Type C
CAT 3516C Trans - 1825 kW | 3081.6 | gallons/yr/engine |  | Type D
CAT 3516C - 2000 kW | 3333.6 | gallons/yr/engine |  | Type E
CAT 3516C - 2500 kW | 4164 | gallons/yr/engine |  | Type F
MTU 2250 - 2250 kW | 3912 | gallons/yr/engine |  | Type G
CAT C18 - 750 kW | 1286.4 | gallons/yr/engine |  | Type H
CAT 3512C - 1500 kW | 2476.8 | gallons/yr/engine |  | Type I
Maximum Exposure Location, UTM Easting (m) |  | 293903.2
Maximum Exposure Location, UTM Northing (m) |  | 5079885.1
Calculated Facility Risk - Acute Non-Cancer Risk |  | 1.4025

## Risk Summary
Table H-5. Risk Summary
| Residential Cancer Risk | Residential Non-Cancer Risk | Child Cancer Risk | Child Non-Cancer Risk | Worker Cancer Risk | Worker Non-Cancer Risk | Acute Non-Cancer Risk
2024 G2 CAO Call-in - Total Facility Calculated Risk | 2.8 | <0.1 | <0.1 | <0.1 | 1.6 | <0.1 | 1.4
Existing Facility Permit Level | 5 | 0.5 | 5 | 0.5 | 5 | 0.5 | 0.5
Permit Required? | No | No | No | No | No | No | Yes
Existing Facility Community Engagement Level | 25 | 1 | 25 | 1 | 25 | 1 | 1
Community Engagement Required? | No | No | No | No | No | No | No
Existing Facility TBACT Level | 50 | 3 | 50 | 3 | 50 | 3 | 3
TBACT Required? | No | No | No | No | No | No | No
1. Risk Action Levels (RALs) from OAR 340-245-8010 Table 1.
2Calculated risk is rounded to one decimal place for comparison to the source permit level and to the nearest whole number when comparing to other RALs as per OAR 340-245-0200(4).
3Pollutants included in this evaluation have a non-cancer class of either HI3 or HI5. For conservatism, all pollutants are treated as HI3 and compared to the non-cancer TBACT RAL of 3 as per OAR 340-245-0200(3).

## Model Results Summary - PDX109 (hidden)
v0.4 models
Table R-1. Maximum Concentrations by Source Group, 24-hr Averaging Period
|  |  | Maximum Concentration1 (µg/m3) |  |  |  |  | Overall Maximum
| Source Group |  | 2013 | 2014 | 2015 | 2016 | 2017
| Combined Emissions |  | 3205.4641 | 2631.6328 | 2701.8009 | 2503.4236 | 2935.6928 | 3205.4641
| 2500 kW Generators |  | 3019.2683 | 2436.4835 | 2489.0207 | 2334.0862 | 2625.887 | 3019.2683
| 1825 kW Generator |  | 251.069 | 186.483 | 201.3113 | 210.0164 | 209.7767 | 251.069
|  | 600 kW Generator | 296.2468 | 195.5374 | 191.7076 | 176.1579 | 212.1882 | 296.2468
|  | 750 kW Generator | 195.8888 | 194.0052 | 223.4244 | 283.0168 | 254.1944 | 283.0168
|  | 100 kW Generator | 1056.2767 | 949.5049 | 607.9347 | 1106.1559 | 798.8296 | 1106.1559
| Fire Pumps |  | 782.7824 | 936.369 | 878.548 | 787.0068 | 957.8114 | 957.8114
| 1 | Maximum concentrations using a unit emission rate of 1 g/s per generator.
Table R-2. Maximum Concentrations by Source Group, Annual Averaging Period
|  |  | Maximum Concentration1 (µg/m3) |  |  |  |  | Overall Maximum
| Source Group |  | 2013 | 2014 | 2015 | 2016 | 2017
| Combined Emissions |  | 754.0664 | 700.223 | 710.3907 | 740.9199 | 715.9527 | 754.0664
| 2500 kW Generators |  | 684.9151 | 643.0373 | 651.9864 | 680.5904 | 655.8276 | 684.9151
| 1825 kW Generator |  | 45.5984 | 45.0394 | 38.3625 | 40.9729 | 36.5598 | 45.5984
|  | 600 kW Generator | 38.8751 | 37.3211 | 38.0929 | 39.2576 | 37.9175 | 39.2576
|  | 750 kW Generator | 28.7315 | 30.6066 | 31.3148 | 30.7775 | 31.4233 | 31.4233
|  | 100 kW Generator | 54.1763 | 52.2821 | 55.6411 | 53.0135 | 45.9549 | 55.6411
| Fire Pumps |  | 58.1284 | 68.1383 | 75.6739 | 69.8384 | 78.239 | 78.239
| 1 | Maximum concentrations using a unit emission rate of 1 g/s per generator.
v0.3 models
Table R-1. Maximum Concentrations by Source Group, 24-hr Averaging Period
|  |  | Maximum Concentration1 (µg/m3) |  |  |  |  | Overall Maximum
| Source Group |  | 2013 | 2014 | 2015 | 2016 | 2017
| Combined Emissions |  | 3727.8471 | 3292.8986 | 3387.0053 | 3122.1978 | 3501.952 | 3727.8471
| 2500 kW Generators |  | 3490.2062 | 3059.8021 | 3120.255 | 2880.2169 | 3137.5453 | 3490.2062
| 1825 kW Generator |  | 251.069 | 186.483 | 201.3113 | 210.0164 | 209.7767 | 251.069
|  | 600 kW Generator | 398.93 | 260.9278 | 238.0628 | 258.4766 | 288.8519 | 398.93
|  | 750 kW Generator | 195.8888 | 194.0052 | 223.4244 | 283.0168 | 254.1944 | 283.0168
|  | 100 kW Generator | 1056.2767 | 949.5049 | 607.9347 | 1106.1559 | 798.8296 | 1106.1559
| Fire Pumps |  | 782.7824 | 936.369 | 878.548 | 787.0068 | 957.8114 | 957.8114
| 1 | Maximum concentrations using a unit emission rate of 1 g/s per generator.
Table R-2. Maximum Concentrations by Source Group, Annual Averaging Period
|  |  | Maximum Concentration1 (µg/m3) |  |  |  |  | Overall Maximum
| Source Group |  | 2013 | 2014 | 2015 | 2016 | 2017
| Combined Emissions |  | 879.8489 | 814.0612 | 815.3493 | 863.0695 | 832.7389 | 879.8489
| 2500 kW Generators |  | 800.2901 | 736.3462 | 748.539 | 785.1238 | 756.4342 | 800.2901
| 1825 kW Generator |  | 45.5984 | 45.0394 | 38.3625 | 40.9729 | 36.5598 | 45.5984
|  | 600 kW Generator | 47.4424 | 45.5035 | 46.4988 | 47.9226 | 46.5123 | 47.9226
|  | 750 kW Generator | 28.7315 | 30.6066 | 31.3148 | 30.7775 | 31.4233 | 31.4233
|  | 100 kW Generator | 54.1763 | 52.2821 | 55.6411 | 53.0135 | 45.9549 | 55.6411
| Fire Pumps |  | 58.1284 | 68.1383 | 75.6739 | 69.8384 | 78.239 | 78.239
| 1 | Maximum concentrations using a unit emission rate of 1 g/s per generator.
Note on D5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Updated to v0.4 (updated stack orientation and height) model results.
Note on D17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Updated to v0.4 (updated stack orientation and height) model results.

## Criteria 39tpy
Amazon Data Services - PDX-4 Data Center
Non-Emergency Fuel Use and Emissions
|  | EPA Tier Rating | Non-Emergency Hours of Operation | 100% Load Fuel Use | Maximum Emission Factor1,2 (lbs/gal) |  |  |  | Non-Emergency Fuel Use3 (gal/yr) | Emission Rate (tpy) |  |  |  | Reference
Type | Quantity |  | (hrs/yr/gen) | (gal/hr/gen) | NOx | CO | VOC | PM |  | NOx | CO | VOC | PM | Make | size kW
Type A | 3 | 2 | 17.1454 | 53.6 | 0.29534 | 0.10517 | 0.018966 | 0.02338 | 2756.9786 | 0.40712 | 0.14498 | 0.026144 | 0.032229 | CAT C27 | 750 | --
Type B | 3 | 2 | 17.1454 | 57.3 | 0.29023 | 0.10417 | 0.015833 | 0.02338 | 2947.2924 | 0.42769 | 0.1535 | 0.023333 | 0.034454 | CAT C27 | 800 | --
Type C | 1 | 2 | 17.1454 | 71.9 | 0.26759 | 0.2224 | 0.0272 | 0.02338 | 1232.7535 | 0.16494 | 0.13708 | 0.016765 | 0.014411 | CAT C32 | 1000 | --
Type D | 1 | 2 | 17.1454 | 128.4 | 0.27835 | 0.15131 | 0.037079 | 0.02338 | 2201.468 | 0.30639 | 0.16655 | 0.040814 | 0.025735 | CAT 3516C Trans | 1825 | Portable
Type E | 6 | 2 | 17.1454 | 138.9 | 0.25119 | 0.085227 | 0.028409 | 0.02338 | 14288.9672 | 1.7946 | 0.6089 | 0.20297 | 0.16704 | CAT 3516C | 2000 | --
Type F | 79 | 2 | 17.1454 | 173.5 | 0.29159 | 0.1476 | 0.030671 | 0.016975 | 235003.2752 | 34.2617 | 17.3437 | 3.6039 | 1.9946 | CAT 3516C | 2500 | Main
Type G | 3 | 2 | 17.1454 | 163 | 0.29406 | 0.04056 | 0.005408 | 0.02338 | 8384.0953 | 1.2327 | 0.17003 | 0.02267 | 0.09801 | MTU 2250 | 2250 | --
Type H | 1 | 2 | 17.1454 | 53.6 | 0.26493 | 0.49789 | 0.20105 | 0.23474 | 918.9929 | 0.12173 | 0.22878 | 0.092383 | 0.10786 | CAT C18 | 750 | Ski Lodge
Type I | 1 | 2 | 17.1454 | 103.2 | 0.32 | 0.21436 | 0.037436 | 0.02338 | 1769.4042 | 0.2831 | 0.18964 | 0.03312 | 0.020684 | CAT 3512C | 1500 | Ski Lodge
[7 empty] | Facility Total |  | 269504 | 39 | 19.1432 | 4.0621 | 2.495
1 Emission factors in lb/gal are calculated by dividing the manufacturer's potential site variation mass emission rates by fuel consumption. The maximum calculated emission factors are used for this inventory.
2 The PM/PM10/PM2.5 emission factor for the CAT 2500 kW engine is obtained using the 2021 stack test results for diesel particulate matter. The reported value includes the average lb/1,000 gal stack test result plus two standard deviations to determine an applicable emission factor. PM/PM10/PM2.5 emission factors for units < 560 kW are obtained from the manufacturer's PM + HC data in order to represent potential filterable and condensable PM in the generator emission estimates. The emission rate provided in the manufacturer’s specifications for these units uses Method 1065 to determine PM emissions whereas Oregon DEQ uses Oregon Method 5. In the absence of specific stationary source stack test information (as used for the 2,500 kW stationary generators), a factor of particulate matter plus measured hydrocarbon has been used to account for condensable particulate matter per Oregon DEQ's request. Oregon DEQ approved emission factor of 23.38 lbs/1,000 gal for diesel particulate matter for units > 560 kW is derived based on evaluation of all engine test data available in Oregon on August 15, 2022. Emission factors for units > 560 kW is determined by comparing the Oregon DEQ approved emission factor with Manufacturer's PM + HC data. The lesser of the two values was used for each of these units; unless the manufacturer's specification shows a higher PM value than Oregon DEQ's emission factor at the specified load level (ex. C18 750 kW) or the unit has an aftertreatment system. Emission factors for units < 560 kW are represented as Manufacturer's PM + HC data. Additionally, if manufacturer data is only supplied at the 100% load level and is less than the Oregon DEQ approved factor, then the Oregon DEQ approved factor is conservatively used because PM emissions are expected to be higher at lower load levels.
3 Fuel use calculated based on total expected operating hours for each engine type for annual testing and maintinence while remaining under the Minor Source limit of 39 tpy of NOx.
Note on B7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Updated to include calculations consistent with EI submittal

## Gen IDs
GenNum | Type | Description | REER_Acute | REER_ResCan | REER_WorCan | REER_ChiCan |  |  | reference
B04_G13A | Type E | CAT 3516C 2000kW | 0.00152 | 0.0562 | 0.00452 | 0.00212
B04_G13B | Type E | CAT 3516C 2000kW | 0.00152 | 0.0562 | 0.00452 | 0.00212 |  | # of Gens | Make | size kW
B04_G14A | Type E | CAT 3516C 2000kW | 0.00152 | 0.0562 | 0.00452 | 0.00212 | 3 | 3 | CAT C27 | 750 |  | Type A
B04_G14B | Type E | CAT 3516C 2000kW | 0.00152 | 0.0562 | 0.00452 | 0.00212 | 3 | 3 | CAT C27 | 800 |  | Type B
B04_G15A | Type E | CAT 3516C 2000kW | 0.00152 | 0.0562 | 0.00452 | 0.00212 | 1 | 1 | CAT C32 | 1000 |  | Type C
B04_G15B | Type E | CAT 3516C 2000kW | 0.00152 | 0.0562 | 0.00452 | 0.00212 | 1 | 1 | CAT 3516C Trans | 1825 | (Portable) | Type D
B04_G15C | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201 | 6 | 6 | CAT 3516C | 2000 |  | Type E
B04_G16A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201 | 79 | 79 | CAT 3516C | 2500 | (Main) | Type F
B04_G16B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201 | 3 | 3 | MTU 2250 | 2250 |  | Type G
B04_G17A | Type G | MTU 2250 2250kW | 0.00178 | 0.0659 | 0.00531 | 0.00249 | 1 | 1 | CAT C18 | 750 | (Ski Lodge) | Type H
B04_G17B | Type G | MTU 2250 2250kW | 0.00178 | 0.0659 | 0.00531 | 0.00249 | 1 | 1 | CAT 3512C | 1500 | (Ski Lodge) | Type I
B04_G17C | Type G | MTU 2250 2250kW | 0.00178 | 0.0659 | 0.00531 | 0.00249 | total | 98
B04_G18A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B04_G18B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B04_G19A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B04_G19B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B04_G20A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B04_G20B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B52_G01A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B52_G01B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B52_G02A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B52_G02B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B52_G03A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B52_G03B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B52_G04A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B52_G04B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B52_G04C | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B52_G05A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B52_G05B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B52_G05C | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B52_G06A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B52_G06B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B52_G07A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B52_G07B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B52_G08A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B52_G08B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B55_G01A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B55_G01B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B55_G02A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B55_G02B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B55_G03A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B55_G03B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B55_G04A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B55_G04B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B55_G04C | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B55_G05A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B55_G05B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B55_G05C | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B55_G06A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B55_G06B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B55_G07A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B55_G07B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B58_G01A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B58_G01B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B58_G02A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B58_G02B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B58_G03A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B58_G03B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B58_G04A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B58_G04B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B58_G04C | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B58_G05A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B58_G05B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B58_G05C | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B58_G06A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B58_G06B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B58_G07A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B58_G07B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B58_G08A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B58_G08B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B61_G01A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B61_G01B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B61_G02A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B61_G02B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B61_G03A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B61_G03B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B61_G04A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B61_G04B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B61_G04C | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B61_G05A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B61_G05B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B61_G05C | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B61_G06A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B61_G06B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B61_G07A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B61_G07B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B61_G08A | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
B61_G08B | Type F | CAT 3516C 2500kW(Main) | 0.00141 | 0.0518 | 0.00406 | 0.00201
P04_GEN1 | Type A | CAT C27 750kW | 0.000586 | 0.0217 | 0.00175 | 0.000818
P04_GEN2 | Type B | CAT C27 800kW | 0.000627 | 0.0232 | 0.00187 | 0.000874
P04_GEN3 | Type B | CAT C27 800kW | 0.000627 | 0.0232 | 0.00187 | 0.000874
P04_GEN4 | Type A | CAT C27 750kW | 0.000586 | 0.0217 | 0.00175 | 0.000818
P04_GEN5 | Type B | CAT C27 800kW | 0.000627 | 0.0232 | 0.00187 | 0.000874
P04_GEN6 | Type A | CAT C27 750kW | 0.000586 | 0.0217 | 0.00175 | 0.000818
P04_GENC | Type C | CAT C32 1000kW | 0.000786 | 0.0291 | 0.00234 | 0.0011
SKILODG1 | Type H | CAT C18 750kW(Ski Lodge) | 0.000586 | 0.187 | 0.0155 | 0.00719
SKILODG2 | Type I | CAT 3512C 1500kW(Ski Lodge) | 0.00113 | 0.0417 | 0.00336 | 0.00157
PORTABLE | Type D | CAT 3516C Trans 1825kW(Portable) | 0.0014 | 0.0519 | 0.00418 | 0.00196

## ODEQ Emissions Factors
Diesel Internal Combustion Engines (stationary and portable)
In order to meet regulatory standards, internal combustion diesel engines were introduced according to a tiered structure where newer engines ahdere to stricter emissions standard than older ones. Emission factors presented here are divided by Tier 0 and 1 engines, and Tiers 2,3, and 4 engines. The emission factors are a combination of recent source test data, and those found in California's South Coast Air Quality Monitoring District AB2588 table B-2 for Internal diesel combustion engines. All engines smaller than 560 kW or 750 hp, regardless of age or tier, should use the first emission factor set. More information is available in the References table in the Instructions tab, or on the Cleaner Air Oregon website.
Ammonia (highlighted yellow): the listed 2.9 lb/M gal value corresponds to equipment with Selective Non-catalytic Reduction (SNCR). For equipment with Selective Catalytic Reduction (SCR), substitute the listed value with 1.4 lb/M gal, and for equipment without SNCR or SCR, substitute listed value with 0.8 lb/M gal. Update Note accordingly.
Relevant units of measure: M gal = 1,000 gallons
Pre-2006 Tier 0 and Tier 1 Diesel Internal Combustion Engines, all engines less than 560 kW (750 hp)
| CAS or DEQ ID | Pollutant Name | Controlled EF? | Control Efficiency | EF Values | Units | EF Reference/Notes
| 106-99-0 | 1,3-Butadiene | N | 0% | 0.2174 | lb/M gal | CAO Diesel RICE (a)
| 75-07-0 | Acetaldehyde | N | 0% | 0.7833 | lb/M gal | CAO Diesel RICE (a)
| 107-02-8 | Acrolein | N | 0% | 0.0339 | lb/M gal | CAO Diesel RICE (a)
| 7664-41-7 | Ammonia | N | 0% | 0.8 | lb/M gal | CAO Diesel RICE (a)
| 7440-36-0 | Antimony and compounds | N | 0% | 0.00031819 | lb/M gal | CAO Diesel RICE (a)
| 7440-38-2 | Arsenic and compounds | N | 0% | 0.0016 | lb/M gal | CAO Diesel RICE (a)
| 7440-39-3 | Barium and compounds | N | 0% | 0.00037389 | lb/M gal | CAO Diesel RICE (a)
| 71-43-2 | Benzene | N | 0% | 0.1863 | lb/M gal | CAO Diesel RICE (a)
| 50-32-8 | Benzo[a]pyrene | N | 0% | 3.52e-05 | lb/M gal | CAO Diesel RICE (a)
| 7440-41-7 | Beryllium and compounds | N | 0% | 4.7708e-06 | lb/M gal | CAO Diesel RICE (a)
| 7440-43-9 | Cadmium and compounds | N | 0% | 0.0015 | lb/M gal | CAO Diesel RICE (a)
| 18540-29-9 | Chromium VI, chromate and dichromate particulate | N | 0% | 0.0001 | lb/M gal | CAO Diesel RICE (a)
| 108-90-7 | Chlorobenzene | N | 0% | 0.0002 | lb/M gal | CAO Diesel RICE (a)
| 7440-48-4 | Cobalt and compounds | N | 0% | 1.5751e-05 | lb/M gal | CAO Diesel RICE (a)
| 7440-50-8 | Copper and compounds | N | 0% | 0.0041 | lb/M gal | CAO Diesel RICE (a)
| 200 | Diesel particulate matter | N | 0% | 33.5 | lb/M gal | CAO Diesel RICE (a)
| 100-41-4 | Ethyl benzene | N | 0% | 0.0109 | lb/M gal | CAO Diesel RICE (a)
| 50-00-0 | Formaldehyde | N | 0% | 1.7261 | lb/M gal | CAO Diesel RICE (a)
| 110-54-3 | Hexane | N | 0% | 0.0269 | lb/M gal | CAO Diesel RICE (a)
| 7647-01-0 | Hydrochloric acid | N | 0% | 0.1863 | lb/M gal | CAO Diesel RICE (a)
| 7439-92-1 | Lead and compounds | N | 0% | 0.0083 | lb/M gal | CAO Diesel RICE (a)
| 7439-96-5 | Manganese and compounds | N | 0% | 0.0031 | lb/M gal | CAO Diesel RICE (a)
| 7439-97-6 | Mercury and compounds | N | 0% | 0.002 | lb/M gal | CAO Diesel RICE (a)
| 91-20-3 | Naphthalene | N | 0% | 0.0197 | lb/M gal | CAO Diesel RICE (a)
| 365 | Nickel and compounds | N | 0% | 0.0039 | lb/M gal | CAO Diesel RICE (a)
| 401 | Polycyclic aromatic hydrocarbons (PAHs) | N | 0% | 0.0362 | lb/M gal | CAO Diesel RICE (a)
| 504 | Phosphorus and compounds | N | 0% | 0.008404 | lb/M gal | CAO Diesel RICE (a)
| 115-07-1 | Propylene | N | 0% | 0.47 | lb/M gal | CAO Diesel RICE (a)
| 7782-49-2 | Selenium and compounds | N | 0% | 0.0022 | lb/M gal | CAO Diesel RICE (a)
| 7440-22-4 | Silver and compounds | N | 0% | 4.8013e-05 | lb/M gal | CAO Diesel RICE (a)
| 7440-28-0 | Thallium and compounds | N | 0% | 0.00024009 | lb/M gal | CAO Diesel RICE (a)
| 108-88-3 | Toluene | N | 0% | 0.1054 | lb/M gal | CAO Diesel RICE (a)
| 1330-20-7 | Xylene (mixture), including m-xylene, o-xylene, p-xylene | N | 0% | 0.0424 | lb/M gal | CAO Diesel RICE (a)
| 7440-66-6 | Zinc and compounds | N | 0% | 0.0052262 | lb/M gal | CAO Diesel RICE (a)
Post-2006 Tier 2, 3 and 4 Diesel Internal Combustion Engines
| CAS or DEQ ID | Pollutant Name | Controlled EF? | Control Efficiency | EF Values | Units | EF Reference/Notes
| 106-99-0 | 1,3-Butadiene | N | 0% | 0.2174 | lb/M gal | CAO Diesel RICE (b)
| 91-57-6 | 2-Methyl naphthalene | N | 0% | 0.012298 | lb/M gal | CAO Diesel RICE (b)
| 83-32-9 | Acenaphthene | N | 0% | 0.00073461 | lb/M gal | CAO Diesel RICE (b)
| 208-96-8 | Acenaphthylene | N | 0% | 0.00080982 | lb/M gal | CAO Diesel RICE (b)
| 75-07-0 | Acetaldehyde | N | 0% | 0.7833 | lb/M gal | CAO Diesel RICE (b)
| 107-02-8 | Acrolein | N | 0% | 0.0339 | lb/M gal | CAO Diesel RICE (b)
| 7664-41-7 | Ammonia | N | 0% | 0.8 | lb/M gal | CAO Diesel RICE (b)
| 120-12-7 | Anthracene | N | 0% | 0.00045209 | lb/M gal | CAO Diesel RICE (b)
| 7440-36-0 | Antimony and compounds | N | 0% | 0.00031819 | lb/M gal | CAO Diesel RICE (b)
| 7440-38-2 | Arsenic and compounds | N | 0% | 0.00027685 | lb/M gal | CAO Diesel RICE (b)
| 7440-39-3 | Barium and compounds | N | 0% | 0.00037389 | lb/M gal | CAO Diesel RICE (b)
| 56-55-3 | Benz[a]anthracene | N | 0% | 4.8541e-05 | lb/M gal | CAO Diesel RICE (b)
| 71-43-2 | Benzene | N | 0% | 0.1863 | lb/M gal | CAO Diesel RICE (b)
| 50-32-8 | Benzo[a]pyrene | N | 0% | 1.4385e-05 | lb/M gal | CAO Diesel RICE (b)
| 205-99-2 | Benzo[b]fluoranthene | N | 0% | 4.4354e-05 | lb/M gal | CAO Diesel RICE (b)
| 192-97-2 | Benzo[e]pyrene | N | 0% | 3.2868e-05 | lb/M gal | CAO Diesel RICE (b)
| 191-24-2 | Benzo[g,h,i]perylene | N | 0% | 2.1874e-05 | lb/M gal | CAO Diesel RICE (b)
| 207-08-9 | Benzo[k]fluoranthene | N | 0% | 1.3054e-05 | lb/M gal | CAO Diesel RICE (b)
| 7440-41-7 | Beryllium and compounds | N | 0% | 4.7708e-06 | lb/M gal | CAO Diesel RICE (b)
| 7440-43-9 | Cadmium and compounds | N | 0% | 8.0778e-05 | lb/M gal | CAO Diesel RICE (b)
| 108-90-7 | Chlorobenzene | N | 0% | 0.0002 | lb/M gal | CAO Diesel RICE (b)
| 18540-29-9 | Chromium VI, chromate and dichromate particulate | N | 0% | 6.3144e-05 | lb/M gal | CAO Diesel RICE (b)
| 218-01-9 | Chrysene | N | 0% | 6.7e-05 | lb/M gal | CAO Diesel RICE (b)
| 7440-48-4 | Cobalt and compounds | N | 0% | 1.5751e-05 | lb/M gal | CAO Diesel RICE (b)
| 7440-50-8 | Copper and compounds | N | 0% | 0.00050214 | lb/M gal | CAO Diesel RICE (b)
| 53-70-3 | Dibenz[a,h]anthracene | N | 0% | 1.037e-06 | lb/M gal | CAO Diesel RICE (b)
| 200 | Diesel particulate matter | N | 0% | 16.9752 | lb/M gal | CAO Diesel RICE (b)
| 100-41-4 | Ethyl benzene | N | 0% | 0.0109 | lb/M gal | CAO Diesel RICE (b)
| 206-44-0 | Fluoranthene | N | 0% | 0.00036995 | lb/M gal | CAO Diesel RICE (b)
| 86-73-7 | Fluorene | N | 0% | 0.0021844 | lb/M gal | CAO Diesel RICE (b)
| 50-00-0 | Formaldehyde | N | 0% | 2.7131 | lb/M gal | CAO Diesel RICE (b)
| 110-54-3 | Hexane | N | 0% | 0.0269 | lb/M gal | CAO Diesel RICE (b)
| 7647-01-0 | Hydrochloric acid | N | 0% | 0.1863 | lb/M gal | CAO Diesel RICE (b)
| 193-39-5 | Indeno[1,2,3-cd]pyrene | N | 0% | 1.0711e-05 | lb/M gal | CAO Diesel RICE (b)
| 7439-92-1 | Lead and compounds | N | 0% | 0.00036367 | lb/M gal | CAO Diesel RICE (b)
| 7439-96-5 | Manganese and compounds | N | 0% | 0.00041991 | lb/M gal | CAO Diesel RICE (b)
| 7439-97-6 | Mercury and compounds | N | 0% | 1.5107e-05 | lb/M gal | CAO Diesel RICE (b)
| 91-20-3 | Naphthalene | N | 0% | 0.026352 | lb/M gal | CAO Diesel RICE (b)
| 365 | Nickel and compounds | N | 0% | 0.00018223 | lb/M gal | CAO Diesel RICE (b)
| 198-55-0 | Perylene | N | 0% | 1.1782e-06 | lb/M gal | CAO Diesel RICE (b)
| 85-01-8 | Phenanthrene | N | 0% | 0.0045419 | lb/M gal | CAO Diesel RICE (b)
| 504 | Phosphorus and compounds | N | 0% | 0.008404 | lb/M gal | CAO Diesel RICE (b)
| 115-07-1 | Propylene | N | 0% | 0.47 | lb/M gal | CAO Diesel RICE (b)
| 129-00-0 | Pyrene | N | 0% | 0.00125 | lb/M gal | CAO Diesel RICE (b)
| 7782-49-2 | Selenium and compounds | N | 0% | 0.00037638 | lb/M gal | CAO Diesel RICE (b)
| 7440-22-4 | Silver and compounds | N | 0% | 4.8013e-05 | lb/M gal | CAO Diesel RICE (b)
| 7440-28-0 | Thallium and compounds | N | 0% | 0.00024009 | lb/M gal | CAO Diesel RICE (b)
| 108-88-3 | Toluene | N | 0% | 0.1054 | lb/M gal | CAO Diesel RICE (b)
| 1330-20-7 | Xylene (mixture), including m-xylene, o-xylene, p-xylene | N | 0% | 0.0424 | lb/M gal | CAO Diesel RICE (b)
| 7440-66-6 | Zinc and compounds | N | 0% | 0.0052262 | lb/M gal | CAO Diesel RICE (b)

## 2019 Stack Test
Table 2-1
Summary of Results – 10% Load
Run Number | Run 1 | Run 2 | Run 3 | Average
Date | 2019-08-03 | 2019-08-03 | 2019-08-03 | -- | All non-detects? | Effective Result
Particulate Matter Data
Filterable PM Emission Rate, lb/hr | 0.34 | 0.33 | 0.38 | 0.35 |  | 0.35 | 0.38
Condensable PM Emission Rate, lb/hr | 0.25 | 0.3 | 0.39 | 0.31 |  | 0.31 | 0.34
Total PM Emission Rate, lb/hr | 0.58 | 0.63 | 0.76 | 0.66 |  | 0.66 | 0.68
Metals Data
Arsenic Emission Rate, lb/hr | 3.85e-06 | 3.9e-06 | 5.7e-05 | 2.1583e-05 |  | 2.1583e-05 | 2.1583e-05
Cadmium Emission Rate, lb/hr | 1.7E-06 | 1.7E-06 | 1.7E-06 | 1.7e-06 | Y | 0 | 6.25e-06
Nickel Emission Rate, lb/hr | 2.2e-05 | 2.2e-05 | 0.00011 | 5.1e-05 |  | 5.1e-05 | 0.00014
Hexavalent Chromium Emission Rate, lb/hr | 7.6E-05 | 3.9E-05 | 7.7E-05 | 6.4e-05 | Y | 0 | 8e-05
Organics Data
Formaldehyde Emission Rate, lb/hr | 0.0051 | 0.039 | 0.043 | 0.029 |  | 0.029 | 0.042
1,3 Butadiene Emission Rate, lb/hr | -0.0025 | -0.0025 | -0.0026 | 0.0025 | Y | 0 | 0
Acetaldehyde Emission Rate, lb/hr | -0.037 | -0.037 | -0.038 | 0.037 | Y | 0 | 0
Benzene Emission Rate, lb/hr | -0.023 | -0.023 | -0.024 | 0.023 | Y | 0 | 0
Ethylbenzene Emission Rate, lb/hr | -0.023 | -0.023 | -0.024 | 0.023 | Y | 0 | 0
Hexane Emission Rate, lb/hr | -0.017 | -0.018 | -0.018 | 0.018 | Y | 0 | 0
Polycyclic Aromatic Hydrocarbons Data
Acenaphthene Emission Rate, lb/hr | 2.8E-05 | 2.9E-05 | 2.8E-05 | 2.8e-05 | Y | 0 | 0
Acenaphthylene Emission Rate, lb/hr | 2.8E-05 | 2.9E-05 | 2.8E-05 | 2.8e-05 | Y | 0 | 0
Anthracene Emission Rate, lb/hr | 9.3E-06 | 9.5E-06 | 9.4E-06 | 9.4e-06 | Y | 0 | 0
Benz[a]anthracene Emission Rate, lb/hr | 7.4E-06 | 7.6E-06 | 7.5E-06 | 7.5e-06 | Y | 0 | 0
Benzo[a]pyrene Emission Rate, lb/hr | 9.3E-06 | 9.5E-06 | 9.4E-06 | 9.4e-06 | Y | 0 | 0
Benzo[a]fluoranthene Emission Rate, lb/hr | 7.4E-06 | 7.6E-06 | 7.5E-06 | 7.5e-06 | Y | 0 | 0
Benzo[g,h,i]perylene Emission Rate, lb/hr | 7.4E-06 | 7.6E-06 | 7.5E-06 | 7.5e-06 | Y | 0 | 0
Benzo[k]fluoranthene Emission Rate, lb/hr | 9.3E-06 | 9.5E-06 | 9.4E-06 | 9.4e-06 | Y | 0 | 0
Chrysene Emission Rate, lb/hr | 7.4E-06 | 7.6E-06 | 7.5E-06 | 7.5e-06 | Y | 0 | 0
Dibenz[a,h]anthracene Emission Rate, lb/hr | 7.4E-06 | 7.6E-06 | 7.5E-06 | 7.5e-06 | Y | 0 | 0
Fluoranthene Emission Rate, lb/hr | 1.9E-05 | 1.9E-05 | 1.9E-05 | 1.9e-05 | Y | 0 | 0
Fluorene Emission Rate, lb/hr | 5.4E-05 | 6.4E-05 | 6.4E-05 | 6e-05 |  | 6e-05 | 6.8e-05
Indeno(1,2,3-cd)pyrene Emission Rate, lb/hr | 9.3E-06 | 9.5E-06 | 9.4E-06 | 9.4e-06 | Y | 0 | 0
Naphthalene Emission Rate, lb/hr | 1.2E-03 | 1.6E-03 | 1.5E-03 | 0.0015 |  | 0.0015 | 0.0015
Phenanthrene Emission Rate, lb/hr | 1.2E-04 | 1.3E-04 | 1.3E-04 | 0.00013 |  | 0.00013 | 0.00015
Pyrene Emission Rate, lb/hr | 1.2E-04 | 1.2E-04 | 1.3E-04 | 0.00013 |  | 0.00013 | 0.00015
Total PAH, excluding Napthalene | [5 empty] | 0.00032 | 0.000368
* Underlined values represent results below the detection limit. The detection limit was used for emission purposes.
Table 2-2
Summary of Results – 25% Load
Run Number | Run 1 | Run 2 | Run 3 | Average |  | Average
Date | 2019-07-03 | 2019-07-03 | 2019-07-03 | -- |  | --
Particulate Matter Data
Filterable PM Emission Rate, lb/hr | 0.36 | 0.32 | 0.34 | 0.34 |  | 0.34
Condensable PM Emission Rate, lb/hr | 0.33 | 0.31 | 0.39 | 0.34 |  | 0.34
Total PM Emission Rate, lb/hr | 0.68 | 0.62 | 0.73 | 0.68 |  | 0.68
Metals Data
Arsenic Emission Rate, lb/hr | 1.1E-05 | 1.1E-05 | 1.1E-05 | 1.1e-05 | Y | 0
Cadmium Emission Rate, lb/hr | 2.5E-06 | 2.5E-06 | 2.4E-06 | 2.5e-06 | Y | 0
Nickel Emission Rate, lb/hr | 2.5E-05 | 2.2E-05 | 2.0E-05 | 2.3e-05 |  | 2.3e-05
Hexavalent Chromium Emission Rate, lb/hr | 5.3E-05 | 5.5E-05 | 5.5E-05 | 5.4e-05 | Y | 0
Organics Data
Formaldehyde Emission Rate, lb/hr | 0.041 | 0.04 | 0.043 | 0.042 |  | 0.042
1,3 Butadiene Emission Rate, lb/hr | -0.0034 | -0.0034 | -0.0033 | 0.0034 | Y | 0
Acetaldehyde Emission Rate, lb/hr | -0.049 | -0.05 | -0.049 | 0.049 | Y | 0
Benzene Emission Rate, lb/hr | -0.029 | -0.03 | -0.029 | 0.029 | Y | 0
Ethylbenzene Emission Rate, lb/hr | -0.031 | -0.031 | -0.031 | 0.031 | Y | 0
Hexane Emission Rate, lb/hr | -0.023 | -0.024 | -0.023 | 0.023 | Y | 0
Polycyclic Aromatic Hydrocarbons Data
Acenaphthene Emission Rate, lb/hr | 4.3E-05 | 4.2E-05 | 4.3E-05 | 4.3e-05 | Y | 0
Acenaphthylene Emission Rate, lb/hr | 4.3E-05 | 4.2E-05 | 4.3E-05 | 4.3e-05 | Y | 0
Anthracene Emission Rate, lb/hr | 1.1E-05 | 1.1E-05 | 1.4E-05 | 1.2e-05 | Y | 0
Benz[a]anthracene Emission Rate, lb/hr | 1.1E-05 | 1.1E-05 | 1.2E-05 | 1.1e-05 | Y | 0
Benzo[a]pyrene Emission Rate, lb/hr | 1.4E-05 | 1.4E-05 | 1.4E-05 | 1.4e-05 | Y | 0
Benzo[a]fluoranthene Emission Rate, lb/hr | 1.1E-05 | 1.1E-05 | 1.2E-05 | 1.1e-05 | Y | 0
Benzo[g,h,i]perylene Emission Rate, lb/hr | 1.1E-05 | 1.1E-05 | 1.2E-05 | 1.1e-05 | Y | 0
Benzo[k]fluoranthene Emission Rate, lb/hr | 1.4E-05 | 1.4E-05 | 1.4E-05 | 1.4e-05 | Y | 0
Chrysene Emission Rate, lb/hr | 1.1E-05 | 1.1E-05 | 1.2E-05 | 1.1e-05 | Y | 0
Dibenz[a,h]anthracene Emission Rate, lb/hr | 1.1E-05 | 1.1E-05 | 1.2E-05 | 1.1e-05 | Y | 0
Fluoranthene Emission Rate, lb/hr | 1.1E-05 | 1.1E-05 | 2.9E-05 | 1.7e-05 | Y | 0
Fluorene Emission Rate, lb/hr | 4.4E-05 | 4.4E-05 | 4.9E-05 | 4.6e-05 |  | 4.6e-05
Indeno(1,2,3-cd)pyrene Emission Rate, lb/hr | 1.4E-05 | 1.4E-05 | 1.4E-05 | 1.4e-05 | Y | 0
Naphthalene Emission Rate, lb/hr | 1.1E-03 | 1.2E-03 | 1.2E-03 | 0.0012 |  | 0.0012
Phenanthrene Emission Rate, lb/hr | 1.1E-04 | 1.0E-04 | 1.2E-04 | 0.00011 |  | 0.00011
Pyrene Emission Rate, lb/hr | 1.3E-04 | 9.8E-05 | 1.4E-04 | 0.00012 |  | 0.00012
Total PAH, excluding Napthalene | [5 empty] | 0.000276
* Underlined values represent results below the detection limit. The detection limit was used for emission purposes.
Table 2-3
Summary of Results – 50% Load
Run Number | Run 1 | Run 2 | Run 3 | Average |  | Average
Date | 2019-06-03 | 2019-06-03 | 2019-06-03 | -- |  | --
Particulate Matter Data
Filterable PM Emission Rate, lb/hr | 0.22 | 0.38 | 0.54 | 0.38 |  | 0.38
Condensable PM Emission Rate, lb/hr | 0.27 | 0.29 | 0.29 | 0.28 |  | 0.28
Total PM Emission Rate, lb/hr | 0.49 | 0.67 | 0.83 | 0.66 |  | 0.66
Metals Data
Arsenic Emission Rate, lb/hr | 2.0E-05 | 2.0E-05 | 2.0E-05 | 2e-05 | Y | 0
Cadmium Emission Rate, lb/hr | 2.25e-06 | 4.6e-06 | 2.25e-06 | 3.0333e-06 |  | 3.0333e-06
Nickel Emission Rate, lb/hr | 6.2E-05 | 6.6E-05 | 8.9E-05 | 7.3e-05 |  | 7.3e-05
Hexavalent Chromium Emission Rate, lb/hr | 4.9E-06 | 4.9E-06 | 1.2E-05 | 7.4e-06 | Y | 0
Organics Data
Formaldehyde Emission Rate, lb/hr | 0.028 | 0.037 | 0.037 | 0.034 |  | 0.034
1,3 Butadiene Emission Rate, lb/hr | -0.0049 | -0.0048 | -0.0048 | 0.0048 | Y | 0
Acetaldehyde Emission Rate, lb/hr | -0.072 | -0.07 | -0.071 | 0.071 | Y | 0
Benzene Emission Rate, lb/hr | -0.043 | -0.042 | -0.042 | 0.043 | Y | 0
Ethylbenzene Emission Rate, lb/hr | -0.045 | -0.044 | -0.044 | 0.045 | Y | 0
Hexane Emission Rate, lb/hr | -0.034 | -0.034 | -0.034 | 0.034 | Y | 0
Polycyclic Aromatic Hydrocarbons Data
Acenaphthene Emission Rate, lb/hr | 6.3E-05 | 6.2E-05 | 6.3E-05 | 6.3e-05 | Y | 0
Acenaphthylene Emission Rate, lb/hr | 6.3E-05 | 6.2E-05 | 6.3E-05 | 6.3e-05 | Y | 0
Anthracene Emission Rate, lb/hr | 1.7E-05 | 1.7E-05 | 1.7E-05 | 1.7e-05 | Y | 0
Benz[a]anthracene Emission Rate, lb/hr | 1.7E-05 | 1.7E-05 | 1.7E-05 | 1.7e-05 | Y | 0
Benzo[a]pyrene Emission Rate, lb/hr | 2.1E-05 | 2.1E-05 | 2.1E-05 | 2.1e-05 | Y | 0
Benzo[a]fluoranthene Emission Rate, lb/hr | 1.7E-05 | 1.7E-05 | 1.7E-05 | 1.7e-05 | Y | 0
Benzo[g,h,i]perylene Emission Rate, lb/hr | 1.7E-05 | 1.7E-05 | 1.7E-05 | 1.7e-05 | Y | 0
Benzo[k]fluoranthene Emission Rate, lb/hr | 2.1E-05 | 2.1E-05 | 2.1E-05 | 2.1e-05 | Y | 0
Chrysene Emission Rate, lb/hr | 1.7E-05 | 1.7E-05 | 1.7E-05 | 1.7e-05 | Y | 0
Dibenz[a,h]anthracene Emission Rate, lb/hr | 1.7E-05 | 1.7E-05 | 1.7E-05 | 1.7e-05 | Y | 0
Fluoranthene Emission Rate, lb/hr | 1.7E-05 | 1.7E-05 | 1.7E-05 | 1.7e-05 | Y | 0
Fluorene Emission Rate, lb/hr | 4.8E-05 | 4.2E-05 | 4.8E-05 | 4.6e-05 |  | 4.6e-05
Indeno(1,2,3-cd)pyrene Emission Rate, lb/hr | 2.1E-05 | 2.1E-05 | 2.1E-05 | 2.1e-05 | Y | 0
Naphthalene Emission Rate, lb/hr | 8.4E-04 | 9.2E-04 | 9.8E-04 | 0.00091 |  | 0.00091
Phenanthrene Emission Rate, lb/hr | 9.4E-05 | 9.2E-05 | 1.0E-04 | 9.5e-05 |  | 9.5e-05
Pyrene Emission Rate, lb/hr | 1.3E-04 | 1.0E-04 | 1.0E-04 | 0.00011 |  | 0.00011
Total PAH, excluding Napthalene | [5 empty] | 0.000251
* Underlined values represent results below the detection limit. The detection limit was used for emission purposes.
Table 2-4
Summary of Results – 75% Load
Run Number | Run 1 | Run 2 | Run 3 | Average |  | Average
Date | 2019-06-03 | 2019-06-03 | 2019-06-03 | -- |  | --
Particulate Matter Data
Filterable PM Emission Rate, lb/hr | 0.33 | 0.23 | 0.21 | 0.26 |  | 0.26
Condensable PM Emission Rate, lb/hr | 0.22 | 0.23 | 0.21 | 0.22 |  | 0.22
Total PM Emission Rate, lb/hr | 0.54 | 0.46 | 0.42 | 0.47 |  | 0.47
Metals Data
Arsenic Emission Rate, lb/hr | 1.9E-05 | 1.9E-05 | 1.9E-05 | 1.9e-05 | Y | 0
Cadmium Emission Rate, lb/hr | 4.3E-06 | 4.2E-06 | 4.3E-06 | 4.3e-06 | Y | 0
Nickel Emission Rate, lb/hr | 7.1E-05 | 6.3E-05 | 6.9E-05 | 6.8e-05 |  | 6.8e-05
Hexavalent Chromium Emission Rate, lb/hr | 9.9E-05 | 1.0E-04 | 2.5E-05 | 7.5e-05 | Y | 0
Organics Data
Formaldehyde Emission Rate, lb/hr | 0.029 | 0.02 | 0.036 | 0.028 |  | 0.028
1,3 Butadiene Emission Rate, lb/hr | -0.0062 | -0.0059 | -0.0059 | 0.006 | Y | 0
Acetaldehyde Emission Rate, lb/hr | -0.091 | -0.087 | -0.086 | 0.088 | Y | 0
Benzene Emission Rate, lb/hr | -0.055 | -0.052 | -0.052 | 0.053 | Y | 0
Ethylbenzene Emission Rate, lb/hr | -0.058 | -0.055 | -0.054 | 0.056 | Y | 0
Hexane Emission Rate, lb/hr | -0.044 | -0.042 | -0.041 | 0.042 | Y | 0
Polycyclic Aromatic Hydrocarbons Data
Acenaphthene Emission Rate, lb/hr | 4.2E-05 | 4.2E-05 | 4.2E-05 | 4.2e-05 | Y | 0
Acenaphthylene Emission Rate, lb/hr | 4.2E-05 | 4.2E-05 | 4.2E-05 | 4.2e-05 | Y | 0
Anthracene Emission Rate, lb/hr | 1.1E-05 | 1.1E-05 | 1.4E-05 | 1.2e-05 | Y | 0
Benz[a]anthracene Emission Rate, lb/hr | 1.1E-05 | 1.1E-05 | 1.1E-05 | 1.1e-05 | Y | 0
Benzo[a]pyrene Emission Rate, lb/hr | 1.4E-05 | 1.4E-05 | 1.4E-05 | 1.4e-05 | Y | 0
Benzo[a]fluoranthene Emission Rate, lb/hr | 1.1E-05 | 1.1E-05 | 1.1E-05 | 1.1e-05 | Y | 0
Benzo[g,h,i]perylene Emission Rate, lb/hr | 1.1E-05 | 1.1E-05 | 1.1E-05 | 1.1e-05 | Y | 0
Benzo[k]fluoranthene Emission Rate, lb/hr | 1.4E-05 | 1.4E-05 | 1.4E-05 | 1.4e-05 | Y | 0
Chrysene Emission Rate, lb/hr | 1.1E-05 | 1.1E-05 | 1.1E-05 | 1.1e-05 | Y | 0
Dibenz[a,h]anthracene Emission Rate, lb/hr | 1.1E-05 | 1.1E-05 | 1.1E-05 | 1.1e-05 | Y | 0
Fluoranthene Emission Rate, lb/hr | 1.1E-05 | 1.1E-05 | 1.1E-05 | 1.1e-05 | Y | 0
Fluorene Emission Rate, lb/hr | 4.9E-05 | 4.8E-05 | 4.2E-05 | 4.6e-05 |  | 4.6e-05
Indeno(1,2,3-cd)pyrene Emission Rate, lb/hr | 1.4E-05 | 1.4E-05 | 1.4E-05 | 1.4e-05 | Y | 0
Naphthalene Emission Rate, lb/hr | 8.8E-04 | 8.4E-04 | 8.9E-04 | 0.00087 |  | 0.00087
Phenanthrene Emission Rate, lb/hr | 1.0E-04 | 8.8E-05 | 1.1E-04 | 0.0001 |  | 0.0001
Pyrene Emission Rate, lb/hr | 1.1E-04 | 9.8E-05 | 1.1E-04 | 0.00011 |  | 0.00011
Total PAH, excluding Napthalene | [5 empty] | 0.000256
* Underlined values represent results below the detection limit. The detection limit was used for emission purposes.
Table 2-5
Summary of Results – 100% Load
Run Number | Run 1 | Run 2 | Run 3 | Average |  | Average
Date | 2019-05-03 | 2019-05-03 | 2019-05-03 | -- |  | --
Particulate Matter Data
Filterable PM Emission Rate, lb/hr | 0.33 | 0.44 | 0.35 | 0.37 |  | 0.37
Condensable PM Emission Rate, lb/hr | 0.21 | 0.35 | 0.26 | 0.28 |  | 0.28
Total PM Emission Rate, lb/hr | 0.54 | 0.79 | 0.61 | 0.65 |  | 0.65
Metals Data
Arsenic Emission Rate, lb/hr | 2.0E-05 | 1.9E-05 | 1.9E-05 | 1.9e-05 | Y | 0
Cadmium Emission Rate, lb/hr | 1.1e-05 | 2.15e-06 | 5.6e-06 | 6.25e-06 |  | 6.25e-06
Nickel Emission Rate, lb/hr | 1.8E-04 | 1.1E-04 | 1.5E-04 | 0.00014 |  | 0.00014
Hexavalent Chromium Emission Rate, lb/hr | 0.00011 | 6.5e-05 | 6.5e-05 | 8e-05 |  | 8e-05
Organics Data
Formaldehyde Emission Rate, lb/hr | 0.037 | 0.035 | 0.024 | 0.032 |  | 0.032
1,3 Butadiene Emission Rate, lb/hr | -0.007 | -0.0069 | -0.0069 | 0.0069 | Y | 0
Acetaldehyde Emission Rate, lb/hr | -0.1 | -0.1 | -0.1 | 0.1 | Y | 0
Benzene Emission Rate, lb/hr | -0.06 | -0.061 | -0.06 | 0.061 | Y | 0
Ethylbenzene Emission Rate, lb/hr | -0.063 | -0.064 | -0.063 | 0.064 | Y | 0
Hexane Emission Rate, lb/hr | -0.048 | -0.049 | -0.048 | 0.048 | Y | 0
Polycyclic Aromatic Hydrocarbons Data
Acenaphthene Emission Rate, lb/hr | 4.4E-05 | 4.2E-05 | 4.2E-05 | 4.3e-05 | Y | 0
Acenaphthylene Emission Rate, lb/hr | 4.4E-05 | 4.2E-05 | 4.2E-05 | 4.3e-05 | Y | 0
Anthracene Emission Rate, lb/hr | 1.5E-05 | 1.4E-05 | 1.4E-05 | 1.4e-05 | Y | 0
Benz[a]anthracene Emission Rate, lb/hr | 1.2E-05 | 1.1E-05 | 1.1E-05 | 1.1e-05 | Y | 0
Benzo[a]pyrene Emission Rate, lb/hr | 1.5E-05 | 1.4E-05 | 1.4E-05 | 1.4e-05 | Y | 0
Benzo[a]fluoranthene Emission Rate, lb/hr | 1.2E-05 | 1.1E-05 | 1.1E-05 | 1.1e-05 | Y | 0
Benzo[g,h,i]perylene Emission Rate, lb/hr | 1.2E-05 | 1.1E-05 | 1.1E-05 | 1.1e-05 | Y | 0
Benzo[k]fluoranthene Emission Rate, lb/hr | 1.5E-05 | 1.4E-05 | 1.4E-05 | 1.4e-05 | Y | 0
Chrysene Emission Rate, lb/hr | 1.2E-05 | 1.1E-05 | 1.1E-05 | 1.1e-05 | Y | 0
Dibenz[a,h]anthracene Emission Rate, lb/hr | 1.2E-05 | 1.1E-05 | 1.1E-05 | 1.1e-05 | Y | 0
Fluoranthene Emission Rate, lb/hr | 3.0E-05 | 2.8E-05 | 2.8E-05 | 2.9e-05 | Y | 0
Fluorene Emission Rate, lb/hr | 5.9E-05 | 8.5E-05 | 6.0E-05 | 6.8e-05 |  | 6.8e-05
Indeno(1,2,3-cd)pyrene Emission Rate, lb/hr | 1.5E-05 | 1.4E-05 | 1.4E-05 | 1.4e-05 | Y | 0
Naphthalene Emission Rate, lb/hr | 1.1E-03 | 1.0E-03 | 9.6E-04 | 0.001 |  | 0.001
Phenanthrene Emission Rate, lb/hr | 1.5E-04 | 1.6E-04 | 1.4E-04 | 0.00015 |  | 0.00015
Pyrene Emission Rate, lb/hr | 1.6E-04 | 1.6E-04 | 1.3E-04 | 0.00015 |  | 0.00015
Total PAH, excluding Napthalene | [5 empty] | 0.000368
* Underlined values represent results below the detection limit. The detection limit was used for emission purposes.

## OAR 340-245 Table 2 RBCs
DRAFT OAR 340-245-8010 Table 2 Risk-Based Concentrations
|  |  |  | Residential Chronic RBCa |  |  |  | Non-Residential Chronic RBCa
|  |  | Noncancer | Cancer | Cancer | Noncancer | Noncancer | Child Cancer | Child Cancer | Child Noncancer | Child Noncancer | Worker Cancer | Worker Cancer | Worker Noncancer | Worker Noncancer | Acute RBCa | Acute RBCa | True | Adjusted | Early | Multipathway Adjustment Factor (MPAF)
CAS#b | Chemical | Notes | Class | (µg/m3) | (µg/m3) | (µg/m3) | (µg/m3) | (µg/m3) | (µg/m3) | (µg/m3) | (µg/m3) | (µg/m3) | (µg/m3) | (µg/m3) | (µg/m3) | (µg/m3) | (µg/m3) | Count | Count | Life | Resident | Non-Resident | Resident | Non-Resident
75-07-0 | Acetaldehyde |  | HI3 | 0.45455 | 0.45 | 140 | 140 | 11.8182 | 12 | 616 | 620 | 5.4545 | 5.5 | 616 | 620 | 470 | 470 | 1 | 1 | N | 1 | 1 | 1 | 1
60-35-5 | Acetamide |  | -- | 0.05 | 0.05 | -- | -- | 1.3 | 1.3 | -- | -- | 0.6 | 0.6 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
67-64-1 | Acetone |  | HI3 | -- | -- | 31000 | 31000 | -- | -- | 136400 | 140000 | -- | -- | 136400 | 140000 | 62000 | 62000 | 1 | 1 | N | 1 | 1 | 1 | 1
75-05-8 | Acetonitrile |  | HI3 | -- | -- | 60 | 60 | -- | -- | 264 | 260 | -- | -- | 264 | 260 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
107-02-8 | Acrolein |  | HI5 | -- | -- | 0.35 | 0.35 | -- | -- | 1.54 | 1.5 | -- | -- | 1.54 | 1.5 | 6.9 | 6.9 | 1 | 1 | N | 1 | 1 | 1 | 1
79-06-1 | Acrylamide | g | HI3 | 0.0058824 | 0.0059 | 6 | 6 | 0.061905 | 0.062 | 26.4 | 26 | 0.12 | 0.12 | 26.4 | 26 | -- | -- | 1 | 1 | Y | 1 | 1 | 1 | 1
79-10-7 | Acrylic acid |  | HI3 | -- | -- | 1 | 1 | -- | -- | 4.4 | 4.4 | -- | -- | 4.4 | 4.4 | 6000 | 6000 | 1 | 1 | N | 1 | 1 | 1 | 1
107-13-1 | Acrylonitrile |  | HI3 | 0.014706 | 0.015 | 5 | 5 | 0.38235 | 0.38 | 22 | 22 | 0.17647 | 0.18 | 22 | 22 | 220 | 220 | 1 | 1 | N | 1 | 1 | 1 | 1
309-00-2 | Aldrin |  | -- | 0.00020408 | 0.0002 | -- | -- | 0.0053061 | 0.0053 | -- | -- | 0.002449 | 0.0024 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
107-05-1 | Allyl chloride |  | HI3 | 0.16667 | 0.17 | 1 | 1 | 4.3333 | 4.3 | 4.4 | 4.4 | 2 | 2 | 4.4 | 4.4 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
7429-90-5 | Aluminum and compounds | l | HI5 | -- | -- | 5 | 5 | -- | -- | 22 | 22 | -- | -- | 22 | 22 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
7664-41-7 | Ammonia |  | HI3 | -- | -- | 500 | 500 | -- | -- | 2200 | 2200 | -- | -- | 2200 | 2200 | 1200 | 1200 | 1 | 1 | N | 1 | 1 | 1 | 1
62-53-3 | Aniline |  | HI5 | 0.625 | 0.63 | 1 | 1 | 16.25 | 16 | 4.4 | 4.4 | 7.5 | 7.5 | 4.4 | 4.4 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
7440-36-0 | Antimony and compounds |  | HI3 | -- | -- | 0.3 | 0.3 | -- | -- | 1.32 | 1.3 | -- | -- | 1.32 | 1.3 | 1 | 1 | 1 | 1 | N | 1 | 1 | 1 | 1
140-57-8 | Aramite |  | -- | 0.14085 | 0.14 | -- | -- | 3.662 | 3.7 | -- | -- | 1.6901 | 1.7 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
7440-38-2 | Arsenic and compounds | l | HI3 | 2.3975e-05 | 2.4e-05 | 0.00017045 | 0.00017 | 0.0013437 | 0.0013 | 0.0023571 | 0.0024 | 0.00062016 | 0.00062 | 0.0023571 | 0.0024 | 0.2 | 0.2 | 1 | 1 | N | 9.7 | 4.5 | 88 | 28
7784-42-1 | Arsine |  | HI3 | -- | -- | 0.015 | 0.015 | -- | -- | 0.066 | 0.066 | -- | -- | 0.066 | 0.066 | 0.2 | 0.2 | 1 | 1 | N | 1 | 1 | 1 | 1
1332-21-4 | Asbestos | i | -- | 4.3478e-06 | 4.3e-06 | -- | -- | 0.00011304 | 0.00011 | -- | -- | 5.2174e-05 | 5.2e-05 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
103-33-3 | Azobenzene |  | -- | 0.032258 | 0.032 | -- | -- | 0.83871 | 0.84 | -- | -- | 0.3871 | 0.39 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
71-43-2 | Benzene |  | HI3 | 0.12821 | 0.13 | 3 | 3 | 3.3333 | 3.3 | 13.2 | 13 | 1.5385 | 1.5 | 13.2 | 13 | 29 | 29 | 1 | 1 | N | 1 | 1 | 1 | 1
92-87-5 | Benzidine (and its salts) | g | -- | 4.2017e-06 | 4.2e-06 | -- | -- | 4.4218e-05 | 4.4e-05 | -- | -- | 8.5714e-05 | 8.6e-05 | -- | -- | -- | -- | 1 | 1 | Y | 1 | 1 | 1 | 1
100-44-7 | Benzyl chloride |  | HI3 | 0.020408 | 0.02 | 1 | 1 | 0.53061 | 0.53 | 4.4 | 4.4 | 0.2449 | 0.24 | 4.4 | 4.4 | 240 | 240 | 1 | 1 | N | 1 | 1 | 1 | 1
7440-41-7 | Beryllium and compounds | l | HI3 | 0.00041667 | 0.00042 | 0.007 | 0.007 | 0.010833 | 0.011 | 0.0308 | 0.031 | 0.005 | 0.005 | 0.0308 | 0.031 | 0.02 | 0.02 | 1 | 1 | N | 1 | 1 | 1 | 1
111-44-4 | Bis(2-chloroethyl) ether (BCEE) |  | HI3 | 0.0014085 | 0.0014 | -- | -- | 0.03662 | 0.037 | -- | -- | 0.016901 | 0.017 | -- | -- | 120 | 120 | 1 | 1 | N | 1 | 1 | 1 | 1
542-88-1 | Bis(chloromethyl) ether |  | HI5 | 7.6923e-05 | 7.7e-05 | -- | -- | 0.002 | 0.002 | -- | -- | 0.00092308 | 0.00092 | -- | -- | 1.4 | 1.4 | 1 | 1 | N | 1 | 1 | 1 | 1
117-81-7 | Bis(2-ethylhexyl) phthalate (DEHP) | c | -- | 0.080128 | 0.08 | -- | -- | 10.8333 | 11 | -- | -- | 5 | 5 | -- | -- | -- | -- | 1 | 1 | N | 5.2 | 1 | 1 | 1
75-25-2 | Bromoform |  | -- | 0.90909 | 0.91 | -- | -- | 23.6364 | 24 | -- | -- | 10.9091 | 11 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
74-83-9 | Bromomethane (Methyl bromide) |  | HI3 | -- | -- | 5 | 5 | -- | -- | 22 | 22 | -- | -- | 22 | 22 | 3900 | 3900 | 1 | 1 | N | 1 | 1 | 1 | 1
106-94-5 | 1-Bromopropane (n-propyl bromide) |  | HI3 | 0.47619 | 0.48 | 33.1 | 33 | 12.381 | 12 | 145.64 | 150 | 5.7143 | 5.7 | 145.64 | 150 | 1654 | 1700 | 1 | 1 | N | 1 | 1 | 1 | 1
106-99-0 | 1,3-Butadiene |  | HI3 | 0.033003 | 0.033 | 2 | 2 | 0.85809 | 0.86 | 8.8 | 8.8 | 0.39604 | 0.4 | 8.8 | 8.8 | 660 | 660 | 1 | 1 | N | 1 | 1 | 1 | 1
78-93-3 | 2-Butanone (Methyl ethyl ketone) |  | HI3 | -- | -- | 5000 | 5000 | -- | -- | 22000 | 22000 | -- | -- | 22000 | 22000 | 5000 | 5000 | 1 | 1 | N | 1 | 1 | 1 | 1
78-92-2 | sec-Butyl alcohol |  | HI3 | -- | -- | 30000 | 30000 | -- | -- | 132000 | 130000 | -- | -- | 132000 | 130000 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
7440-43-9 | Cadmium and compounds | c, l | HI3 | 0.00055556 | 0.00056 | 0.005 | 0.005 | 0.014444 | 0.014 | 0.036667 | 0.037 | 0.0066667 | 0.0067 | 0.036667 | 0.037 | 0.03 | 0.03 | 1 | 1 | N | 1 | 1 | 2 | 1.2
105-60-2 | Caprolactam |  | HI3 | -- | -- | 2.2 | 2.2 | -- | -- | 9.68 | 9.7 | -- | -- | 9.68 | 9.7 | 50 | 50 | 1 | 1 | N | 1 | 1 | 1 | 1
75-15-0 | Carbon disulfide |  | HI3 | -- | -- | 800 | 800 | -- | -- | 3520 | 3500 | -- | -- | 3520 | 3500 | 6200 | 6200 | 1 | 1 | N | 1 | 1 | 1 | 1
56-23-5 | Carbon tetrachloride |  | HI3 | 0.16667 | 0.17 | 100 | 100 | 4.3333 | 4.3 | 440 | 440 | 2 | 2 | 440 | 440 | 1900 | 1900 | 1 | 1 | N | 1 | 1 | 1 | 1
463-58-1 | Carbonyl sulfide |  | HI3 | -- | -- | 10 | 10 | -- | -- | 44 | 44 | -- | -- | 44 | 44 | 660 | 660 | 1 | 1 | N | 1 | 1 | 1 | 1
57-74-9 | Chlordane |  | HI3 | 0.01 | 0.01 | 0.02 | 0.02 | 0.26 | 0.26 | 0.088 | 0.088 | 0.12 | 0.12 | 0.088 | 0.088 | 0.2 | 0.2 | 1 | 1 | N | 1 | 1 | 1 | 1
108171-26-2 | Chlorinated paraffins | j | -- | 0.04 | 0.04 | -- | -- | 1.04 | 1 | -- | -- | 0.48 | 0.48 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
7782-50-5 | Chlorine |  | HI3 | -- | -- | 0.15 | 0.15 | -- | -- | 0.66 | 0.66 | -- | -- | 0.66 | 0.66 | 170 | 170 | 1 | 1 | N | 1 | 1 | 1 | 1
10049-04-4 | Chlorine dioxide |  | HI3 | -- | -- | 0.6 | 0.6 | -- | -- | 2.64 | 2.6 | -- | -- | 2.64 | 2.6 | 2.8 | 2.8 | 1 | 1 | N | 1 | 1 | 1 | 1
532-27-4 | 2-Chloroacetophenone |  | HI5 | -- | -- | 0.03 | 0.03 | -- | -- | 0.132 | 0.13 | -- | -- | 0.132 | 0.13 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
108-90-7 | Chlorobenzene |  | HI3 | -- | -- | 50 | 50 | -- | -- | 220 | 220 | -- | -- | 220 | 220 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
75-68-3 | 1-Chloro-1,1-difluoroethane |  | HI3 | -- | -- | 50000 | 50000 | -- | -- | 220000 | 220000 | -- | -- | 220000 | 220000 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
75-45-6 | Chlorodifluoromethane (Freon 22) |  | HI3 | -- | -- | 50000 | 50000 | -- | -- | 220000 | 220000 | -- | -- | 220000 | 220000 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
75-00-3 | Chloroethane (Ethyl chloride) |  | HI3 | -- | -- | 30000 | 30000 | -- | -- | 132000 | 130000 | -- | -- | 132000 | 130000 | 40000 | 40000 | 1 | 1 | N | 1 | 1 | 1 | 1
67-66-3 | Chloroform |  | HI3 | -- | -- | 300 | 300 | -- | -- | 1320 | 1300 | -- | -- | 1320 | 1300 | 490 | 490 | 1 | 1 | N | 1 | 1 | 1 | 1
74-87-3 | Chloromethane (Methyl chloride) |  | HI3 | -- | -- | 90 | 90 | -- | -- | 396 | 400 | -- | -- | 396 | 400 | 1000 | 1000 | 1 | 1 | N | 1 | 1 | 1 | 1
95-83-0 | 4-Chloro-o-phenylenediamine |  | -- | 0.21739 | 0.22 | -- | -- | 5.6522 | 5.7 | -- | -- | 2.6087 | 2.6 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
76-06-2 | Chloropicrin |  | HI3 | -- | -- | 0.4 | 0.4 | -- | -- | 1.76 | 1.8 | -- | -- | 1.76 | 1.8 | 29 | 29 | 1 | 1 | N | 1 | 1 | 1 | 1
126-99-8 | Chloroprene |  | HI3 | 0.0033333 | 0.0033 | 20 | 20 | 0.086667 | 0.087 | 88 | 88 | 0.04 | 0.04 | 88 | 88 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
95-69-2 | p-Chloro-o-toluidine |  | -- | 0.012987 | 0.013 | -- | -- | 0.33766 | 0.34 | -- | -- | 0.15584 | 0.16 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
18540-29-9 | Chromium VI, chromate and dichromate particulate | c, d | HI3 | 3.0637e-05 | 3.1e-05 | 0.083333 | 0.083 | 0.00051587 | 0.00052 | 0.88 | 0.88 | 0.001 | 0.001 | 0.88 | 0.88 | 0.3 | 0.3 | 1 | 1 | Y | 1.6 | 1 | 2.4 | 1
7738-94-5 | Chromic(VI) acid, including chromic acid aerosol mist and chromium trioxide | c, d | HI3 | 3.0637e-05 | 3.1e-05 | 0.0020833 | 0.0021 | 0.00051587 | 0.00052 | 0.022 | 0.022 | 0.001 | 0.001 | 0.022 | 0.022 | 0.005 | 0.005 | 1 | 1 | Y | 1.6 | 1 | 2.4 | 1
7440-48-4 | Cobalt and compounds | l | HI3 | -- | -- | 0.1 | 0.1 | -- | -- | 0.44 | 0.44 | -- | -- | 0.44 | 0.44 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
148 | Coke Oven Emissions | g | -- | 0.00094877 | 0.00095 | -- | -- | 0.0099846 | 0.01 | -- | -- | 0.019355 | 0.019 | -- | -- | -- | -- | 1 | 1 | Y | 1 | 1 | 1 | 1
7440-50-8 | Copper and compounds | l | HI3 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 100 | 100 | 1 | 1 | N | 1 | 1 | 1 | 1
120-71-8 | p-Cresidine |  | -- | 0.023256 | 0.023 | -- | -- | 0.60465 | 0.6 | -- | -- | 0.27907 | 0.28 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
1319-77-3 | Cresols (mixture), including m-cresol, o-cresol, p-cresol |  | HI3 | -- | -- | 600 | 600 | -- | -- | 2640 | 2600 | -- | -- | 2640 | 2600 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
135-20-6 | Cupferron |  | -- | 0.015873 | 0.016 | -- | -- | 0.4127 | 0.41 | -- | -- | 0.19048 | 0.19 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
74-90-8 | Cyanide, Hydrogen |  | HI3 | -- | -- | 0.8 | 0.8 | -- | -- | 3.52 | 3.5 | -- | -- | 3.52 | 3.5 | 340 | 340 | 1 | 1 | N | 1 | 1 | 1 | 1
110-82-7 | Cyclohexane |  | HI3 | -- | -- | 6000 | 6000 | -- | -- | 26400 | 26000 | -- | -- | 26400 | 26000 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
50-29-3 | DDT | e | -- | 0.010309 | 0.01 | -- | -- | 0.26804 | 0.27 | -- | -- | 0.12371 | 0.12 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
615-05-4 | 2,4-Diaminoanisole |  | -- | 0.15152 | 0.15 | -- | -- | 3.9394 | 3.9 | -- | -- | 1.8182 | 1.8 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
95-80-7 | 2,4-Diaminotoluene (2,4-Toluene diamine) |  | -- | 0.00090909 | 0.00091 | -- | -- | 0.023636 | 0.024 | -- | -- | 0.010909 | 0.011 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
333-41-5 | Diazinon |  | HI3 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 10 | 10 | 1 | 1 | N | 1 | 1 | 1 | 1
96-12-8 | 1,2-Dibromo-3-chloropropane (DBCP) | g | HI3 | 9.8039e-05 | 9.8e-05 | 0.2 | 0.2 | 0.0010317 | 0.001 | 0.88 | 0.88 | 0.002 | 0.002 | 0.88 | 0.88 | 1.9 | 1.9 | 1 | 1 | Y | 1 | 1 | 1 | 1
106-46-7 | p-Dichlorobenzene (1,4-Dichlorobenzene) |  | HI3 | 0.090909 | 0.091 | 60 | 60 | 2.3636 | 2.4 | 264 | 260 | 1.0909 | 1.1 | 264 | 260 | 12000 | 12000 | 1 | 1 | N | 1 | 1 | 1 | 1
91-94-1 | 3,3'-Dichlorobenzidine |  | -- | 0.0029412 | 0.0029 | -- | -- | 0.076471 | 0.076 | -- | -- | 0.035294 | 0.035 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
75-34-3 | 1,1-Dichloroethane (Ethylidene dichloride) |  | -- | 0.625 | 0.63 | -- | -- | 16.25 | 16 | -- | -- | 7.5 | 7.5 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
156-60-5 | trans-1,2-dichloroethene |  | HI3 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 790 | 790 | 1 | 1 | N | 1 | 1 | 1 | 1
75-09-2 | Dichloromethane (Methylene chloride) |  | HI3 | 58.8235 | 59 | 600 | 600 | 619.0476 | 620 | 2640 | 2600 | 1200 | 1200 | 2640 | 2600 | 2100 | 2100 | 1 | 1 | Y | 1 | 1 | 1 | 1
78-87-5 | 1,2-Dichloropropane (Propylene dichloride) |  | HI3 | -- | -- | 4 | 4 | -- | -- | 17.6 | 18 | -- | -- | 17.6 | 18 | 230 | 230 | 1 | 1 | N | 1 | 1 | 1 | 1
542-75-6 | 1,3-Dichloropropene |  | HI3 | 0.25 | 0.25 | 32 | 32 | 6.5 | 6.5 | 140.8 | 140 | 3 | 3 | 140.8 | 140 | 36 | 36 | 1 | 1 | N | 1 | 1 | 1 | 1
62-73-7 | Dichlorvos (DDVP) |  | HI5 | -- | -- | 0.54 | 0.54 | -- | -- | 2.376 | 2.4 | -- | -- | 2.376 | 2.4 | 18 | 18 | 1 | 1 | N | 1 | 1 | 1 | 1
60-57-1 | Dieldrin |  | -- | 0.00021739 | 0.00022 | -- | -- | 0.0056522 | 0.0057 | -- | -- | 0.0026087 | 0.0026 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
200 | Diesel Particulate Matter |  | HI3 | 0.1 | 0.1 | 5 | 5 | 2.6 | 2.6 | 22 | 22 | 1.2 | 1.2 | 22 | 22 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
111-42-2 | Diethanolamine |  | HI3 | -- | -- | 0.2 | 0.2 | -- | -- | 0.88 | 0.88 | -- | -- | 0.88 | 0.88 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
112-34-5 | Diethylene glycol monobutyl ether |  | HI3 | -- | -- | 0.1 | 0.1 | -- | -- | 0.44 | 0.44 | -- | -- | 0.44 | 0.44 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
111-90-0 | Diethylene glycol monoethyl ether |  | HI5 | -- | -- | 0.3 | 0.3 | -- | -- | 1.32 | 1.3 | -- | -- | 1.32 | 1.3 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
75-37-6 | 1,1-Difluoroethane |  | HI5 | -- | -- | 40000 | 40000 | -- | -- | 176000 | 180000 | -- | -- | 176000 | 180000 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
60-11-7 | 4-Dimethylaminoazobenzene |  | -- | 0.00076923 | 0.00077 | -- | -- | 0.02 | 0.02 | -- | -- | 0.0092308 | 0.0092 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
68-12-2 | Dimethyl formamide |  | HI3 | -- | -- | 80 | 80 | -- | -- | 352 | 350 | -- | -- | 352 | 350 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
57-14-7 | 1,1-Dimethylhydrazine |  | HI3 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.49 | 0.49 | 1 | 1 | N | 1 | 1 | 1 | 1
121-14-2 | 2,4-Dinitrotoluene |  | -- | 0.011236 | 0.011 | -- | -- | 0.29213 | 0.29 | -- | -- | 0.13483 | 0.13 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
123-91-1 | 1,4-Dioxane |  | HI3 | 0.2 | 0.2 | 30 | 30 | 5.2 | 5.2 | 132 | 130 | 2.4 | 2.4 | 132 | 130 | 7200 | 7200 | 1 | 1 | N | 1 | 1 | 1 | 1
122-66-7 | 1,2-Diphenylhydrazine (Hydrazobenzene) |  | -- | 0.0045455 | 0.0045 | -- | -- | 0.11818 | 0.12 | -- | -- | 0.054545 | 0.055 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
1937-37-7 | Direct Black 38 |  | -- | 7.1429e-06 | 7.1e-06 | -- | -- | 0.00018571 | 0.00019 | -- | -- | 8.5714e-05 | 8.6e-05 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
2602-46-2 | Direct Blue 6 |  | -- | 7.1429e-06 | 7.1e-06 | -- | -- | 0.00018571 | 0.00019 | -- | -- | 8.5714e-05 | 8.6e-05 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
16071-86-6 | Direct Brown 95 (technical grade) |  | -- | 7.1429e-06 | 7.1e-06 | -- | -- | 0.00018571 | 0.00019 | -- | -- | 8.5714e-05 | 8.6e-05 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
298-04-4 | Disulfoton |  | HI3 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 6 | 6 | 1 | 1 | N | 1 | 1 | 1 | 1
106-89-8 | Epichlorohydrin |  | HI3 | 0.043478 | 0.043 | 3 | 3 | 1.1304 | 1.1 | 13.2 | 13 | 0.52174 | 0.52 | 13.2 | 13 | 1300 | 1300 | 1 | 1 | N | 1 | 1 | 1 | 1
106-88-7 | 1,2-Epoxybutane |  | HI5 | -- | -- | 20 | 20 | -- | -- | 88 | 88 | -- | -- | 88 | 88 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
140-88-5 | Ethyl acrylate |  | HI3 | -- | -- | 8 | 8 | -- | -- | 35.2 | 35 | -- | -- | 35.2 | 35 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
100-41-4 | Ethyl benzene |  | HI3 | 0.4 | 0.4 | 260 | 260 | 10.4 | 10 | 1144 | 1100 | 4.8 | 4.8 | 1144 | 1100 | 22000 | 22000 | 1 | 1 | N | 1 | 1 | 1 | 1
106-93-4 | Ethylene dibromide (EDB, 1,2-Dibromoethane) |  | HI3 | 0.0016667 | 0.0017 | 9 | 9 | 0.043333 | 0.043 | 39.6 | 40 | 0.02 | 0.02 | 39.6 | 40 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
107-06-2 | Ethylene dichloride (EDC, 1,2-Dichloroethane) |  | HI3 | 0.038462 | 0.038 | 7 | 7 | 1 | 1 | 30.8 | 31 | 0.46154 | 0.46 | 30.8 | 31 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
107-21-1 | Ethylene glycol |  | HI3 | -- | -- | 400 | 400 | -- | -- | 1760 | 1800 | -- | -- | 1760 | 1800 | 2000 | 2000 | 1 | 1 | N | 1 | 1 | 1 | 1
111-76-2 | Ethylene glycol monobutyl ether |  | HI3 | -- | -- | 82 | 82 | -- | -- | 360.8 | 360 | -- | -- | 360.8 | 360 | 29000 | 29000 | 1 | 1 | N | 1 | 1 | 1 | 1
110-80-5 | Ethylene glycol monoethyl ether |  | HI3 | -- | -- | 70 | 70 | -- | -- | 308 | 310 | -- | -- | 308 | 310 | 370 | 370 | 1 | 1 | N | 1 | 1 | 1 | 1
111-15-9 | Ethylene glycol monoethyl ether acetate |  | HI3 | -- | -- | 60 | 60 | -- | -- | 264 | 260 | -- | -- | 264 | 260 | 140 | 140 | 1 | 1 | N | 1 | 1 | 1 | 1
109-86-4 | Ethylene glycol monomethyl ether |  | HI3 | -- | -- | 60 | 60 | -- | -- | 264 | 260 | -- | -- | 264 | 260 | 93 | 93 | 1 | 1 | N | 1 | 1 | 1 | 1
110-49-6 | Ethylene glycol monomethyl ether acetate |  | HI3 | -- | -- | 1 | 1 | -- | -- | 4.4 | 4.4 | -- | -- | 4.4 | 4.4 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
75-21-8 | Ethylene oxide | g | HI3 | 0.00019608 | 0.0002 | 30 | 30 | 0.0020635 | 0.0021 | 132 | 130 | 0.004 | 0.004 | 132 | 130 | 160 | 160 | 1 | 1 | Y | 1 | 1 | 1 | 1
96-45-7 | Ethylene thiourea |  | -- | 0.076923 | 0.077 | -- | -- | 2 | 2 | -- | -- | 0.92308 | 0.92 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
239 | Fluorides | c | HI3 | -- | -- | 2.2807 | 2.3 | -- | -- | 19.7241 | 20 | -- | -- | 19.7241 | 20 | 240 | 240 | 1 | 1 | N | 1 | 1 | 5.7 | 2.9
7782-41-4 | Fluorine gas |  | HI3 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 16 | 16 | 1 | 1 | N | 1 | 1 | 1 | 1
50-00-0 | Formaldehyde |  | HI3 | 0.16667 | 0.17 | 9 | 9 | 4.3333 | 4.3 | 39.6 | 40 | 2 | 2 | 39.6 | 40 | 49 | 49 | 1 | 1 | N | 1 | 1 | 1 | 1
111-30-8 | Glutaraldehyde |  | HI5 | -- | -- | 0.08 | 0.08 | -- | -- | 0.352 | 0.35 | -- | -- | 0.352 | 0.35 | 4.1 | 4.1 | 1 | 1 | N | 1 | 1 | 1 | 1
76-44-8 | Heptachlor |  | -- | 0.00076923 | 0.00077 | -- | -- | 0.02 | 0.02 | -- | -- | 0.0092308 | 0.0092 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
1024-57-3 | Heptachlor epoxide |  | -- | 0.00038462 | 0.00038 | -- | -- | 0.01 | 0.01 | -- | -- | 0.0046154 | 0.0046 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
118-74-1 | Hexachlorobenzene |  | -- | 0.0019608 | 0.002 | -- | -- | 0.05098 | 0.051 | -- | -- | 0.023529 | 0.024 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
87-68-3 | Hexachlorobutadiene |  | -- | 0.045455 | 0.045 | -- | -- | 1.1818 | 1.2 | -- | -- | 0.54545 | 0.55 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
608-73-1 | Hexachlorocyclohexanes (mixture) including but not limited to: | c | -- | 0.00016835 | 0.00017 | -- | -- | 0.018182 | 0.018 | -- | -- | 0.0083916 | 0.0084 | -- | -- | -- | -- | 1 | 1 | N | 5.4 | 1.3 | 1 | 1
319-84-6 | Hexachlorocyclohexane, alpha- | c | -- | 0.00016835 | 0.00017 | -- | -- | 0.018182 | 0.018 | -- | -- | 0.0083916 | 0.0084 | -- | -- | -- | -- | 1 | 1 | N | 5.4 | 1.3 | 1 | 1
319-85-7 | Hexachlorocyclohexane, beta- | c | -- | 0.00016835 | 0.00017 | -- | -- | 0.018182 | 0.018 | -- | -- | 0.0083916 | 0.0084 | -- | -- | -- | -- | 1 | 1 | N | 5.4 | 1.3 | 1 | 1
58-89-9 | Hexachlorocyclohexane, gamma- (Lindane) | c | -- | 0.00059737 | 0.0006 | -- | -- | 0.064516 | 0.065 | -- | -- | 0.029777 | 0.03 | -- | -- | -- | -- | 1 | 1 | N | 5.4 | 1.3 | 1 | 1
77-47-4 | Hexachlorocyclopentadiene |  | HI3 | -- | -- | 0.2 | 0.2 | -- | -- | 0.88 | 0.88 | -- | -- | 0.88 | 0.88 | 110 | 110 | 1 | 1 | N | 1 | 1 | 1 | 1
67-72-1 | Hexachloroethane |  | HI3 | -- | -- | 30 | 30 | -- | -- | 132 | 130 | -- | -- | 132 | 130 | 58000 | 58000 | 1 | 1 | N | 1 | 1 | 1 | 1
822-06-0 | Hexamethylene-1,6-diisocyanate |  | HI5 | -- | -- | 0.069 | 0.069 | -- | -- | 0.3036 | 0.3 | -- | -- | 0.3036 | 0.3 | 0.21 | 0.21 | 1 | 1 | N | 1 | 1 | 1 | 1
110-54-3 | Hexane |  | HI3 | -- | -- | 700 | 700 | -- | -- | 3080 | 3100 | -- | -- | 3080 | 3100 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
302-01-2 | Hydrazine |  | HI3 | 0.00020408 | 0.0002 | 0.03 | 0.03 | 0.0053061 | 0.0053 | 0.132 | 0.13 | 0.002449 | 0.0024 | 0.132 | 0.13 | 5.2 | 5.2 | 1 | 1 | N | 1 | 1 | 1 | 1
7647-01-0 | Hydrochloric acid |  | HI3 | -- | -- | 20 | 20 | -- | -- | 88 | 88 | -- | -- | 88 | 88 | 2100 | 2100 | 1 | 1 | N | 1 | 1 | 1 | 1
7664-39-3 | Hydrogen fluoride | c | HI3 | -- | -- | 2.1311 | 2.1 | -- | -- | 19.0667 | 19 | -- | -- | 19.0667 | 19 | 16 | 16 | 1 | 1 | N | 1 | 1 | 6.1 | 3
7783-06-4 | Hydrogen sulfide |  | HI3 | -- | -- | 2 | 2 | -- | -- | 8.8 | 8.8 | -- | -- | 8.8 | 8.8 | 98 | 98 | 1 | 1 | N | 1 | 1 | 1 | 1
78-59-1 | Isophorone |  | HI3 | -- | -- | 2000 | 2000 | -- | -- | 8800 | 8800 | -- | -- | 8800 | 8800 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
67-63-0 | Isopropyl alcohol |  | HI3 | -- | -- | 200 | 200 | -- | -- | 880 | 880 | -- | -- | 880 | 880 | 3200 | 3200 | 1 | 1 | N | 1 | 1 | 1 | 1
98-82-8 | Isopropylbenzene (Cumene) |  | HI3 | -- | -- | 400 | 400 | -- | -- | 1760 | 1800 | -- | -- | 1760 | 1800 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
7439-92-1 | Lead and compounds | c, l | HI3 | -- | -- | 0.15 | 0.15 | -- | -- | 0.66 | 0.66 | -- | -- | 0.66 | 0.66 | 0.15 | 0.15 | 1 | 1 | N | 11 | 5.8 | 1 | 1
108-31-6 | Maleic anhydride |  | HI5 | -- | -- | 0.7 | 0.7 | -- | -- | 3.08 | 3.1 | -- | -- | 3.08 | 3.1 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
7439-96-5 | Manganese and compounds | l | HI3 | -- | -- | 0.09 | 0.09 | -- | -- | 0.396 | 0.4 | -- | -- | 0.396 | 0.4 | 0.3 | 0.3 | 1 | 1 | N | 1 | 1 | 1 | 1
7439-97-6 | Mercury and compounds | c, l | HI3 | -- | -- | 0.076923 | 0.077 | -- | -- | 0.62857 | 0.63 | -- | -- | 0.62857 | 0.63 | 0.6 | 0.6 | 1 | 1 | N | 1 | 1 | 3.9 | 2.1
67-56-1 | Methanol |  | HI3 | -- | -- | 4000 | 4000 | -- | -- | 17600 | 18000 | -- | -- | 17600 | 18000 | 28000 | 28000 | 1 | 1 | N | 1 | 1 | 1 | 1
101-14-4 | 4,4'-Methylene bis(2-chloroaniline) (MOCA) |  | -- | 0.0023256 | 0.0023 | -- | -- | 0.060465 | 0.06 | -- | -- | 0.027907 | 0.028 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
101-77-9 | 4,4'-Methylenedianiline (and its dichloride) |  | HI5 | 0.00030193 | 0.0003 | 20 | 20 | 0.022609 | 0.023 | 88 | 88 | 0.010435 | 0.01 | 88 | 88 | -- | -- | 1 | 1 | N | 7.2 | 2.5 | 1 | 1
101-68-8 | Methylene diphenyl diisocyanate (MDI) |  | HI3 | -- | -- | 0.08 | 0.08 | -- | -- | 0.352 | 0.35 | -- | -- | 0.352 | 0.35 | 12 | 12 | 1 | 1 | N | 1 | 1 | 1 | 1
108-10-1 | Methyl isobutyl ketone (MIBK, Hexone) |  | HI3 | -- | -- | 3000 | 3000 | -- | -- | 13200 | 13000 | -- | -- | 13200 | 13000 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
624-83-9 | Methyl isocyanate |  | HI3 | -- | -- | 1 | 1 | -- | -- | 4.4 | 4.4 | -- | -- | 4.4 | 4.4 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
80-62-6 | Methyl methacrylate |  | HI5 | -- | -- | 700 | 700 | -- | -- | 3080 | 3100 | -- | -- | 3080 | 3100 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
1634-04-4 | Methyl tert-butyl ether |  | HI3 | 3.8462 | 3.8 | 8000 | 8000 | 100 | 100 | 35200 | 35000 | 46.1538 | 46 | 35200 | 35000 | 8000 | 8000 | 1 | 1 | N | 1 | 1 | 1 | 1
90-94-8 | Michler's ketone |  | -- | 0.004 | 0.004 | -- | -- | 0.104 | 0.1 | -- | -- | 0.048 | 0.048 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
91-20-3 | Naphthalene | c | HI3 | 0.029412 | 0.029 | 3.7 | 3.7 | 0.76471 | 0.76 | 16.28 | 16 | 0.35294 | 0.35 | 16.28 | 16 | 200 | 200 | 1 | 1 | N | 1 | 1 | 1 | 1
365 | Nickel compounds, insoluble | f | HI3 | 0.0038462 | 0.0038 | 0.014 | 0.014 | 0.1 | 0.1 | 0.0616 | 0.062 | 0.046154 | 0.046 | 0.0616 | 0.062 | 0.2 | 0.2 | 1 | 1 | N | 1 | 1 | 1 | 1
368 | Nickel compounds, soluble | f | HI3 | -- | -- | 0.014 | 0.014 | -- | -- | 0.0616 | 0.062 | -- | -- | 0.0616 | 0.062 | 0.2 | 0.2 | 1 | 1 | N | 1 | 1 | 1 | 1
7697-37-2 | Nitric acid |  | HI5 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 86 | 86 | 1 | 1 | N | 1 | 1 | 1 | 1
98-95-3 | Nitrobenzene |  | HI3 | 0.025 | 0.025 | 9 | 9 | 0.65 | 0.65 | 39.6 | 40 | 0.3 | 0.3 | 39.6 | 40 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
79-46-9 | 2-Nitropropane |  | HI3 | -- | -- | 20 | 20 | -- | -- | 88 | 88 | -- | -- | 88 | 88 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
924-16-3 | N-Nitrosodi-n-butylamine |  | -- | 0.00032258 | 0.00032 | -- | -- | 0.0083871 | 0.0084 | -- | -- | 0.003871 | 0.0039 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
55-18-5 | N-Nitrosodiethylamine | g | -- | 5.8824e-05 | 5.9e-05 | -- | -- | 0.00061905 | 0.00062 | -- | -- | 0.0012 | 0.0012 | -- | -- | -- | -- | 1 | 1 | Y | 1 | 1 | 1 | 1
62-75-9 | N-Nitrosodimethylamine | g | -- | 0.00012788 | 0.00013 | -- | -- | 0.0013458 | 0.0013 | -- | -- | 0.0026087 | 0.0026 | -- | -- | -- | -- | 1 | 1 | Y | 1 | 1 | 1 | 1
86-30-6 | N-Nitrosodiphenylamine |  | -- | 0.38462 | 0.38 | -- | -- | 10 | 10 | -- | -- | 4.6154 | 4.6 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
156-10-5 | p-Nitrosodiphenylamine |  | -- | 0.15873 | 0.16 | -- | -- | 4.127 | 4.1 | -- | -- | 1.9048 | 1.9 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
621-64-7 | N-Nitrosodi-n-propylamine |  | -- | 0.0005 | 0.0005 | -- | -- | 0.013 | 0.013 | -- | -- | 0.006 | 0.006 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
10595-95-6 | N-Nitrosomethylethylamine |  | -- | 0.00015873 | 0.00016 | -- | -- | 0.004127 | 0.0041 | -- | -- | 0.0019048 | 0.0019 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
59-89-2 | N-Nitrosomorpholine |  | -- | 0.00052632 | 0.00053 | -- | -- | 0.013684 | 0.014 | -- | -- | 0.0063158 | 0.0063 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
100-75-4 | N-Nitrosopiperidine |  | -- | 0.00037037 | 0.00037 | -- | -- | 0.0096296 | 0.0096 | -- | -- | 0.0044444 | 0.0044 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
930-55-2 | N-Nitrosopyrrolidine |  | -- | 0.0016667 | 0.0017 | -- | -- | 0.043333 | 0.043 | -- | -- | 0.02 | 0.02 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
8014-95-7 | Oleum (fuming sulfuric acid) |  | HI3 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 120 | 120 | 1 | 1 | N | 1 | 1 | 1 | 1
56-38-2 | Parathion |  | HI3 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.02 | 0.02 | 1 | 1 | N | 1 | 1 | 1 | 1
87-86-5 | Pentachlorophenol |  | -- | 0.19608 | 0.2 | -- | -- | 5.098 | 5.1 | -- | -- | 2.3529 | 2.4 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
108-95-2 | Phenol |  | HI3 | -- | -- | 200 | 200 | -- | -- | 880 | 880 | -- | -- | 880 | 880 | 5800 | 5800 | 1 | 1 | N | 1 | 1 | 1 | 1
75-44-5 | Phosgene |  | HI3 | -- | -- | 0.3 | 0.3 | -- | -- | 1.32 | 1.3 | -- | -- | 1.32 | 1.3 | 4 | 4 | 1 | 1 | N | 1 | 1 | 1 | 1
7803-51-2 | Phosphine |  | HI3 | -- | -- | 0.8 | 0.8 | -- | -- | 3.52 | 3.5 | -- | -- | 3.52 | 3.5 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
7664-38-2 | Phosphoric acid |  | HI3 | -- | -- | 10 | 10 | -- | -- | 44 | 44 | -- | -- | 44 | 44 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
12185-10-3 | Phosphorus, white |  | HI3 | -- | -- | 9 | 9 | -- | -- | 39.6 | 40 | -- | -- | 39.6 | 40 | 20 | 20 | 1 | 1 | N | 1 | 1 | 1 | 1
85-44-9 | Phthalic anhydride |  | HI3 | -- | -- | 20 | 20 | -- | -- | 88 | 88 | -- | -- | 88 | 88 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
447 | Polybrominated diphenyl ethers (PBDEs) | h | HI3 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 6 | 6 | 1 | 1 | N | 1 | 1 | 1 | 1
1336-36-3 | Polychlorinated biphenyls (PCBs) | c | -- | 0.00052632 | 0.00053 | -- | -- | 0.02 | 0.02 | -- | -- | 0.0092308 | 0.0092 | -- | -- | -- | -- | 1 | 1 | N | 19 | 13 | 240 | 11
645 | Polychlorinated biphenyls (PCBs) TEQ | c | HI3 | 1.0121e-09 | 1e-09 | 1.2903e-07 | 1.3e-07 | 9.0028e-08 | 9e-08 | 2.6269e-05 | 2.6e-05 | 4.1551e-08 | 4.2e-08 | 2.6269e-05 | 2.6e-05 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
32598-13-3 | PCB 77 [3,3',4,4'-tetrachlorobiphenyl] | c | HI3 | 1.0121e-05 | 1e-05 | 0.0012903 | 0.0013 | 0.00090028 | 0.0009 | 0.26269 | 0.26 | 0.00041551 | 0.00042 | 0.26269 | 0.26 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
70362-50-4 | PCB 81 [3,4,4',5-tetrachlorobiphenyl] | c | HI3 | 3.3738e-06 | 3.4e-06 | 0.00041935 | 0.00042 | 0.00030009 | 0.0003 | 0.085373 | 0.085 | 0.0001385 | 0.00014 | 0.085373 | 0.085 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
32598-14-4 | PCB 105 [2,3,3',4,4'-pentachlorobiphenyl] | c | HI3 | 3.3738e-05 | 3.4e-05 | 0.0041935 | 0.0042 | 0.0030009 | 0.003 | 0.85373 | 0.85 | 0.001385 | 0.0014 | 0.85373 | 0.85 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
74472-37-0 | PCB 114 [2,3,4,4',5-pentachlorobiphenyl] | c | HI3 | 3.3738e-05 | 3.4e-05 | 0.0041935 | 0.0042 | 0.0030009 | 0.003 | 0.85373 | 0.85 | 0.001385 | 0.0014 | 0.85373 | 0.85 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
31508-00-6 | PCB 118 [2,3',4,4',5-pentachlorobiphenyl] | c | HI3 | 3.3738e-05 | 3.4e-05 | 0.0041935 | 0.0042 | 0.0030009 | 0.003 | 0.85373 | 0.85 | 0.001385 | 0.0014 | 0.85373 | 0.85 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
65510-44-3 | PCB 123 [2,3',4,4',5'-pentachlorobiphenyl] | c | HI3 | 3.3738e-05 | 3.4e-05 | 0.0041935 | 0.0042 | 0.0030009 | 0.003 | 0.85373 | 0.85 | 0.001385 | 0.0014 | 0.85373 | 0.85 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
57465-28-8 | PCB 126 [3,3',4,4',5-pentachlorobiphenyl] | c | HI3 | 1.0121e-08 | 1e-08 | 1.2903e-06 | 1.3e-06 | 9.0028e-07 | 9e-07 | 0.00026269 | 0.00026 | 4.1551e-07 | 4.2e-07 | 0.00026269 | 0.00026 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
38380-08-4 | PCB 156 [2,3,3',4,4',5-hexachlorobiphenyl] | c | HI3 | 3.3738e-05 | 3.4e-05 | 0.0041935 | 0.0042 | 0.0030009 | 0.003 | 0.85373 | 0.85 | 0.001385 | 0.0014 | 0.85373 | 0.85 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
69782-90-7 | PCB 157 [2,3,3',4,4',5'-hexachlorobiphenyl] | c | HI3 | 3.3738e-05 | 3.4e-05 | 0.0041935 | 0.0042 | 0.0030009 | 0.003 | 0.85373 | 0.85 | 0.001385 | 0.0014 | 0.85373 | 0.85 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
52663-72-6 | PCB 167 [2,3',4,4',5,5'-hexachlorobiphenyl] | c | HI3 | 3.3738e-05 | 3.4e-05 | 0.0041935 | 0.0042 | 0.0030009 | 0.003 | 0.85373 | 0.85 | 0.001385 | 0.0014 | 0.85373 | 0.85 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
32774-16-6 | PCB 169 [3,3',4,4',5,5'-hexachlorobiphenyl] | c | HI3 | 3.3738e-08 | 3.4e-08 | 4.1935e-06 | 4.2e-06 | 3.0009e-06 | 3e-06 | 0.00085373 | 0.00085 | 1.385e-06 | 1.4e-06 | 0.00085373 | 0.00085 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
39635-31-9 | PCB 189 [2,3,3',4,4',5,5'-heptachlorobiphenyl] | c | HI3 | 3.3738e-05 | 3.4e-05 | 0.0041935 | 0.0042 | 0.0030009 | 0.003 | 0.85373 | 0.85 | 0.001385 | 0.0014 | 0.85373 | 0.85 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
646 | Polychlorinated dibenzo-p-dioxins (PCDDs) & dibenzofurans (PCDFs) TEQ | c | HI3 | 1.0121e-09 | 1e-09 | 1.2903e-07 | 1.3e-07 | 9.0028e-08 | 9e-08 | 2.6269e-05 | 2.6e-05 | 4.1551e-08 | 4.2e-08 | 2.6269e-05 | 2.6e-05 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
1746-01-6 | 2,3,7,8-Tetrachlorodibenzo-p-dioxin (TCDD) | c | HI3 | 1.0121e-09 | 1e-09 | 1.2903e-07 | 1.3e-07 | 9.0028e-08 | 9e-08 | 2.6269e-05 | 2.6e-05 | 4.1551e-08 | 4.2e-08 | 2.6269e-05 | 2.6e-05 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
40321-76-4 | 1,2,3,7,8-Pentachlorodibenzo-p-dioxin (PeCDD) | c | HI3 | 1.0121e-09 | 1e-09 | 1.2903e-07 | 1.3e-07 | 9.0028e-08 | 9e-08 | 2.6269e-05 | 2.6e-05 | 4.1551e-08 | 4.2e-08 | 2.6269e-05 | 2.6e-05 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
39227-28-6 | 1,2,3,4,7,8-Hexachlorodibenzo-p-dioxin (HxCDD) | c | HI3 | 1.0121e-08 | 1e-08 | 1.2903e-06 | 1.3e-06 | 9.0028e-07 | 9e-07 | 0.00026269 | 0.00026 | 4.1551e-07 | 4.2e-07 | 0.00026269 | 0.00026 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
57653-85-7 | 1,2,3,6,7,8-Hexachlorodibenzo-p-dioxin (HxCDD) | c | HI3 | 1.0121e-08 | 1e-08 | 1.2903e-06 | 1.3e-06 | 9.0028e-07 | 9e-07 | 0.00026269 | 0.00026 | 4.1551e-07 | 4.2e-07 | 0.00026269 | 0.00026 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
19408-74-3 | 1,2,3,7,8,9-Hexachlorodibenzo-p-dioxin (HxCDD) | c | HI3 | 1.0121e-08 | 1e-08 | 1.2903e-06 | 1.3e-06 | 9.0028e-07 | 9e-07 | 0.00026269 | 0.00026 | 4.1551e-07 | 4.2e-07 | 0.00026269 | 0.00026 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
35822-46-9 | 1,2,3,4,6,7,8-Heptachlorodibenzo-p-dioxin (HpCDD) | c | HI3 | 1.0121e-07 | 1e-07 | 1.2903e-05 | 1.3e-05 | 9.0028e-06 | 9e-06 | 0.0026269 | 0.0026 | 4.1551e-06 | 4.2e-06 | 0.0026269 | 0.0026 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
3268-87-9 | Octachlorodibenzo-p-dioxin (OCDD) | c | HI3 | 3.3738e-06 | 3.4e-06 | 0.00041935 | 0.00042 | 0.00030009 | 0.0003 | 0.085373 | 0.085 | 0.0001385 | 0.00014 | 0.085373 | 0.085 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
51207-31-9 | 2,3,7,8-Tetrachlorodibenzofuran (TcDF) | c | HI3 | 1.0121e-08 | 1e-08 | 1.2903e-06 | 1.3e-06 | 9.0028e-07 | 9e-07 | 0.00026269 | 0.00026 | 4.1551e-07 | 4.2e-07 | 0.00026269 | 0.00026 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
57117-41-6 | 1,2,3,7,8-Pentachlorodibenzofuran (PeCDF) | c | HI3 | 3.3738e-08 | 3.4e-08 | 4.1935e-06 | 4.2e-06 | 3.0009e-06 | 3e-06 | 0.00085373 | 0.00085 | 1.385e-06 | 1.4e-06 | 0.00085373 | 0.00085 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
57117-31-4 | 2,3,4,7,8-Pentachlorodibenzofuran (PeCDF) | c | HI3 | 3.3738e-09 | 3.4e-09 | 4.1935e-07 | 4.2e-07 | 3.0009e-07 | 3e-07 | 8.5373e-05 | 8.5e-05 | 1.385e-07 | 1.4e-07 | 8.5373e-05 | 8.5e-05 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
70648-26-9 | 1,2,3,4,7,8-Hexachlorodibenzofuran (HxCDF) | c | HI3 | 1.0121e-08 | 1e-08 | 1.2903e-06 | 1.3e-06 | 9.0028e-07 | 9e-07 | 0.00026269 | 0.00026 | 4.1551e-07 | 4.2e-07 | 0.00026269 | 0.00026 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
57117-44-9 | 1,2,3,6,7,8-Hexachlorodibenzofuran (HxCDF) | c | HI3 | 1.0121e-08 | 1e-08 | 1.2903e-06 | 1.3e-06 | 9.0028e-07 | 9e-07 | 0.00026269 | 0.00026 | 4.1551e-07 | 4.2e-07 | 0.00026269 | 0.00026 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
72918-21-9 | 1,2,3,7,8,9-Hexachlorodibenzofuran (HxCDF) | c | HI3 | 1.0121e-08 | 1e-08 | 1.2903e-06 | 1.3e-06 | 9.0028e-07 | 9e-07 | 0.00026269 | 0.00026 | 4.1551e-07 | 4.2e-07 | 0.00026269 | 0.00026 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
60851-34-5 | 2,3,4,6,7,8-Hexachlorodibenzofuran (HxCDF) | c | HI3 | 1.0121e-08 | 1e-08 | 1.2903e-06 | 1.3e-06 | 9.0028e-07 | 9e-07 | 0.00026269 | 0.00026 | 4.1551e-07 | 4.2e-07 | 0.00026269 | 0.00026 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
67562-39-4 | 1,2,3,4,6,7,8-Heptachlorodibenzofuran (HpCDF) | c | HI3 | 1.0121e-07 | 1e-07 | 1.2903e-05 | 1.3e-05 | 9.0028e-06 | 9e-06 | 0.0026269 | 0.0026 | 4.1551e-06 | 4.2e-06 | 0.0026269 | 0.0026 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
55673-89-7 | 1,2,3,4,7,8,9-Heptachlorodibenzofuran (HpCDF) | c | HI3 | 1.0121e-07 | 1e-07 | 1.2903e-05 | 1.3e-05 | 9.0028e-06 | 9e-06 | 0.0026269 | 0.0026 | 4.1551e-06 | 4.2e-06 | 0.0026269 | 0.0026 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
39001-02-0 | Octachlorodibenzofuran (OCDF) | c | HI3 | 3.3738e-06 | 3.4e-06 | 0.00041935 | 0.00042 | 0.00030009 | 0.0003 | 0.085373 | 0.085 | 0.0001385 | 0.00014 | 0.085373 | 0.085 | -- | -- | 1 | 1 | N | 26 | 7.6 | 310 | 6.7
401 | Polycyclic aromatic hydrocarbons (PAHs) | c, g | -- | 4.2626e-05 | 4.3e-05 | -- | -- | 0.0015633 | 0.0016 | -- | -- | 0.0030303 | 0.003 | -- | -- | -- | -- | 1 | 1 | Y | 23 | 6.6 | 1 | 1
191-26-4 | Anthanthrene | c, g | -- | 0.00010656 | 0.00011 | -- | -- | 0.0039081 | 0.0039 | -- | -- | 0.0075758 | 0.0076 | -- | -- | -- | -- | 1 | 1 | Y | 23 | 6.6 | 1 | 1
56-55-3 | Benz[a]anthracene | c, g | -- | 0.00021313 | 0.00021 | -- | -- | 0.0078163 | 0.0078 | -- | -- | 0.015152 | 0.015 | -- | -- | -- | -- | 1 | 1 | Y | 23 | 6.6 | 1 | 1
50-32-8 | Benzo[a]pyrene | c, g | HI3 | 4.2626e-05 | 4.3e-05 | 0.002 | 0.002 | 0.0015633 | 0.0016 | 0.0088 | 0.0088 | 0.0030303 | 0.003 | 0.0088 | 0.0088 | 0.002 | 0.002 | 1 | 1 | Y | 23 | 6.6 | 1 | 1
205-99-2 | Benzo[b]fluoranthene | c, g | -- | 5.3282e-05 | 5.3e-05 | -- | -- | 0.0019541 | 0.002 | -- | -- | 0.0037879 | 0.0038 | -- | -- | -- | -- | 1 | 1 | Y | 23 | 6.6 | 1 | 1
205-12-9 | Benzo[c]fluorene | c, g | -- | 2.1313e-06 | 2.1e-06 | -- | -- | 7.8163e-05 | 7.8e-05 | -- | -- | 0.00015152 | 0.00015 | -- | -- | -- | -- | 1 | 1 | Y | 23 | 6.6 | 1 | 1
191-24-2 | Benzo[g,h,i]perylene | c, g | -- | 0.0047362 | 0.0047 | -- | -- | 0.17369 | 0.17 | -- | -- | 0.3367 | 0.34 | -- | -- | -- | -- | 1 | 1 | Y | 23 | 6.6 | 1 | 1
205-82-3 | Benzo[j]fluoranthene | c, g | -- | 0.00014209 | 0.00014 | -- | -- | 0.0052108 | 0.0052 | -- | -- | 0.010101 | 0.01 | -- | -- | -- | -- | 1 | 1 | Y | 23 | 6.6 | 1 | 1
207-08-9 | Benzo[k]fluoranthene | c, g | -- | 0.0014209 | 0.0014 | -- | -- | 0.052108 | 0.052 | -- | -- | 0.10101 | 0.1 | -- | -- | -- | -- | 1 | 1 | Y | 23 | 6.6 | 1 | 1
218-01-9 | Chrysene | c, g | -- | 0.00042626 | 0.00043 | -- | -- | 0.015633 | 0.016 | -- | -- | 0.030303 | 0.03 | -- | -- | -- | -- | 1 | 1 | Y | 23 | 6.6 | 1 | 1
27208-37-3 | Cyclopenta[c,d]pyrene | c, g | -- | 0.00010656 | 0.00011 | -- | -- | 0.0039081 | 0.0039 | -- | -- | 0.0075758 | 0.0076 | -- | -- | -- | -- | 1 | 1 | Y | 23 | 6.6 | 1 | 1
53-70-3 | Dibenz[a,h]anthracene | c, g | -- | 4.2626e-06 | 4.3e-06 | -- | -- | 0.00015633 | 0.00016 | -- | -- | 0.00030303 | 0.0003 | -- | -- | -- | -- | 1 | 1 | Y | 23 | 6.6 | 1 | 1
192-65-4 | Dibenzo[a,e]pyrene | c, g | -- | 0.00010656 | 0.00011 | -- | -- | 0.0039081 | 0.0039 | -- | -- | 0.0075758 | 0.0076 | -- | -- | -- | -- | 1 | 1 | Y | 23 | 6.6 | 1 | 1
189-64-0 | Dibenzo[a,h]pyrene | c, g | -- | 4.7362e-05 | 4.7e-05 | -- | -- | 0.0017369 | 0.0017 | -- | -- | 0.003367 | 0.0034 | -- | -- | -- | -- | 1 | 1 | Y | 23 | 6.6 | 1 | 1
189-55-9 | Dibenzo[a,i]pyrene | c, g | -- | 7.1043e-05 | 7.1e-05 | -- | -- | 0.0026054 | 0.0026 | -- | -- | 0.0050505 | 0.0051 | -- | -- | -- | -- | 1 | 1 | Y | 23 | 6.6 | 1 | 1
191-30-0 | Dibenzo[a,l]pyrene | c, g | -- | 1.4209e-06 | 1.4e-06 | -- | -- | 5.2108e-05 | 5.2e-05 | -- | -- | 0.00010101 | 0.0001 | -- | -- | -- | -- | 1 | 1 | Y | 23 | 6.6 | 1 | 1
206-44-0 | Fluoranthene | c, g | -- | 0.00053282 | 0.00053 | -- | -- | 0.019541 | 0.02 | -- | -- | 0.037879 | 0.038 | -- | -- | -- | -- | 1 | 1 | Y | 23 | 6.6 | 1 | 1
193-39-5 | Indeno[1,2,3-cd]pyrene | c, g | -- | 0.00060894 | 0.00061 | -- | -- | 0.022332 | 0.022 | -- | -- | 0.04329 | 0.043 | -- | -- | -- | -- | 1 | 1 | Y | 23 | 6.6 | 1 | 1
3697-24-3 | 5-Methylchrysene | c, g | -- | 4.2626e-05 | 4.3e-05 | -- | -- | 0.0015633 | 0.0016 | -- | -- | 0.0030303 | 0.003 | -- | -- | -- | -- | 1 | 1 | Y | 23 | 6.6 | 1 | 1
7496-02-8 | 6-Nitrochrysene | c, g | -- | 4.2626e-06 | 4.3e-06 | -- | -- | 0.00015633 | 0.00016 | -- | -- | 0.00030303 | 0.0003 | -- | -- | -- | -- | 1 | 1 | Y | 23 | 6.6 | 1 | 1
7758-01-2 | Potassium bromate |  | -- | 0.0071429 | 0.0071 | -- | -- | 0.18571 | 0.19 | -- | -- | 0.085714 | 0.086 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
1120-71-4 | 1,3-Propane sultone |  | -- | 0.0014493 | 0.0014 | -- | -- | 0.037681 | 0.038 | -- | -- | 0.017391 | 0.017 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
123-38-6 | Propionaldehyde |  | HI5 | -- | -- | 8 | 8 | -- | -- | 35.2 | 35 | -- | -- | 35.2 | 35 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
115-07-1 | Propylene |  | HI5 | -- | -- | 3000 | 3000 | -- | -- | 13200 | 13000 | -- | -- | 13200 | 13000 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
6423-43-4 | Propylene glycol dinitrate |  | HI5 | -- | -- | 0.27 | 0.27 | -- | -- | 1.188 | 1.2 | -- | -- | 1.188 | 1.2 | 20 | 20 | 1 | 1 | N | 1 | 1 | 1 | 1
107-98-2 | Propylene glycol monomethyl ether |  | HI3 | -- | -- | 7000 | 7000 | -- | -- | 30800 | 31000 | -- | -- | 30800 | 31000 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
75-56-9 | Propylene oxide |  | HI3 | 0.27027 | 0.27 | 30 | 30 | 7.027 | 7 | 132 | 130 | 3.2432 | 3.2 | 132 | 130 | 3100 | 3100 | 1 | 1 | N | 1 | 1 | 1 | 1
572 | Refractory Ceramic Fibers | i | HI5 | -- | -- | 0.03 | 0.03 | -- | -- | 0.132 | 0.13 | -- | -- | 0.132 | 0.13 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
7783-07-5 | Selenide, hydrogen |  | HI3 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 5 | 5 | 1 | 1 | N | 1 | 1 | 1 | 1
7782-49-2 | Selenium and compounds | l | HI3 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 2 | 2 | 1 | 1 | N | 1 | 1 | 200 | 24
7631-86-9 | Silica, crystalline (respirable) |  | HI5 | -- | -- | 3 | 3 | -- | -- | 13.2 | 13 | -- | -- | 13.2 | 13 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
1310-73-2 | Sodium hydroxide |  | HI3 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 8 | 8 | 1 | 1 | N | 1 | 1 | 1 | 1
100-42-5 | Styrene |  | HI3 | -- | -- | 1000 | 1000 | -- | -- | 4400 | 4400 | -- | -- | 4400 | 4400 | 21000 | 21000 | 1 | 1 | N | 1 | 1 | 1 | 1
7664-93-9 | Sulfuric acid |  | HI5 | -- | -- | 1 | 1 | -- | -- | 4.4 | 4.4 | -- | -- | 4.4 | 4.4 | 120 | 120 | 1 | 1 | N | 1 | 1 | 1 | 1
505-60-2 | Sulfur Mustard |  | HI3 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.7 | 0.7 | 1 | 1 | N | 1 | 1 | 1 | 1
7446-11-9 | Sulfur trioxide |  | HI5 | -- | -- | 1 | 1 | -- | -- | 4.4 | 4.4 | -- | -- | 4.4 | 4.4 | 120 | 120 | 1 | 1 | N | 1 | 1 | 1 | 1
630-20-6 | 1,1,1,2-Tetrachloroethane |  | -- | 0.13514 | 0.14 | -- | -- | 3.5135 | 3.5 | -- | -- | 1.6216 | 1.6 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
79-34-5 | 1,1,2,2-Tetrachloroethane |  | -- | 0.017241 | 0.017 | -- | -- | 0.44828 | 0.45 | -- | -- | 0.2069 | 0.21 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
127-18-4 | Tetrachloroethene (Perchloroethylene) |  | HI3 | 3.8462 | 3.8 | 41 | 41 | 100 | 100 | 180.4 | 180 | 46.1538 | 46 | 180.4 | 180 | 41 | 41 | 1 | 1 | N | 1 | 1 | 1 | 1
811-97-2 | 1,1,1,2-Tetrafluoroethane |  | HI3 | -- | -- | 80000 | 80000 | -- | -- | 352000 | 350000 | -- | -- | 352000 | 350000 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
62-55-5 | Thioacetamide |  | -- | 0.00058824 | 0.00059 | -- | -- | 0.015294 | 0.015 | -- | -- | 0.0070588 | 0.0071 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
7550-45-0 | Titanium tetrachloride |  | HI3 | -- | -- | 0.1 | 0.1 | -- | -- | 0.44 | 0.44 | -- | -- | 0.44 | 0.44 | 10 | 10 | 1 | 1 | N | 1 | 1 | 1 | 1
108-88-3 | Toluene |  | HI3 | -- | -- | 5000 | 5000 | -- | -- | 22000 | 22000 | -- | -- | 22000 | 22000 | 7500 | 7500 | 1 | 1 | N | 1 | 1 | 1 | 1
26471-62-5 | Toluene diisocyanates (2,4- and 2,6-) |  | HI3 | 0.090909 | 0.091 | 0.021 | 0.021 | 2.3636 | 2.4 | 0.0924 | 0.092 | 1.0909 | 1.1 | 0.0924 | 0.092 | 0.071 | 0.071 | 1 | 1 | N | 1 | 1 | 1 | 1
8001-35-2 | Toxaphene (Polychlorinated camphenes) |  | -- | 0.003125 | 0.0031 | -- | -- | 0.08125 | 0.081 | -- | -- | 0.0375 | 0.038 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
71-55-6 | 1,1,1-Trichloroethane (Methyl chloroform) |  | HI3 | -- | -- | 5000 | 5000 | -- | -- | 22000 | 22000 | -- | -- | 22000 | 22000 | 11000 | 11000 | 1 | 1 | N | 1 | 1 | 1 | 1
79-00-5 | 1,1,2-Trichloroethane (Vinyl trichloride) |  | -- | 0.0625 | 0.063 | -- | -- | 1.625 | 1.6 | -- | -- | 0.75 | 0.75 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
79-01-6 | Trichloroethene (TCE, Trichloroethylene) | g | HI3 | 0.20325 | 0.2 | 2.1 | 2.1 | 3.523 | 3.5 | 9.24 | 9.2 | 2.9268 | 2.9 | 9.24 | 9.2 | 2.1 | 2.1 | 1 | 1 | Y | 1 | 1 | 1 | 1
88-06-2 | 2,4,6-Trichlorophenol |  | -- | 0.05 | 0.05 | -- | -- | 1.3 | 1.3 | -- | -- | 0.6 | 0.6 | -- | -- | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
96-18-4 | 1,2,3-Trichloropropane |  | HI5 | -- | -- | 0.3 | 0.3 | -- | -- | 1.32 | 1.3 | -- | -- | 1.32 | 1.3 | 1.8 | 1.8 | 1 | 1 | N | 1 | 1 | 1 | 1
121-44-8 | Triethylamine |  | HI3 | -- | -- | 200 | 200 | -- | -- | 880 | 880 | -- | -- | 880 | 880 | 2800 | 2800 | 1 | 1 | N | 1 | 1 | 1 | 1
526-73-8 | 1,2,3-Trimethylbenzene |  | HI3 | -- | -- | 60 | 60 | -- | -- | 264 | 260 | -- | -- | 264 | 260 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
95-63-6 | 1,2,4-Trimethylbenzene |  | HI3 | -- | -- | 60 | 60 | -- | -- | 264 | 260 | -- | -- | 264 | 260 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
108-67-8 | 1,3,5-Trimethylbenzene |  | HI3 | -- | -- | 60 | 60 | -- | -- | 264 | 260 | -- | -- | 264 | 260 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
51-79-6 | Urethane (Ethyl carbamate) | g | -- | 0.0020284 | 0.002 | -- | -- | 0.021346 | 0.021 | -- | -- | 0.041379 | 0.041 | -- | -- | -- | -- | 1 | 1 | Y | 1 | 1 | 1 | 1
7440-62-2 | Vanadium (fume or dust) |  | HI3 | -- | -- | 0.1 | 0.1 | -- | -- | 0.44 | 0.44 | -- | -- | 0.44 | 0.44 | 0.8 | 0.8 | 1 | 1 | N | 1 | 1 | 1 | 1
1314-62-1 | Vanadium pentoxide |  | HI3 | 0.00012048 | 0.00012 | 0.007 | 0.007 | 0.0031325 | 0.0031 | 0.0308 | 0.031 | 0.0014458 | 0.0014 | 0.0308 | 0.031 | 30 | 30 | 1 | 1 | N | 1 | 1 | 1 | 1
108-05-4 | Vinyl acetate |  | HI3 | -- | -- | 200 | 200 | -- | -- | 880 | 880 | -- | -- | 880 | 880 | 200 | 200 | 1 | 1 | N | 1 | 1 | 1 | 1
593-60-2 | Vinyl bromide |  | HI5 | -- | -- | 3 | 3 | -- | -- | 13.2 | 13 | -- | -- | 13.2 | 13 | -- | -- | 1 | 1 | N | 1 | 1 | 1 | 1
75-01-4 | Vinyl chloride | g, k | HI3 | 0.11364 | 0.11 | 100 | 100 | 0.21886 | 0.22 | 440 | 440 | 2.7273 | 2.7 | 440 | 440 | 1300 | 1300 | 1 | 1 | Y | 1 | 1 | 1 | 1
75-35-4 | Vinylidene chloride |  | HI3 | -- | -- | 200 | 200 | -- | -- | 880 | 880 | -- | -- | 880 | 880 | 200 | 200 | 1 | 1 | N | 1 | 1 | 1 | 1
1330-20-7 | Xylene (mixture), including m-xylene, o-xylene, p-xylene |  | HI3 | -- | -- | 220 | 220 | -- | -- | 968 | 970 | -- | -- | 968 | 970 | 8700 | 8700 | 1 | 1 | N | 1 | 1 | 1 | 1
Notes:
(a) RBCs calculated using the following formulas: | [18 empty] | 261
Residential RBC for cancer effects = residRBCc (µg/m3) = TRVc / ELAFr / MPAFrc
Residential RBC for noncancer effects = residRBCnc (µg/m3) = TRVnc / MPAFrnc
Nonresidential child RBC for cancer effects = nrchildRBCc (µg/m3) = TRVc * childNRAFc / ELAFnr / MPAFnrc
Nonresidential child RBC for noncancer effects = nrchildRBCnc (µg/m3) = TRVnc * childNRAFnc / MPAFnrnc
Nonresidential worker RBC for cancer effects = workerRBCc (µg/m3) = TRVc * workerNRAFc / MPAFnrc
Nonresidential worker RBC for noncancer effects = workerRBCnc (µg/m3) = TRVnc * workerNRAFnc / MPAFnrnc
Acute RBC (µg/m3) = TRVa
TRVc = Toxicity reference value, cancer (µg/m3)
TRVnc = Toxicity reference value, noncancer (µg/m3)
TRVa = Toxicity reference value, acute (µg/m3)
ELAFr = early-life adjustment factor, residential (unitless)
ELAFr = early-life adjustment factor, nonresidential (unitless)
MPAFrc = multipathway adjustment factor, resident cancer (unitless)
MPAFrnc = multipathway adjustment factor, resident noncancer (unitless)
MPAFnrc = multipathway adjustment factor, nonresident cancer (unitless)
MPAFnrnc = multipathway adjustment factor, nonresident noncancer (unitless)
childNRAFc = Nonresident adjustment factor, child cancer (26) (unitless) = (24 hr/day / 8 hr/day) * (365 days/yr / 250 days/yr) * (70 years / 12 years)
childNRAFnc = Nonresident adjustment factor, child noncancer (4.4) (unitless) = (24 hr/day / 8 hr/day) * (365 days/yr / 250 days/yr)
workerNRAFc = Nonresident adjustment factor, worker cancer (12) (unitless) = (24 hr/day / 8 hr/day) * (365 days/yr / 250 days/yr) * (70 yr / 25 yr)
workerNRAFnc = Nonresident adjustment factor, worker noncancer (4.4) (unitless) = (24 hr/day / 8 hr/day) * (365 days/yr / 250 days/yr)
(b) CAS# = Chemical Abstracts Service number
(c) Chronic RBCs include factors for multipathway risk. Multipathway adjustment factors are provided in Table B-1 of Draft Recommended Procedures for Conducting Toxic Air Contaminant Health Risk Assessments.
(d) The RBCs presented for chromium are applicable to hexavalent chromium. In the absence of data indicating otherwise, assume that any total chromium (i.e., unspeciated) that is measured or modeled is entirely in the hexavalent form.
Determine, based on information about the source of emissions, whether hexavalent chromium is emitted in aerosol or particulate form, and apply the corresponding RBC
Because there are no RBCs for trivalent chromium, a source determined to be emitting only trivalent chromium cannot be shown to pose an unacceptable risk, so the risk in this case will be considered acceptable.
(e) DDT RBCs apply to the sum of DDT, DDE, and DDD compounds.
(f) As recommended by the ATSAC in 2015, the two categories of nickel compounds contain the following specific nickel compounds:
Soluble nickel compounds are considered to be emitted mainly in aerosol form, to be less potent carcinogens than insoluble nickel compounds, and include nickel acetate, nickel chloride, nickel carbonate, nickel hydroxide, nickelocene, nickel sulfate, nickel sulfate hexahydrate, nickel nitrate hexahydrate, nickel carbonate hydroxide.
Insoluble nickel compounds are considered to be emitted mainly in particulate form, to be more potent carcinogens than soluble nickel compounds, and to include nickel subsulfide, nickel oxide, nickel sulfide, nickel metal.
(g) RBCs adjusted to protect early-life exposure to infants and children because chemical is carcinogenic by a mutagenic mode of action.
See Table B-1 of Draft Recommended Procedures for Conducting Toxic Air Contaminant Health Risk Assessments.
(h ) RBCs apply to octabrominated diphenyl ethers (CAS# 32536-52-0) and pentabrominated diphenyl ethers (CAS# 32534-81-9), including BDE-99.
(i) RBCs for asbestos and refractory ceramic fibers are in units of fibers/cm3.
(j) Chlorinated paraffins of average chain length of C12, approximately 60% chlorine by weight.
(k) DEQ followed the ATSAC recommendation to develop a vinyl chloride TRV that already includes early-life exposure. For the RBC calculations, DEQ applied the adjustment factors from
Table B-1 of Draft Recommended Procedures for Conducting Toxic Air Contaminant Health Risk Assessments to a TRV of 0.2 μg/m3, not the adult/child TRV of 0.1 μg/m3.
(l) Inorganic chemicals are designated with "and compounds" to indicate that the RBC applies to the sum of all forms of the chemical, expressed as the inorganic element.
|  |  |  | Parameter | Value
Early-life adjustment factor, residential |  |  |  | ELAFr | 1.7 | unitless | Rounded | =(2yr*10 + 14yr*3 + 54yr*1)/70yr
Early-life adjustment factor, non-residential |  |  |  | ELAFnr | 4.2 | unitless | Rounded | =(2yr*10 + 10yr*3)/12yr
child NonResident Adjustment Factor, cancer |  |  |  | childNRAFc | 26 | unitless | Rounded | =24hr/8hr * 365d/250d * 70yr/12yr
child NonResident Adjustment Factor, noncancer |  |  |  | childNRAFnc | 4.4 | unitless | Rounded | =24hr/8hr * 365d/250d
worker NonResident Adjustment Factor, cancer |  |  |  | workNRAFc | 12 | unitless | Rounded | =24hr/8hr * 365d/250d * 70yr/25yr
worker NonResident Adjustment Factor, noncancer |  |  |  | workNRAFnc | 4.4 | unitless | Rounded | =24hr/8hr * 365d/250d
Note on E253: POULSEN Mike: Calculated using ELAF developed by applying ADAFs to one of three toxic endpoints for TCE.
Note on I253: POULSEN Mike: Calculated using ELAF developed by applying ADAFs to one of three toxic endpoints for TCE.
Note on M253: POULSEN Mike: Calculated using ELAF developed by applying ADAFs to one of three toxic endpoints for TCE.
Note on E265: POULSEN Mike: Includes 2*TRV to remove early-life consideration already included in ABC. Calculated using ELAF specific to vinyl chloride.
Note on I265: POULSEN Mike: Includes 2*TRV to remove early-life consideration already included in ABC. Calculated using ELAF specific to vinyl chloride.
Note on M265: POULSEN Mike: Includes 2*TRV to remove early-life consideration already included in ABC. Calculated using ELAF specific to vinyl chloride.