## Input_Cooling Towers
Toxics Emissions Sub-Unit (TESU) ID (1) |  |  | Site | Building | Peak Recirculation Rate (2) (gpm) | Drift Loss of Circulating Water (2) (%)
RAC4-CT114-1 |  |  | Ronler Acres | CUB4 | 10722 | 0.0005
RAC4-CT114-2 |  |  | Ronler Acres | CUB4 | 10722 | 0.0005
RAC4-CT114-3 |  |  | Ronler Acres | CUB4 | 10722 | 0.0005
RAC4-CT114-4 |  |  | Ronler Acres | CUB4 | 10722 | 0.0005
RAC4-CT114-5 |  |  | Ronler Acres | CUB4 | 10722 | 0.0005
RAC4-CT114-6 |  |  | Ronler Acres | CUB4 | 10722 | 0.0005
RAC4-CT114-7 |  |  | Ronler Acres | CUB4 | 10722 | 0.0005
RAC4-CT114-8 |  |  | Ronler Acres | CUB4 | 10722 | 0.0005
RAC4-CT114-9 |  |  | Ronler Acres | CUB4 | 10722 | 0.0005
RAC4-CT114-10 |  |  | Ronler Acres | CUB4 | 10722 | 0.0005
RAC4-CT114-11 |  |  | Ronler Acres | CUB4 | 10722 | 0.0005
RAC4-CT114-12 |  |  | Ronler Acres | CUB4 | 10722 | 0.0005
RAC4-CT114-13 |  |  | Ronler Acres | CUB4 | 10722 | 0.0005
RAC4-CT114-14 |  |  | Ronler Acres | CUB4 | 10722 | 0.0005
RAC4-CT114-15 |  |  | Ronler Acres | CUB4 | 10722 | 0.0005
RAC4-CT114-16 |  |  | Ronler Acres | CUB4 | 10722 | 0.0005
RAC4-CT114-17 |  |  | Ronler Acres | CUB4X | 10722 | 0.0005
RAC4-CT114-18 |  |  | Ronler Acres | CUB4X | 10722 | 0.0005
RAC4-CT114-19 |  |  | Ronler Acres | CUB4X | 10722 | 0.0005
RAC4-CT114-20 |  |  | Ronler Acres | CUB4X | 10722 | 0.0005
RAC5-CT115-1 |  |  | Ronler Acres | CUB5 | 10722 | 0.0005
RAC5-CT115-2 |  |  | Ronler Acres | CUB5 | 10722 | 0.0005
RAC5-CT115-3 |  |  | Ronler Acres | CUB5 | 10722 | 0.0005
RAC5-CT115-4 |  |  | Ronler Acres | CUB5 | 10722 | 0.0005
RAC5-CT115-5 |  |  | Ronler Acres | CUB5 | 10722 | 0.0005
RAC5-CT115-6 |  |  | Ronler Acres | CUB5 | 10722 | 0.0005
RAC5-CT115-7 |  |  | Ronler Acres | CUB5 | 10722 | 0.0005
RAC5-CT115-8 |  |  | Ronler Acres | CUB5 | 10722 | 0.0005
RA5-CT114-1 |  |  | Ronler Acres | RA5 | 10722 | 0.0005
RA6-CT114-1 |  |  | Ronler Acres | RA6 | 10722 | 0.0005
RAC5-CT115-9 |  | (3) | Ronler Acres | CUB5 | 10722 | 0.0005
RAC5-CT115-10 |  | (3) | Ronler Acres | CUB5 | 10722 | 0.0005
RAC5-CT115-11 |  | (3) | Ronler Acres | CUB5 | 10722 | 0.0005
RAC5-CT115-12 |  | (3) | Ronler Acres | CUB5 | 10722 | 0.0005
RAC5-CT115-13 |  | (3) | Ronler Acres | CUB5 | 10722 | 0.0005
RAC5-CT115-14 |  | (3) | Ronler Acres | CUB5 | 10722 | 0.0005
RAC5-CT115-15 |  | (3) | Ronler Acres | CUB5 | 10722 | 0.0005
RAC5-CT115-16 |  | (3) | Ronler Acres | CUB5 | 10722 | 0.0005
RAC5-CT115-17 |  | (3) | Ronler Acres | CUB5 | 10722 | 0.0005
CT-114-1-210 |  |  | Ronler Acres | CUB3 | 7700 | 0.001
CT-114-2-210 |  |  | Ronler Acres | CUB3 | 7700 | 0.001
CT-114-3-210 |  |  | Ronler Acres | CUB3 | 7700 | 0.001
CT-114-4-210 |  |  | Ronler Acres | CUB3 | 7700 | 0.001
CT-114-5-210 |  |  | Ronler Acres | CUB3 | 7700 | 0.001
CUB3-CT114-21-10 |  |  | Ronler Acres | CUB3X | 7700 | 0.001
CUB3-CT114-22-10 |  |  | Ronler Acres | CUB3X | 7700 | 0.001
CUB3-CT114-23-10 |  |  | Ronler Acres | CUB3X | 7700 | 0.001
CUB3-CT114-24-10 |  |  | Ronler Acres | CUB3X | 7700 | 0.001
CUB3-CT114-25-10 |  |  | Ronler Acres | CUB3X | 7700 | 0.001
CUB3-CT114-26-10 |  |  | Ronler Acres | CUB3X | 7700 | 0.001
RP1-CT114-1-200 |  |  | Ronler Acres | RP1 | 3844 | 0.001
RP1-CT114-2-200 |  |  | Ronler Acres | RP1 | 3844 | 0.001
RP1-CT114-3-00 |  | (3) | Ronler Acres | RP1 | 3844 | 0.001
CUB2-CT114-1-210 |  |  | Ronler Acres | CUB2 | 8000 | 0.001
CUB2-CT114-2-210 |  |  | Ronler Acres | CUB2 | 8000 | 0.001
CUB2-CT114-3-210 |  |  | Ronler Acres | CUB2 | 8000 | 0.001
CUB2-CT114-4-210 |  |  | Ronler Acres | CUB2 | 8000 | 0.001
CUB2-CT114-5-210 |  |  | Ronler Acres | CUB2 | 8000 | 0.001
CUB2-CT114-6-210 |  |  | Ronler Acres | CUB2 | 8000 | 0.001
CUB2-CT114-7-210 |  |  | Ronler Acres | CUB2 | 8000 | 0.001
CUB2-CT114-8-210 |  |  | Ronler Acres | CUB2 | 8000 | 0.001
CUB2-CT114-9-210 |  |  | Ronler Acres | CUB2 | 8000 | 0.001
CUB2-CT114-10-210 |  | (3) | Ronler Acres | CUB2 | 8000 | 0.001
CUB2-CT114-11-10 |  |  | Ronler Acres | CUB2X | 8000 | 0.001
CUB2-CT114-12-10 |  |  | Ronler Acres | CUB2X | 8000 | 0.001
CUB2-CT114-13-10 |  |  | Ronler Acres | CUB2X | 8000 | 0.001
CUB2-CT114-14-10 |  | (3) | Ronler Acres | CUB2X | 8000 | 0.001
F20-CT114-1-210 |  |  | Ronler Acres | CUB1 | 8000 | 0.001
F20-CT114-2-210 |  |  | Ronler Acres | CUB1 | 8000 | 0.001
F20-CT114-3-210 |  |  | Ronler Acres | CUB1 | 8000 | 0.001
F20-CT114-4-210 |  |  | Ronler Acres | CUB1 | 8000 | 0.001
F20-CT114-5-210 |  |  | Ronler Acres | CUB1 | 8000 | 0.001
F20-CT114-6-210 |  |  | Ronler Acres | CUB1 | 8000 | 0.001
F20-CT114-7-210 |  |  | Ronler Acres | CUB1 | 8000 | 0.001
F20-CT114-8-210 |  |  | Ronler Acres | CUB1 | 8000 | 0.001
F20-CT114-9-210 |  |  | Ronler Acres | CUB1 | 8000 | 0.001
F20-CT114-10-210 |  | (3) | Ronler Acres | CUB1 | 8000 | 0.001
F20-CT114-11-210 |  | (3) | Ronler Acres | CUB1 | 8000 | 0.001
N2-CT114-1 |  |  | Ronler Acres | N2 Plant | 10220 | 0.001
N2-CT114-2 |  |  | Ronler Acres | N2 Plant | 14090 | 0.001
N2-CT114-3 |  |  | Ronler Acres | N2 Plant | 14090 | 0.001
RACB3-CT-114-1-35 |  |  | Ronler Acres | PCB-1 | 7700 | 0.001
RACB3-CT-114-2-35 |  |  | Ronler Acres | PCB-1 | 7700 | 0.001
RACB3-CT-114-3-35 |  |  | Ronler Acres | PCB-1 | 7700 | 0.001
AL4-CHW-CT2 |  |  | Aloha | AL4 | 1500 | 0.001
AL4-CHW-CT3 |  |  | Aloha | AL4 | 1500 | 0.001
F15-CT29-1-1 |  |  | Aloha | F15 | 4680 | 0.001
F15-CT29-1-2 |  |  | Aloha | F15 | 4680 | 0.001
F15-CT29-1-3 |  |  | Aloha | F15 | 4680 | 0.001
F15-CT29-1-4 |  |  | Aloha | F15 | 4680 | 0.001
F15-CT29-1-5 |  |  | Aloha | F15 | 4680 | 0.001
F15-CT29-1-6-1 |  |  | Aloha | F15 | 840 | 0.001
References
(1) | Only those cooling towers dosed with chemicals listed in OAR 340-245-8040 were included.
(2) | Information provided by Intel Corporation based on vendor specifications.
(3) | Equipment is planned for future use.

## COOL_Ronler
TESU ID |  | Drift Loss of Circulating Water (1) (%) | Peak Recirculation Flow Rate (1) (gpm) | Average Recirculation Flow Rate (1) (gpm) | Drift Loss |  | TAC Concentration (2) (ppm) |  |  |  |  | Emissions Estimate (5)
[12 empty] | Glutaraldehyde |  | Methanol |  | Aluminum |  | Phosphoric Acid |  | Sulfuric Acid
[12 empty] | 111-30-8 |  | 67-56-1 |  | 7429-90-5 |  | 7664-38-2 |  | 7664-93-9
[5 empty] | Daily (a) (lb/day) | Annual (b) (lb/yr) | Glutaraldehyde | Methanol | Aluminum (e) | Phosphoric Acid | Sulfuric Acid | Daily (c) (lb/day) | Annual (d) (lb/yr) | Daily (c) (lb/day) | Annual (d) (lb/yr) | Daily (d) (lb/day) | Annual (e) (lb/yr) | Daily (c) (lb/day) | Annual (d) (lb/yr) | Daily (c) (lb/day) | Annual (d) (lb/yr)
RAC4-CT114-1 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | 0.3 | 0.3 | -- | -- | -- | -- | 1.0663e-06 | 0.0001946 | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-2 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | 0.3 | 0.3 | -- | -- | -- | -- | 1.0663e-06 | 0.0001946 | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-3 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | 0.3 | 0.3 | -- | -- | -- | -- | 1.0663e-06 | 0.0001946 | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-4 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | 0.3 | 0.3 | -- | -- | -- | -- | 1.0663e-06 | 0.0001946 | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-5 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | 0.3 | 0.3 | -- | -- | -- | -- | 1.0663e-06 | 0.0001946 | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-6 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | 0.3 | 0.3 | -- | -- | -- | -- | 1.0663e-06 | 0.0001946 | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-7 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | 0.3 | 0.3 | -- | -- | -- | -- | 1.0663e-06 | 0.0001946 | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-8 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | 0.3 | 0.3 | -- | -- | -- | -- | 1.0663e-06 | 0.0001946 | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-9 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | 0.3 | 0.3 | -- | -- | -- | -- | 1.0663e-06 | 0.0001946 | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-10 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | 0.3 | 0.3 | -- | -- | -- | -- | 1.0663e-06 | 0.0001946 | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-11 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | 0.3 | 0.3 | -- | -- | -- | -- | 1.0663e-06 | 0.0001946 | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-12 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | 0.3 | 0.3 | -- | -- | -- | -- | 1.0663e-06 | 0.0001946 | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-13 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | 0.3 | 0.3 | -- | -- | -- | -- | 1.0663e-06 | 0.0001946 | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-14 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | 0.3 | 0.3 | -- | -- | -- | -- | 1.0663e-06 | 0.0001946 | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-15 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | 0.3 | 0.3 | -- | -- | -- | -- | 1.0663e-06 | 0.0001946 | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-16 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | 0.3 | 0.3 | -- | -- | -- | -- | 1.0663e-06 | 0.0001946 | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-17 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | 0.3 | 0.3 | -- | -- | -- | -- | 1.0663e-06 | 0.0001946 | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-18 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | 0.3 | 0.3 | -- | -- | -- | -- | 1.0663e-06 | 0.0001946 | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-19 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | 0.3 | 0.3 | -- | -- | -- | -- | 1.0663e-06 | 0.0001946 | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-20 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | 0.3 | 0.3 | -- | -- | -- | -- | 1.0663e-06 | 0.0001946 | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC5-CT115-1 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019484 | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022894 | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-2 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019484 | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022894 | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-3 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019484 | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022894 | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-4 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019484 | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022894 | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-5 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019484 | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022894 | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-6 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019484 | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022894 | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-7 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019484 | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022894 | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-8 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019484 | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022894 | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-9 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019484 | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022894 | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-10 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019484 | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022894 | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-11 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019484 | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022894 | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-12 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019484 | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022894 | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-13 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019484 | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022894 | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-14 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019484 | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022894 | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-15 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019484 | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022894 | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-16 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019484 | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022894 | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-17 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019484 | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022894 | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RA5-CT114-1 | (6) | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.033123 | 4.5 | 4.5 | -- | -- | -- | -- | 2.1326e-05 | 0.0038919 | 0.0028973 | 0.52875 | 0.0028973 | 0.52875
RA6-CT114-1 | (6) | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.033123 | 4.5 | 4.5 | -- | -- | -- | -- | 2.1326e-05 | 0.0038919 | 0.0028973 | 0.52875 | 0.0028973 | 0.52875
CT-114-1-210 |  | 0.001 | 7700 | 3850 | 924.7392 | 168764.904 | -- | -- | 0.0030112 | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.7845e-06 | 0.00050818 | 0.00042559 | 0.07767 | 0.00019861 | 0.036246
CT-114-2-210 |  | 0.001 | 7700 | 3850 | 924.7392 | 168764.904 | -- | -- | 0.0030112 | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.7845e-06 | 0.00050818 | 0.00042559 | 0.07767 | 0.00019861 | 0.036246
CT-114-3-210 |  | 0.001 | 7700 | 3850 | 924.7392 | 168764.904 | -- | -- | 0.0030112 | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.7845e-06 | 0.00050818 | 0.00042559 | 0.07767 | 0.00019861 | 0.036246
CT-114-4-210 |  | 0.001 | 7700 | 3850 | 924.7392 | 168764.904 | -- | -- | 0.0030112 | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.7845e-06 | 0.00050818 | 0.00042559 | 0.07767 | 0.00019861 | 0.036246
CT-114-5-210 |  | 0.001 | 7700 | 3850 | 924.7392 | 168764.904 | -- | -- | 0.0030112 | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.7845e-06 | 0.00050818 | 0.00042559 | 0.07767 | 0.00019861 | 0.036246
CUB3-CT114-21-10 |  | 0.001 | 7700 | 3850 | 924.7392 | 168764.904 | -- | -- | 0.0030112 | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.7845e-06 | 0.00050818 | 0.00042559 | 0.07767 | 0.00019861 | 0.036246
CUB3-CT114-22-10 |  | 0.001 | 7700 | 3850 | 924.7392 | 168764.904 | -- | -- | 0.0030112 | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.7845e-06 | 0.00050818 | 0.00042559 | 0.07767 | 0.00019861 | 0.036246
CUB3-CT114-23-10 |  | 0.001 | 7700 | 3850 | 924.7392 | 168764.904 | -- | -- | 0.0030112 | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.7845e-06 | 0.00050818 | 0.00042559 | 0.07767 | 0.00019861 | 0.036246
CUB3-CT114-24-10 |  | 0.001 | 7700 | 3850 | 924.7392 | 168764.904 | -- | -- | 0.0030112 | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.7845e-06 | 0.00050818 | 0.00042559 | 0.07767 | 0.00019861 | 0.036246
CUB3-CT114-25-10 |  | 0.001 | 7700 | 3850 | 924.7392 | 168764.904 | -- | -- | 0.0030112 | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.7845e-06 | 0.00050818 | 0.00042559 | 0.07767 | 0.00019861 | 0.036246
CUB3-CT114-26-10 |  | 0.001 | 7700 | 3850 | 924.7392 | 168764.904 | -- | -- | 0.0030112 | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.7845e-06 | 0.00050818 | 0.00042559 | 0.07767 | 0.00019861 | 0.036246
RP1-CT114-1-200 |  | 0.001 | 3844 | 1922 | 461.649 | 84250.9469 | 25 | 0.275 | 0.011041 | 1.6875 | 0.7875 | 0.011541 | 2.1063 | 0.00012695 | 0.023169 | 5.097e-06 | 0.00093021 | 0.00077903 | 0.14217 | 0.00036355 | 0.066348
RP1-CT114-2-200 |  | 0.001 | 3844 | 1922 | 461.649 | 84250.9469 | 25 | 0.275 | 0.011041 | 1.6875 | 0.7875 | 0.011541 | 2.1063 | 0.00012695 | 0.023169 | 5.097e-06 | 0.00093021 | 0.00077903 | 0.14217 | 0.00036355 | 0.066348
RP1-CT114-3-00 |  | 0.001 | 3844 | 1922 | 461.649 | 84250.9469 | 25 | 0.275 | 0.011041 | 1.6875 | 0.7875 | 0.011541 | 2.1063 | 0.00012695 | 0.023169 | 5.097e-06 | 0.00093021 | 0.00077903 | 0.14217 | 0.00036355 | 0.066348
CUB2-CT114-1-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | 7.5 | 0.0825 | 0.0033123 | 0.50625 | 0.23625 | 0.0072058 | 1.3151 | 7.9263e-05 | 0.014466 | 3.1823e-06 | 0.00058077 | 0.00048639 | 0.088766 | 0.00022698 | 0.041424
CUB2-CT114-2-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | 7.5 | 0.0825 | 0.0033123 | 0.50625 | 0.23625 | 0.0072058 | 1.3151 | 7.9263e-05 | 0.014466 | 3.1823e-06 | 0.00058077 | 0.00048639 | 0.088766 | 0.00022698 | 0.041424
CUB2-CT114-3-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | 7.5 | 0.0825 | 0.0033123 | 0.50625 | 0.23625 | 0.0072058 | 1.3151 | 7.9263e-05 | 0.014466 | 3.1823e-06 | 0.00058077 | 0.00048639 | 0.088766 | 0.00022698 | 0.041424
CUB2-CT114-4-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | 7.5 | 0.0825 | 0.0033123 | 0.50625 | 0.23625 | 0.0072058 | 1.3151 | 7.9263e-05 | 0.014466 | 3.1823e-06 | 0.00058077 | 0.00048639 | 0.088766 | 0.00022698 | 0.041424
CUB2-CT114-5-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | 7.5 | 0.0825 | 0.0033123 | 0.50625 | 0.23625 | 0.0072058 | 1.3151 | 7.9263e-05 | 0.014466 | 3.1823e-06 | 0.00058077 | 0.00048639 | 0.088766 | 0.00022698 | 0.041424
CUB2-CT114-6-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | 7.5 | 0.0825 | 0.0033123 | 0.50625 | 0.23625 | 0.0072058 | 1.3151 | 7.9263e-05 | 0.014466 | 3.1823e-06 | 0.00058077 | 0.00048639 | 0.088766 | 0.00022698 | 0.041424
CUB2-CT114-7-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | 7.5 | 0.0825 | 0.0033123 | 0.50625 | 0.23625 | 0.0072058 | 1.3151 | 7.9263e-05 | 0.014466 | 3.1823e-06 | 0.00058077 | 0.00048639 | 0.088766 | 0.00022698 | 0.041424
CUB2-CT114-8-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | 7.5 | 0.0825 | 0.0033123 | 0.50625 | 0.23625 | 0.0072058 | 1.3151 | 7.9263e-05 | 0.014466 | 3.1823e-06 | 0.00058077 | 0.00048639 | 0.088766 | 0.00022698 | 0.041424
CUB2-CT114-9-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | 7.5 | 0.0825 | 0.0033123 | 0.50625 | 0.23625 | 0.0072058 | 1.3151 | 7.9263e-05 | 0.014466 | 3.1823e-06 | 0.00058077 | 0.00048639 | 0.088766 | 0.00022698 | 0.041424
CUB2-CT114-10-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | 7.5 | 0.0825 | 0.0033123 | 0.50625 | 0.23625 | 0.0072058 | 1.3151 | 7.9263e-05 | 0.014466 | 3.1823e-06 | 0.00058077 | 0.00048639 | 0.088766 | 0.00022698 | 0.041424
CUB2-CT114-11-10 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | 18.75 | 0.20625 | 0.0082807 | 1.2656 | 0.59063 | 0.018014 | 3.2876 | 0.00019816 | 0.036164 | 7.9558e-06 | 0.0014519 | 0.001216 | 0.22191 | 0.00056745 | 0.10356
CUB2-CT114-12-10 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | 18.75 | 0.20625 | 0.0082807 | 1.2656 | 0.59063 | 0.018014 | 3.2876 | 0.00019816 | 0.036164 | 7.9558e-06 | 0.0014519 | 0.001216 | 0.22191 | 0.00056745 | 0.10356
CUB2-CT114-13-10 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | 18.75 | 0.20625 | 0.0082807 | 1.2656 | 0.59063 | 0.018014 | 3.2876 | 0.00019816 | 0.036164 | 7.9558e-06 | 0.0014519 | 0.001216 | 0.22191 | 0.00056745 | 0.10356
CUB2-CT114-14-10 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | 18.75 | 0.20625 | 0.0082807 | 1.2656 | 0.59063 | 0.018014 | 3.2876 | 0.00019816 | 0.036164 | 7.9558e-06 | 0.0014519 | 0.001216 | 0.22191 | 0.00056745 | 0.10356
F20-CT114-1-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | -- | -- | 0.0030112 | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.893e-06 | 0.00052798 | 0.00044217 | 0.080696 | 0.00020635 | 0.037658
F20-CT114-2-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | -- | -- | 0.0030112 | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.893e-06 | 0.00052798 | 0.00044217 | 0.080696 | 0.00020635 | 0.037658
F20-CT114-3-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | -- | -- | 0.0030112 | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.893e-06 | 0.00052798 | 0.00044217 | 0.080696 | 0.00020635 | 0.037658
F20-CT114-4-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | -- | -- | 0.0030112 | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.893e-06 | 0.00052798 | 0.00044217 | 0.080696 | 0.00020635 | 0.037658
F20-CT114-5-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | -- | -- | 0.0030112 | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.893e-06 | 0.00052798 | 0.00044217 | 0.080696 | 0.00020635 | 0.037658
F20-CT114-6-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | -- | -- | 0.0030112 | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.893e-06 | 0.00052798 | 0.00044217 | 0.080696 | 0.00020635 | 0.037658
F20-CT114-7-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | -- | -- | 0.0030112 | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.893e-06 | 0.00052798 | 0.00044217 | 0.080696 | 0.00020635 | 0.037658
F20-CT114-8-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | -- | -- | 0.0030112 | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.893e-06 | 0.00052798 | 0.00044217 | 0.080696 | 0.00020635 | 0.037658
F20-CT114-9-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | -- | -- | 0.0030112 | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.893e-06 | 0.00052798 | 0.00044217 | 0.080696 | 0.00020635 | 0.037658
F20-CT114-10-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | -- | -- | 0.0030112 | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.893e-06 | 0.00052798 | 0.00044217 | 0.080696 | 0.00020635 | 0.037658
F20-CT114-11-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | -- | -- | 0.0030112 | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.893e-06 | 0.00052798 | 0.00044217 | 0.080696 | 0.00020635 | 0.037658
N2-CT114-1 |  | 0.001 | 10220 | 5110 | 1227.3811 | 223997.0544 | -- | -- | -- | 4.05 | 4.05 | -- | -- | -- | -- | -- | -- | 0.0049709 | 0.90719 | 0.0049709 | 0.90719
N2-CT114-2 |  | 0.001 | 14090 | 7045 | 1692.1526 | 308817.8568 | -- | -- | -- | 4.05 | 4.05 | -- | -- | -- | -- | -- | -- | 0.0068532 | 1.2507 | 0.0068532 | 1.2507
N2-CT114-3 |  | 0.001 | 14090 | 7045 | 1692.1526 | 308817.8568 | -- | -- | -- | 4.05 | 4.05 | -- | -- | -- | -- | -- | -- | 0.0068532 | 1.2507 | 0.0068532 | 1.2507
RACB3-CT-114-1-35 |  | 0.001 | 7700 | 3850 | 924.7392 | 168764.904 | 25 | 0.275 | 0.011041 | 1.6875 | 0.7875 | 0.023118 | 4.2191 | 0.0002543 | 0.04641 | 1.021e-05 | 0.0018633 | 0.0015605 | 0.28479 | 0.00072823 | 0.1329
RACB3-CT-114-2-35 |  | 0.001 | 7700 | 3850 | 924.7392 | 168764.904 | 25 | 0.275 | 0.011041 | 1.6875 | 0.7875 | 0.023118 | 4.2191 | 0.0002543 | 0.04641 | 1.021e-05 | 0.0018633 | 0.0015605 | 0.28479 | 0.00072823 | 0.1329
RACB3-CT-114-3-35 |  | 0.001 | 7700 | 3850 | 924.7392 | 168764.904 | 25 | 0.275 | 0.011041 | 1.6875 | 0.7875 | 0.023118 | 4.2191 | 0.0002543 | 0.04641 | 1.021e-05 | 0.0018633 | 0.0015605 | 0.28479 | 0.00072823 | 0.1329
Total | [11 empty] | 0.24809 | 45.2772 | 0.002729 | 0.49805 | 0.00025732 | 0.046961 | 0.057524 | 10.4981 | 0.043502 | 7.939
Notes
TAC = Toxic Air Contaminant
(a) | Daily drift loss (lb/day) = (total water circulation rate [gpm]) x (density of water [lb/gal]) x (drift loss percent of circulating water [%] / 100) x (60 min/hr) x (daily hours of operation [hrs/day])
[6 empty] | Density of water (lb/gal) = | 8.34
[6 empty] | Daily hours of operation (hrs/day) = | 24 | (3)
(b) | Annual drift loss (lb/yr) = (daily drift loss [lb/day]) x (annual days of operation [days/yr])
[6 empty] | Annual days of operation (days/yr) = | 365 | (3)
(c) | Daily emissions estimate (lb/day) = (daily drift loss [lb/day]) x (concentration [ppm] / 1,000,000) | [6 empty] | (4)
(d) | Annual emissions estimate (lb/yr) = (annual drift loss [lb/yr]) x (concentration [ppm] / 1,000,000) | [6 empty] | (4)
(e) | Aluminum concentration (ppm) = (aluminum distearate concentration [ppm]) x (molecular weight of aluminum [g/mol]) / (molecular weight of aluminum distearate [g/mol])
[6 empty] | Molecular weight of aluminum (g/mol) = | 26.98
[6 empty] | Molecular weight of aluminum distearate (g/mol) = | 610.91
References
(1) | See Input Cooling Tower for Rates and Parameters
(2) | Information provided by Intel Corporation. TAC concentration Is based on dosage rates and TAC percentage in SDS.
(3) | Based on continuous operation.
(4) | Assumes the composition of the drift loss is same as the cooling tower makeup water.
(5) | Assumes that dosing frequency is daily
(6) | Dosing rates for RA5 and RA6 assumed to be similar to RAC5

## COOL_Aloha
Source |  | Drift Loss of Circulating Water (1) (%) | Peak Recirculation Flow Rate (1) (gpm) | Average Recirculation Flow Rate (1) (gpm) | Drift Loss |  | TAC Concentration (2) (ppm) |  | Emissions Estimate (5)
[9 empty] | Phosphoric Acid |  | Sulfuric Acid
[9 empty] | 7664-38-2 |  | 7664-93-9
[5 empty] | Daily (a) (lb/day) | Annual (b) (lb/yr) | Phosphoric Acid | Sulfuric Acid | Daily (c) (lb/day) | Annual (d) (lb/yr) | Daily (c) (lb/day) | Annual (d) (lb/yr)
AL4-CHW-CT2 |  | 0.001 | 1500 | 750 | 180.144 | 65752.56 | 2.5312 | 1.1813 | 0.00045599 | 0.16644 | 0.0002128 | 0.07767
AL4-CHW-CT3 |  | 0.001 | 1500 | 750 | 180.144 | 65752.56 | 2.5312 | 1.1813 | 0.00045599 | 0.16644 | 0.0002128 | 0.07767
F15-CT29-1-1 |  | 0.001 | 4680 | 2340 | 562.0493 | 205147.9872 | 1.0125 | 0.4725 | 0.00056907 | 0.20771 | 0.00026557 | 0.096932
F15-CT29-1-2 |  | 0.001 | 4680 | 2340 | 562.0493 | 205147.9872 | 1.0125 | 0.4725 | 0.00056907 | 0.20771 | 0.00026557 | 0.096932
F15-CT29-1-3 |  | 0.001 | 4680 | 2340 | 562.0493 | 205147.9872 | 1.0125 | 0.4725 | 0.00056907 | 0.20771 | 0.00026557 | 0.096932
F15-CT29-1-4 |  | 0.001 | 4680 | 2340 | 562.0493 | 205147.9872 | 1.0125 | 0.4725 | 0.00056907 | 0.20771 | 0.00026557 | 0.096932
F15-CT29-1-5 |  | 0.001 | 4680 | 2340 | 562.0493 | 205147.9872 | 1.0125 | 0.4725 | 0.00056907 | 0.20771 | 0.00026557 | 0.096932
F15-CT29-1-6-1 |  | 0.001 | 840 | 420 | 100.8806 | 36821.4336 | 5.0625 | 2.3625 | 0.00051071 | 0.18641 | 0.00023833 | 0.086991
Total | [8 empty] | 0.0042681 | 1.5578 | 0.0019918 | 0.72699
Notes
TAC = Toxic Air Contaminant
(a) | Daily drift loss (lb/day) = (total water circulation rate [gpm]) x (density of water [lb/gal]) x (drift loss percent of circulating water [%] / 100) x (60 min/hr) x (daily hours of operation [hrs/day])
[6 empty] | Density of water (lb/gal) = | 8.34
[6 empty] | Daily hours of operation (hrs/day) = | 24 | (3)
(b) | Annual drift loss (lb/yr) = (daily drift loss [lb/day]) x (annual days of operation [days/yr])
[6 empty] | Annual days of operation (days/yr) = | 365 | (3)
(c) | Daily emissions estimate (lb/day) = (daily drift loss [lb/day]) x (concentration [ppm] / 1,000,000) | [6 empty] | (4)
(d) | Annual emissions estimate (lb/yr) = (annual drift loss [lb/yr]) x (concentration [ppm] / 1,000,000) | [6 empty] | (4)
References
(1) | See Input Cooling Tower for Rates and Parameters
(2) | Information provided by Intel Corporation. TAC concentration Is based on dosage rates and TAC percentage in SDS.
(3) | Based on continuous operation.
(4) | Assumes the composition of the drift loss is same as the cooling tower makeup water.
(5) | Assumes that dosing frequency is daily

## Cooling Towers
Emission Unit | Site | Building | Equipment Type | Equipment Tag | Air Dispersion ID | Install Date | Drift Rate | Peak Flow Rate per pump (gpm) | Peak TDS (ppm) | Avg Pump Recirculation (gpm) | Avg TDS (ppm)
EU-COOLING TOWER | Ronler Acres | CUB4 | Cooling Towers | RAC4-CT114-1 | CTC4_01 | 2013-07-01 | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB4 | Cooling Towers | RAC4-CT114-2 | CTC4_02 | 2013-07-01 | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB4 | Cooling Towers | RAC4-CT114-3 | CTC4_03 | 2013-07-01 | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB4 | Cooling Towers | RAC4-CT114-4 | CTC4_04 | 2013-07-01 | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB4 | Cooling Towers | RAC4-CT114-5 | CTC4_05 | 2013-07-01 | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB4 | Cooling Towers | RAC4-CT114-6 | CTC4_06 | 2013-07-01 | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB4 | Cooling Towers | RAC4-CT114-7 | CTC4_07 | 2013-07-01 | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB4 | Cooling Towers | RAC4-CT114-8 | CTC4_08 | 2013-07-01 | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB4 | Cooling Towers | RAC4-CT114-9 | CTC4_09 | 2014-01-01 | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB4 | Cooling Towers | RAC4-CT114-10 | CTC4_10 | 2014-01-01 | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB4 | Cooling Towers | RAC4-CT114-11 | CTC4_11 | 2014-01-01 | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB4 | Cooling Towers | RAC4-CT114-12 | CTC4_12 | 2014-01-01 | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB4 | Cooling Towers | RAC4-CT114-13 | CTC4_13 | 2021-08-01 | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB4 | Cooling Towers | RAC4-CT114-14 | CTC4_14 | 2022-08-01 | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB4 | Cooling Towers | RAC4-CT114-15 | CTC4_15 | 2023-07-01 | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB4 | Cooling Towers | RAC4-CT114-16 | CTC4_16 | 2024-07-01 | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB4X | Cooling Towers | RAC4-CT114-17 | CTC4_17 | 2028-12-01 | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB4X | Cooling Towers | RAC4-CT114-18 | CTC4_18 | 2028-12-01 | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB4X | Cooling Towers | RAC4-CT114-19 | CTC4_19 | 2028-12-01 | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB4X | Cooling Towers | RAC4-CT114-20 | CTC4_20 | 2028-12-01 | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB5 | Cooling Towers | RAC5-CT115-1 | CTC5_01 | 2021-04-01 | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB5 | Cooling Towers | RAC5-CT115-2 | CTC5_02 | 2021-04-02 | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB5 | Cooling Towers | RAC5-CT115-3 | CTC5_03 | 2021-04-03 | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB5 | Cooling Towers | RAC5-CT115-4 | CTC5_04 | 2021-04-04 | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB5 | Cooling Towers | RAC5-CT115-5 | CTC5_05 | 2021-04-05 | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB5 | Cooling Towers | RAC5-CT115-6 | CTC5_06 | 2021-04-06 | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB5 | Cooling Towers | RAC5-CT115-7 | CTC5_07 | 2021-04-07 | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB5 | Cooling Towers | RAC5-CT115-8 | CTC5_08 | 2021-04-08 | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB5 | Cooling Towers | RAC5-CT115-9 | CTC5_09 | Planned | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB5 | Cooling Towers | RAC5-CT115-10 | CTC5_10 | Planned | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB5 | Cooling Towers | RAC5-CT115-11 | CTC5_11 | Planned | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB5 | Cooling Towers | RAC5-CT115-12 | CTC5_12 | Planned | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB5 | Cooling Towers | RAC5-CT115-13 | CTC5_13 | Planned | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB5 | Cooling Towers | RAC5-CT115-14 | CTC5_14 | Planned | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB5 | Cooling Towers | RAC5-CT115-15 | CTC5_15 | Planned | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB5 | Cooling Towers | RAC5-CT115-16 | CTC5_16 | Planned | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB5 | Cooling Towers | RAC5-CT115-17 | CTC5_17 | Planned | 0.0005% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB3 | Cooling Towers | CT-114-1-210 | CTC3_01 | 2001-05-01 | 0.001% | 7700 | 3350 | 3850 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB3 | Cooling Towers | CT-114-2-210 | CTC3_02 | 2001-05-01 | 0.001% | 7700 | 3350 | 3850 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB3 | Cooling Towers | CT-114-3-210 | CTC3_03 | 2001-05-01 | 0.001% | 7700 | 3350 | 3850 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB3 | Cooling Towers | CT-114-4-210 | CTC3_04 | 2001-05-01 | 0.001% | 7700 | 3350 | 3850 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB3 | Cooling Towers | CT-114-5-210 | CTC3_05 | 2001-05-01 | 0.001% | 7700 | 3350 | 3850 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB3X | Cooling Towers | CUB3-CT114-21-10 | CTC3_06 | 2018-05-01 | 0.001% | 7700 | 3350 | 3850 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB3X | Cooling Towers | CUB3-CT114-22-10 | CTC3_07 | 2018-05-02 | 0.001% | 7700 | 3350 | 3850 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB3X | Cooling Towers | CUB3-CT114-23-10 | CTC3_08 | 2018-05-03 | 0.001% | 7700 | 3350 | 3850 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB3X | Cooling Towers | CUB3-CT114-24-10 | CTC3_09 | 2018-05-04 | 0.001% | 7700 | 3350 | 3850 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB3X | Cooling Towers | CUB3-CT114-25-10 | CTC3_10 | 2018-05-05 | 0.001% | 7700 | 3350 | 3850 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB3X | Cooling Towers | CUB3-CT114-26-10 | CTC3_11 | 2018-05-06 | 0.001% | 7700 | 3350 | 3850 | 1057.26
EU-COOLING TOWER | Ronler Acres | RP1 | Cooling Towers | RP1-CT114-1-200 | CTRP1_01 | 2003-06-01 | 0.001% | 3844 | 3350 | 1922 | 1057.26
EU-COOLING TOWER | Ronler Acres | RP1 | Cooling Towers | RP1-CT114-2-200 | CTRP1_02 | 2001-05-01 | 0.001% | 3844 | 3350 | 1922 | 1057.26
EU-COOLING TOWER | Ronler Acres | RP1 | Cooling Towers | RP1-CT114-3-00 | CTRP1_03 | Planned | 0.001% | 3844 | 3350 | 1922 | 1057.26
EU-COOLING TOWER | Ronler Acres | RA4 | Cooling Towers | RA4-CT113-1-10 | CTR4_01 | 2014-07-01 | 0.001% | 5600 | 3350 | 2800 | 1057.26
EU-COOLING TOWER | Ronler Acres | RA4 | Cooling Towers | RA4-CT113-2-10 | CTR4_02 | 2016-01-01 | 0.001% | 5600 | 3350 | 2800 | 1057.26
EU-COOLING TOWER | Ronler Acres | RA4 | Cooling Towers | RA4-CT113-3-10 | CTR4_03 | 2016-01-01 | 0.001% | 5600 | 3350 | 2800 | 1057.26
EU-COOLING TOWER | Ronler Acres | RA4 | Cooling Towers | RA4-CT113-4-10 | CTR4_04 | Planned | 0.001% | 5600 | 3350 | 2800 | 1057.26
EU-COOLING TOWER | Ronler Acres | RA4 | Cooling Towers | RA4-CT113-5-10 | CTR4_05 | Planned | 0.001% | 5600 | 3350 | 2800 | 1057.26
EU-COOLING TOWER | Ronler Acres | RA4 | Cooling Towers | RA4-CT113-6-10 | CTR4_06 | Planned | 0.001% | 5600 | 3350 | 2800 | 1057.26
EU-COOLING TOWER | Ronler Acres | RA5 | Cooling Towers | RA5-CT114-1 | CTR5_01 | Planned | 0.001% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | RA6 | Cooling Towers | RA6-CT114-1 | CTR6_01 | Planned | 0.001% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB2 | Cooling Towers | CUB2-CT114-1-210 | CTC2_01 | 1998-05-01 | 0.001% | 8000 | 3350 | 4000 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB2 | Cooling Towers | CUB2-CT114-2-210 | CTC2_02 | 1998-05-01 | 0.001% | 8000 | 3350 | 4000 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB2 | Cooling Towers | CUB2-CT114-3-210 | CTC2_03 | 1998-05-01 | 0.001% | 8000 | 3350 | 4000 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB2 | Cooling Towers | CUB2-CT114-4-210 | CTC2_04 | 1998-05-01 | 0.001% | 8000 | 3350 | 4000 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB2 | Cooling Towers | CUB2-CT114-5-210 | CTC2_05 | 1998-05-01 | 0.001% | 8000 | 3350 | 4000 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB2 | Cooling Towers | CUB2-CT114-6-210 | CTC2_06 | 1998-05-01 | 0.001% | 8000 | 3350 | 4000 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB2 | Cooling Towers | CUB2-CT114-7-210 | CTC2_07 | 2000-06-01 | 0.001% | 8000 | 3350 | 4000 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB2 | Cooling Towers | CUB2-CT114-8-210 | CTC2_08 | 2000-06-01 | 0.001% | 8000 | 3350 | 4000 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB2 | Cooling Towers | CUB2-CT114-9-210 | CTC2_09 | 2000-06-01 | 0.001% | 8000 | 3350 | 4000 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB2 | Cooling Towers | CUB2-CT114-10-210 | CTC2_10 | Planned | 0.001% | 8000 | 3350 | 4000 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB2X | Cooling Towers | CUB2-CT114-11-10 | CTC2_11 | 2012-07-01 | 0.001% | 8000 | 3350 | 4000 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB2X | Cooling Towers | CUB2-CT114-12-10 | CTC2_12 | 2012-07-01 | 0.001% | 8000 | 3350 | 4000 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB2X | Cooling Towers | CUB2-CT114-13-10 | CTC2_13 | 2017-01-01 | 0.001% | 8000 | 3350 | 4000 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB2X | Cooling Towers | CUB2-CT114-14-10 | CTC2_14 | Planned | 0.001% | 8000 | 3350 | 4000 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB1 | Cooling Towers | F20-CT114-1-210 | CTC1_01 | Pre-project | 0.001% | 8000 | 3350 | 4000 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB1 | Cooling Towers | F20-CT114-2-210 | CTC1_02 | Pre-project | 0.001% | 8000 | 3350 | 4000 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB1 | Cooling Towers | F20-CT114-3-210 | CTC1_03 | Pre-project | 0.001% | 8000 | 3350 | 4000 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB1 | Cooling Towers | F20-CT114-4-210 | CTC1_04 | Pre-project | 0.001% | 8000 | 3350 | 4000 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB1 | Cooling Towers | F20-CT114-5-210 | CTC1_05 | Pre-project | 0.001% | 8000 | 3350 | 4000 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB1 | Cooling Towers | F20-CT114-6-210 | CTC1_06 | Pre-project | 0.001% | 8000 | 3350 | 4000 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB1 | Cooling Towers | F20-CT114-7-210 | CTC1_07 | Pre-project | 0.001% | 8000 | 3350 | 4000 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB1 | Cooling Towers | F20-CT114-8-210 | CTC1_08 | Pre-project | 0.001% | 8000 | 3350 | 4000 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB1 | Cooling Towers | F20-CT114-9-210 | CTC1_09 | Pre-project | 0.001% | 8000 | 3350 | 4000 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB1 | Cooling Towers | F20-CT114-10-210 | CTC1_10 | Planned | 0.001% | 8000 | 3350 | 4000 | 1057.26
EU-COOLING TOWER | Ronler Acres | CUB1 | Cooling Towers | F20-CT114-11-210 | CTC1_11 | Planned | 0.001% | 8000 | 3350 | 4000 | 1057.26
EU-COOLING TOWER | Ronler Acres | N2 Plant | Cooling Towers | N2-CT114-1 | CTN2_01 | 2018 | 0.001% | 10220 | 3350 | 5110 | 1057.26
EU-COOLING TOWER | Ronler Acres | N2 Plant | Cooling Towers | N2-CT114-2 | CTN2_02 | 2016-01-01 | 0.001% | 14090 | 3350 | 7045 | 1057.26
EU-COOLING TOWER | Ronler Acres | N2 Plant | Cooling Towers | N2-CT114-3 | CTN2_03 | Planned | 0.001% | 14090 | 3350 | 7045 | 1057.26
EU-COOLING TOWER | Ronler Acres | PCB-1 | Cooling Towers | RACB3-CT-114-1-35 | CTCB_01 | 2016-07-01 | 0.001% | 7700 | 3350 | 3850 | 1057.26
EU-COOLING TOWER | Ronler Acres | PCB-1 | Cooling Towers | RACB3-CT-114-2-35 | CTCB_02 | 2016-07-01 | 0.001% | 7700 | 3350 | 3850 | 1057.26
EU-COOLING TOWER | Ronler Acres | PCB-1 | Cooling Towers | RACB3-CT-114-3-35 | CTCB_03 | 2019-04-01 | 0.001% | 7700 | 3350 | 3850 | 1057.26
EU-COOLING TOWER | Ronler Acres | WATR | Cooling Towers | RAWTR1-CH918-1-11 | CTWTR_01 | 2019-04-01 | 0.001% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | WATR | Cooling Towers | RAWTR1-CH918-2-11 | CTWTR_02 | 2019-04-01 | 0.001% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | WATR | Cooling Towers | RAWTR1-CH918-3-11 | CTWTR_03 | 2019-04-01 | 0.001% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | WATR | Cooling Towers | RAWTR1-CH918-4-11 | CTWTR_04 | 2019-04-01 | 0.001% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | WATR | Cooling Towers | RAWTR1-CH918-5-11 | CTWTR_05 | 2019-04-01 | 0.001% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | WATR | Cooling Towers | RAWTR1-CH918-6-11 | CTWTR_06 | 2019-04-01 | 0.001% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | WATR | Cooling Towers | RAWTR1-CH918-7-11 | CTWTR_07 | 2019-04-01 | 0.001% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | WATR | Cooling Towers | RAWTR1-CH918-8-11 | CTWTR_08 | 2019-04-01 | 0.001% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | WATR | Cooling Towers | RAWTR1-CH918-9-11 | CTWTR_09 | Planned | 0.001% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | WATR | Cooling Towers | RAWTR1-CH918-10-11 | CTWTR_10 | Planned | 0.001% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | WATR | Cooling Towers | RAWTR1-CH918-11-11 | CTWTR_11 | Planned | 0.001% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Ronler Acres | WATR | Cooling Towers | RAWTR1-CH918-12-11 | CTWTR_12 | Planned | 0.001% | 10722 | 3350 | 5361 | 1057.26
EU-COOLING TOWER | Aloha | AL4 | Cooling Towers | AL4-CHW-CT2 | CTA4_01 | 1991-02-01 | 0.001% | 1500 | 3350 | 750 | 1057.26
EU-COOLING TOWER | Aloha | AL4 | Cooling Towers | AL4-CHW-CT3 | CTA4_02 | 1991-02-01 | 0.001% | 1500 | 3350 | 750 | 1057.26
EU-COOLING TOWER | Aloha | F15 | Cooling Towers | F15-CT29-1-1 | CTF15_01 | 1992-01-01 | 0.001% | 4680 | 3350 | 2340 | 1057.26
EU-COOLING TOWER | Aloha | F15 | Cooling Towers | F15-CT29-1-2 | CTF15_02 | 1992-01-01 | 0.001% | 4680 | 3350 | 2340 | 1057.26
EU-COOLING TOWER | Aloha | F15 | Cooling Towers | F15-CT29-1-3 | CTF15_03 | 1992-01-01 | 0.001% | 4680 | 3350 | 2340 | 1057.26
EU-COOLING TOWER | Aloha | F15 | Cooling Towers | F15-CT29-1-4 | CTF15_04 | 1992-01-01 | 0.001% | 4680 | 3350 | 2340 | 1057.26
EU-COOLING TOWER | Aloha | F15 | Cooling Towers | F15-CT29-1-5 | CTF15_05 | 1992-01-01 | 0.001% | 4680 | 3350 | 2340 | 1057.26
EU-COOLING TOWER | Aloha | F15 | Cooling Towers | F15-CT29-1-6-1 | CTF15_06 | 2015-06-01 | 0.001% | 840 | 3350 | 420 | 1057.26