## Input_EGEN
Toxics Emissions Sub-Unit (TESU) ID |  | Site | Building | Install Date | Diesel Particulate Filter (Yes/No) | Fuel Consumption (1) (gal/hr) | Daily Hours of Operation (hrs/day) | Annual Hours of Operation (3) (hrs/yr)
RA1-ELEC-CPS-GEN01 |  | Ronler Acres | RA1 | 1996 | No | 113.51 | 10 | 25
RA1-ELEC-CPS-GEN02 |  | Ronler Acres | RA1 | 1996 | No | 113.51 | 10 | 25
RA1-ELEC-CPS-GEN03 |  | Ronler Acres | RA1 | 1996 | No | 113.51 | 10 | 25
RA1-ELEC-CPS-GEN04 |  | Ronler Acres | RA1 | 1996 | No | 113.51 | 10 | 25
D1C-CPS-GEN01 |  | Ronler Acres | D1C | 1998 | No | 89.71 | 10 | 25
D1C-CPS-GEN02 |  | Ronler Acres | D1C | 1998 | No | 89.71 | 10 | 25
D1C-CPS-GEN03 |  | Ronler Acres | D1C | 1998 | No | 89.71 | 10 | 25
D1C-EPS-GEN01 |  | Ronler Acres | D1C | 1998 | No | 208 | 10 | 25
D1C-EPS-GEN02 |  | Ronler Acres | D1C | 1998 | No | 208 | 10 | 25
RB1-EPS-GEN01 |  | Ronler Acres | RB1 | 1998 | No | 137.5 | 10 | 25
RP1-EPS-GEN01 |  | Ronler Acres | RP1 | 2000 | No | 145.4 | 10 | 25
RP1-GEN-2 | (4) | Ronler Acres | RP1 | Future - TBD | No | 145.4 | 10 | 25
EPS-GEN01 |  | Ronler Acres | D1D EGEN | 2002 | No | 147.46 | 10 | 25
EPS-GEN02 |  | Ronler Acres | D1D EGEN | 2002 | No | 147.46 | 10 | 25
EPS-GEN03 |  | Ronler Acres | D1D EGEN | 2002 | No | 147.46 | 10 | 25
EPS-GEN04 |  | Ronler Acres | D1D EGEN | 2002 | No | 147.46 | 10 | 25
EPS-GEN05 |  | Ronler Acres | D1D EGEN | 2002 | No | 147.46 | 10 | 25
EPS-GEN06 |  | Ronler Acres | D1D EGEN | 2002 | No | 147.46 | 10 | 25
D1D-GEN-7 | (4) | Ronler Acres | D1D EGEN | Future - TBD | No | 147.5 | 10 | 25
RS4-ELEC-EG-4-1 |  | Ronler Acres | RS4 | 2005 | No | 22.9 | 10 | 25
RS6-ELEC-EG-6-1 |  | Ronler Acres | RS6 | 2005 | No | 22.9 | 10 | 25
RS6-GEN-2 | (4) | Ronler Acres | RS6 | Future - TBD | No | 147.5 | 10 | 25
D1X-GEN-1A |  | Ronler Acres | D1X EGEN1 | 2012 | No | 176 | 10 | 25
D1X-GEN-1B |  | Ronler Acres | D1X EGEN1 | 2013 | No | 172.1 | 10 | 25
D1X-GEN-1C |  | Ronler Acres | D1X EGEN1 | 2012 | No | 176 | 10 | 25
D1X-GEN-2A |  | Ronler Acres | D1X EGEN1 | 2012 | No | 176 | 10 | 25
D1X-GEN-2B |  | Ronler Acres | D1X EGEN1 | 2012 | No | 176 | 10 | 25
D1X-GEN-2C |  | Ronler Acres | D1X EGEN1 | 2012 | No | 176 | 10 | 25
D1X-GEN-3A |  | Ronler Acres | D1X EGEN1 | 2013 | No | 172.1 | 10 | 25
D1X-GEN-3B |  | Ronler Acres | D1X EGEN1 | 2012 | No | 176 | 10 | 25
D1X-GEN-3C |  | Ronler Acres | D1X EGEN1 | 2013 | No | 172.1 | 10 | 25
D1X-GEN-4A |  | Ronler Acres | D1X EGEN1 | 2013 | No | 172.1 | 10 | 25
D1X-GEN-4B |  | Ronler Acres | D1X EGEN1 | 2013 | No | 172.1 | 10 | 25
D1X-GEN-5C |  | Ronler Acres | D1X EGEN1 | 2017 | No | 206 | 10 | 25
D1X-GEN-5A |  | Ronler Acres | D1X EGEN1 | 2017 | Yes | 206 | 10 | 25
D1X-GEN-5B |  | Ronler Acres | D1X EGEN1 | 2017 | Yes | 206 | 10 | 25
D1X-GEN-4C |  | Ronler Acres | D1X EGEN1 | 2013 | Yes | 172.1 | 10 | 25
D1X-GEN-6A |  | Ronler Acres | D1X EGEN1 | 2018 | Yes | 206 | 10 | 25
D1X-GEN-6B |  | Ronler Acres | D1X EGEN1 | 2018 | Yes | 206 | 10 | 25
D1X-GEN-6C |  | Ronler Acres | D1X EGEN1 | 2018 | Yes | 206 | 10 | 25
D1X-GEN-7A | (4) | Ronler Acres | D1X EGEN1 | Future - TBD | Yes | 172 | 10 | 25
D1X-GEN-7B | (4) | Ronler Acres | D1X EGEN1 | Future - TBD | Yes | 172 | 10 | 25
D1X-GEN-7C | (4) | Ronler Acres | D1X EGEN1 | Future - TBD | Yes | 172 | 10 | 25
D1X2-GEN-6A | (4) | Ronler Acres | CUB5 | Future - TBD | Yes | 240 | 10 | 25
D1X2-GEN-6B | (4) | Ronler Acres | CUB5 | Future - TBD | Yes | 240 | 10 | 25
D1X2-GEN-6C | (4) | Ronler Acres | CUB5 | Future - TBD | Yes | 240 | 10 | 25
D1X2-GEN-7A | (4) | Ronler Acres | CUB5 | Future - TBD | Yes | 240 | 10 | 25
D1X2-GEN-7B | (4) | Ronler Acres | CUB5 | Future - TBD | Yes | 240 | 10 | 25
D1X2-GEN-7C | (4) | Ronler Acres | CUB5 | Future - TBD | Yes | 240 | 10 | 25
D1X2-GEN-1A |  | Ronler Acres | CUB5 | 2021 | Yes | 240 | 10 | 25
D1X2-GEN-1B |  | Ronler Acres | CUB5 | 2021 | Yes | 240 | 10 | 25
D1X2-GEN-1C |  | Ronler Acres | CUB5 | 2021 | Yes | 240 | 10 | 25
D1X2-GEN-2A |  | Ronler Acres | CUB5 | 2021 | Yes | 240 | 10 | 25
D1X2-GEN-2B |  | Ronler Acres | CUB5 | 2021 | Yes | 240 | 10 | 25
D1X2-GEN-2C |  | Ronler Acres | CUB5 | 2021 | Yes | 240 | 10 | 25
D1X2-GEN-3A |  | Ronler Acres | CUB5 | 2021 | Yes | 240 | 10 | 25
D1X2-GEN-3B |  | Ronler Acres | CUB5 | 2021 | Yes | 240 | 10 | 25
D1X2-GEN-3C |  | Ronler Acres | CUB5 | 2021 | Yes | 240 | 10 | 25
D1X2-GEN-4A |  | Ronler Acres | CUB5 | 2021 | Yes | 240 | 10 | 25
D1X2-GEN-4B |  | Ronler Acres | CUB5 | 2021 | Yes | 240 | 10 | 25
D1X2-GEN-4C |  | Ronler Acres | CUB5 | 2021 | Yes | 240 | 10 | 25
D1X2-GEN-5A | (4) | Ronler Acres | CUB5 | Future - TBD | Yes | 240 | 10 | 25
D1X2-GEN-5B | (4) | Ronler Acres | CUB5 | Future - TBD | Yes | 240 | 10 | 25
D1X2-GEN-5C | (4) | Ronler Acres | CUB5 | Future - TBD | Yes | 240 | 10 | 25
F20-EPS-1 |  | Ronler Acres | D1B | 2016 | Yes | 206 | 10 | 25
F20-EPS-2 |  | Ronler Acres | D1B | 2016 | Yes | 206 | 10 | 25
F20-CPS-1 | (5) | Ronler Acres | D1B | stored | No | 46.4 | 10 | 25
F15-EG01 |  | Aloha | F15 | 1994 | No | 107.8 | 10 | 25
F15-EG02 |  | Aloha | F15 | 1994 | No | 107.8 | 10 | 25
F15-EG03 |  | Aloha | F15 | 1994 | No | 107.8 | 10 | 25
F15.5-EG01 |  | Aloha | F5 | 2001 | No | 107.86 | 10 | 25
F15.5-EG02 |  | Aloha | F5 | 2001 | No | 107.28 | 10 | 25
PH #1 |  | Ronler Acres | Pump House #1 | 2009 | No | 10.4 | 10 | 50
PH #2 |  | Ronler Acres | Pump House #2 | 2013 | No | 11.3 | 10 | 50
PH #3 |  | Ronler Acres | Pump House #3 | 2009 | No | 6.6 | 10 | 50
PH #4 |  | Ronler Acres | Pump House #4 | 2021 | No | 6.1 | 10 | 50
N2-GEN-1A |  | Ronler Acres | N2 Plant | 2017 | Yes | 30.1 | 10 | 25
IWW-PS-1 |  | Ronler Acres | IWW | 2018 | Yes | 34.4 | 10 | 25
IWW-GEN-2 | (4) | Ronler Acres | IWW | Future - TBD | Yes | 206 | 10 | 25
IWW-GEN-1 |  | Ronler Acres | IWW PS | 2018 | Yes | 206 | 10 | 25
MAX-EGEN |  | Ronler Acres | RS7 | 2005 | No | 19.4 | 10 | 25
H2-GEN-1 | (4) | Ronler Acres | H2 Plant | Future - TBD | Yes | 21.4 | 10 | 25
D1A-GEN-1 | (4) | Ronler Acres | D1A | Future - TBD | Yes | 240 | 10 | 25
D1A-GEN-2 | (4) | Ronler Acres | D1A | Future - TBD | Yes | 240 | 10 | 25
D1A-GEN-3 | (4) | Ronler Acres | D1A | Future - TBD | Yes | 240 | 10 | 25
D1A-GEN-4 | (4) | Ronler Acres | D1A | Future - TBD | Yes | 240 | 10 | 25
D1A-GEN-5 | (4) | Ronler Acres | D1A | Future - TBD | Yes | 240 | 10 | 25
D1A-GEN-6 | (4) | Ronler Acres | D1A | Future - TBD | Yes | 240 | 10 | 25
D1A-GEN-7 | (4) | Ronler Acres | D1A | Future - TBD | Yes | 240 | 10 | 25
D1A-GEN-8 | (4) | Ronler Acres | D1A | Future - TBD | Yes | 240 | 10 | 25
References
(1) | Information provided by Intel.
(2) | Emergency generators are limited to 10 hours/day. Although only 10 generators are permitted to operate in one day, daily emissions have been provided for all
emergency generators for informational purposes only. Intel will operate a maximum on 10 emergency generators in one day.
(3) | Emergency generators are limited to 25 hours/year.
(4) | Future engine details (hp and fuel consumption) are estimates based on similar existing engines or other best estimates and are subject to change.
(5) | EGEN is currently stored and not in use. For completeness, the EGEN was included in the PTE.

## EGEN_DPF_a_RONLER
TESU ID | [6 empty] | N2-GEN-1A |  | H2-GEN-1
Fuel Consumption (gal/hr) | [6 empty] | 30.1 |  | 21.4
Daily Hours of Operation (hrs/day) | [5 empty] | (1) | 10 |  | 10
Annual Hours of Operation (hrs/yr) | [5 empty] | (1) | 25 |  | 25
Pollutant |  | CAS | Emission Factor (2) (lb/Mgal) |  | Johnson Matthey DPF Control Efficiency (%) |  | Emissions Estimate
[7 empty] | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr)
METALS
| Antimony and Compounds | 7440-36-0 | 0.00031819 |  | 70 | (9) | 2.8732e-05 | 7.1831e-05 | 2.0428e-05 | 5.1069e-05
| Arsenic and Compounds | 7440-38-2 | 0.0016 |  | 70 | (9) | 0.00014448 | 0.0003612 | 0.00010272 | 0.0002568
| Barium and Compounds | 7440-39-3 | 0.00037389 |  | 94.5 | (7) | 6.1898e-06 | 1.5475e-05 | 4.4007e-06 | 1.1002e-05
| Beryllium and compounds | 7440-41-7 | 4.7708e-06 |  | 70 | (9) | 4.3081e-07 | 1.077e-06 | 3.0629e-07 | 7.6572e-07
| Cadmium and Compounds | 7440-43-9 | 0.0015 |  | 70 | (7) | 0.00013545 | 0.00033863 | 9.63e-05 | 0.00024075
| Chromium VI | 18540-29-9 | 0.0001 |  | 94.5 | (7) | 1.6555e-06 | 4.1388e-06 | 1.177e-06 | 2.9425e-06
| Copper and Compounds | 7440-50-8 | 0.0041 |  | 94.5 | (7) | 6.7876e-05 | 0.00016969 | 4.8257e-05 | 0.00012064
| Cobalt and compounds | 7440-48-4 | 1.5751e-05 |  | 70 | (9) | 1.4223e-06 | 3.5558e-06 | 1.0112e-06 | 2.5281e-06
| Lead and Compounds | 7439-92-1 | 0.0083 |  | 70 | (7) | 0.00074949 | 0.0018737 | 0.00053286 | 0.0013322
| Manganese and Compounds | 7439-96-5 | 0.0031 |  | 94.5 | (9) | 5.1321e-05 | 0.0001283 | 3.6487e-05 | 9.1218e-05
| Mercury and Compounds | 7439-97-6 | 0.002 |  | 40 | (7) | 0.0003612 | 0.000903 | 0.0002568 | 0.000642
| Nickel and Compounds | 7440-02-0 | 0.0039 |  | 94.5 | (7) | 6.4565e-05 | 0.00016141 | 4.5903e-05 | 0.00011476
| Phosphorus and compounds | 504 | 0.008404 |  | 95 | (7) | 0.00012648 | 0.0003162 | 8.9923e-05 | 0.00022481
| Selenium and Compounds | 7782-49-2 | 0.0022 |  | 70 | (9) | 0.00019866 | 0.00049665 | 0.00014124 | 0.0003531
| Silver and compounds | 7440-22-4 | 4.8013e-05 |  | 70 | (9) | 4.3356e-06 | 1.0839e-05 | 3.0824e-06 | 7.7061e-06
| Thallium and compounds | 7440-28-0 | 0.00024009 |  | 70 | (9) | 2.168e-05 | 5.4201e-05 | 1.5414e-05 | 3.8535e-05
| Zinc and compounds | 7440-66-6 | 0.0052262 |  | 95 | (7) | 7.8654e-05 | 0.00019663 | 5.592e-05 | 0.0001398
ORGANIC COMPOUNDS
| 1,3-Butadiene | 106-99-0 | 0.2174 |  | 70 | (8) | 0.019739 | 0.050374 | 0.014034 | 0.035814
| Acetaldehyde | 75-07-0 | 0.7833 |  | 63 | (7) | 0.087716 | 0.22385 | 0.062363 | 0.15915
| Acrolein | 107-02-8 | 0.0339 |  | 70 | (7) | 0.003078 | 0.007855 | 0.0021884 | 0.0055846
| Benzene | 71-43-2 | 0.1863 |  | 65 | (7) | 0.019735 | 0.050362 | 0.014031 | 0.035806
| Chlorobenzene | 108-90-7 | 0.0002 |  | 63 | (8) | 2.2397e-05 | 5.7155e-05 | 1.5923e-05 | 4.0635e-05
| Ethylbenzene | 100-41-4 | 0.0109 |  | 67 | (7) | 0.0010887 | 0.0027782 | 0.00077399 | 0.0019752
| Formaldehyde | 50-00-0 | 1.7261 |  | 65 | (7) | 0.183 | 0.46843 | 0.1301 | 0.33304
| Hexane | 110-54-3 | 0.0269 |  | 60 | (7) | 0.0032566 | 0.0083107 | 0.0023153 | 0.0059086
| Propylene | 115-07-1 | 0.47 |  | 63 | (8) | 0.052632 | 0.13431 | 0.037419 | 0.095493
| Toluene | 108-88-3 | 0.1054 |  | 73 | (7) | 0.008613 | 0.02198 | 0.0061235 | 0.015627
| Xylene (mixed isomers) | 1330-20-7 | 0.0424 |  | 66 | (7) | 0.0043631 | 0.011134 | 0.003102 | 0.0079162
INORGANIC COMPOUNDS
| Ammonia | 7664-41-7 | 0.8 |  | 0 |  | 0.24212 | 0.61789 | 0.17214 | 0.4393
| Hydrochloric Acid | 7647-01-0 | 0.1863 |  | 0 |  | 0.056385 | 0.14389 | 0.040087 | 0.1023
POLYCYCLIC AROMATIC HYDROCARBONS (PAH)
| Benzo[a]pyrene | 50-32-8 | 3.52e-05 |  | 65 | (7) | 3.7287e-06 | 9.5155e-06 | 2.651e-06 | 6.7652e-06
| Naphthalene | 91-20-3 | 0.0197 |  | 65 | (7) | 0.0020868 | 0.0053255 | 0.0014836 | 0.0037862
| PAH | 401 | 0.0362 |  | 63 | (7) | 0.0040538 | 0.010345 | 0.0028821 | 0.007355
DIESEL PARTICULATE MATTER (DPM)
| DPM | 200 | 33.5 |  | 93 | (6) | 0.70973 | 1.8112 | 0.50459 | 1.2877
Notes
DPF = Diesel Particulate Filter; HAP = Hazardous Air Pollutant; Mgal = 1,000 gallons; TAC = Toxic Air Contaminant.
(a) | Daily emissions estimate (lb/day) = ([emission factor {lb/Mgal}] x [fuel consumption {gal/hr}] x [daily hours of operation {hrs/day}] x [Mgal/1,000 gal] | [8 empty] | (b), (c)
+ [cold start emissions {lb/minute}] x [number of cold starts per day] - [emissions per minute, normal operation {lb/minute}] x [number of cold starts per day])
| x (1 - [DPF control efficiency {%}] / 100)) | [7 empty] | (3)
|  | Cold start adjustment factor = | 4.3 | (4)
|  | Cold start adjustment factor (formaldehyde) = | 4.8 | (4)
|  | Number of cold starts per day = | 1 | (5)
(b) | Cold start emissions (lb/minute) = (emission factor [lb/Mgal]) x (cold start adjustment factor) x (hourly fuel consumption [Mgal/hr]) / 60
(c) | Emissions per minute, normal operation (lb/minute) = (emission factor [lb/Mgal]) x (hourly fuel consumption [Mgal/hr]) / 60
(d) | Annual emissions estimate (lb/yr) = ([emission factor {lb/Mgal}] x [fuel consumption {gal/hr}] x [annual hours of operation {hrs/yr}] x [Mgal/1,000 gal] | [8 empty] | (b), (c)
+ [cold start emissions {lb/minute}] x [number of cold starts per year] - [emissions per minute, normal operation {lb/minute}] x [number of cold starts per year])
| x (1 - [DPF control efficiency {%}] / 100)) | [7 empty] | (3)
|  | Cold start adjustment factor = | 4.3 | (4)
|  | Cold start adjustment factor (formaldehyde) = | 4.8 | (4)
|  | Number of cold starts per year = | 12 | (5)
References
(1) | Permit conditions limit Intel to operate 10 EGENs for 10 hours a day and all EGENs for 25 hours a year.
(2) | Emission factors from the Oregon Department of Environmental Quality, AQ104B, diesel internal combustion, less than
750 hp. Ammonia emission factor assumes value for no SNCR or SCR control. DEQ reference CAO Diesel RICE (a).
(3) | Time allotted for cold starts was omitted from the daily/annual operating capacity in emission calculations. Cold start adjustments are not required for metals.
(4) | Cold start adjustment factors provided by the Oregon Department of Environmental Quality. All applicable pollutants, except formaldehyde,
share the same adjustment factor. Cold start adjustments are not required for metals.
(5) | Based on one cold start per month per engine for Preventative Maintenance activities.
(6) | Value based on filterable PM efficiency provided by Johnson Matthey.
(7) | Information provided by Johnson Matthey.
(8) | Value based on similar TAC.
(9) | Per DEQ guidance, assumed 70%

## EGEN_DPF_b_RONLER
TESU ID | [8 empty] | D1X-GEN-5A |  | D1X-GEN-5B |  |  | D1X-GEN-4C |  | D1X-GEN-6A |  | D1X-GEN-6B |  | D1X-GEN-6C |  | D1X-GEN-7A |  | D1X-GEN-7B |  | D1X-GEN-7C |  | D1X2-GEN-6A |  | D1X2-GEN-6B |  | D1X2-GEN-6C |  | D1X2-GEN-7A |  | D1X2-GEN-7B |  | D1X2-GEN-7C |  | D1X2-GEN-1A |  | D1X2-GEN-1B |  | D1X2-GEN-1C |  | D1X2-GEN-2A |  | D1X2-GEN-2B |  | D1X2-GEN-2C |  | D1X2-GEN-3A |  | D1X2-GEN-3B |  | D1X2-GEN-3C |  | D1X2-GEN-4A |  | D1X2-GEN-4B |  | D1X2-GEN-4C |  | D1X2-GEN-5A |  | D1X2-GEN-5B |  | D1X2-GEN-5C |  | F20-EPS-1 |  | F20-EPS-2 |  | IWW-PS-1 |  | IWW-GEN-2 |  | IWW-GEN-1 |  | D1A-GEN-1 |  | D1A-GEN-2 |  | D1A-GEN-3 |  | D1A-GEN-4 |  | D1A-GEN-5 |  | D1A-GEN-6 |  | D1A-GEN-7 |  | D1A-GEN-8
Fuel Consumption (gal/hr) | [8 empty] | 206 |  | 206 |  |  | 172.1 |  | 206 |  | 206 |  | 206 |  | 172 |  | 172 |  | 172 |  | 240 |  | 240 |  | 240 |  | 240 |  | 240 |  | 240 |  | 240 |  | 240 |  | 240 |  | 240 |  | 240 |  | 240 |  | 240 |  | 240 |  | 240 |  | 240 |  | 240 |  | 240 |  | 240 |  | 240 |  | 240 |  | 206 |  | 206 |  | 34.4 |  | 206 |  | 206 |  | 240 |  | 240 |  | 240 |  | 240 |  | 240 |  | 240 |  | 240 |  | 240
Daily Hours of Operation (hrs/day) | [7 empty] | (1) | 10 |  | 10 |  |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10
Annual Hours of Operation (hrs/yr) | [7 empty] | (1) | 25 |  | 25 |  |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25
Pollutant |  | CAS | Emission Factor (2) (lb/Mgal) |  | DPF Control Efficiency (%) |  |  |  | Emissions Estimate
[9 empty] | D1X-GEN-5A |  | D1X-GEN-5B |  |  | D1X-GEN-4C |  | D1X-GEN-6A |  | D1X-GEN-6B |  | D1X-GEN-6C |  | D1X-GEN-7A |  | D1X-GEN-7B |  | D1X-GEN-7C |  | D1X2-GEN-6A |  | D1X2-GEN-6B |  | D1X2-GEN-6C |  | D1X2-GEN-7A |  | D1X2-GEN-7B |  | D1X2-GEN-7C |  | D1X2-GEN-1A |  | D1X2-GEN-1B |  | D1X2-GEN-1C |  | D1X2-GEN-2A |  | D1X2-GEN-2B |  | D1X2-GEN-2C |  | D1X2-GEN-3A |  | D1X2-GEN-3B |  | D1X2-GEN-3C |  | D1X2-GEN-4A |  | D1X2-GEN-4B |  | D1X2-GEN-4C |  | D1X2-GEN-5A |  | D1X2-GEN-5B |  | D1X2-GEN-5C |  | F20-EPS-1 |  | F20-EPS-2 |  | IWW-PS-1 |  | IWW-GEN-2 |  | IWW-GEN-1 |  | D1A-GEN-1 |  | D1A-GEN-2 |  | D1A-GEN-3 |  | D1A-GEN-4 |  | D1A-GEN-5 |  | D1A-GEN-6 |  | D1A-GEN-7 |  | D1A-GEN-8
[5 empty] | Rypos |  | Johnson Matthey |  | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) |  | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr)
METALS
| Antimony and Compounds | 7440-36-0 | 0.00031819 | (2) | 70 | (6) | 70 | (11) | 0.00019664 | 0.0004916 | 0.00019664 |  | 0.0004916 | 0.00016428 | 0.0004107 | 0.00019664 | 0.0004916 | 0.00019664 | 0.0004916 | 0.00019664 | 0.0004916 | 0.00016418 | 0.00041046 | 0.00016418 | 0.00041046 | 0.00016418 | 0.00041046 | 0.00022909 | 0.00057274 | 0.00022909 | 0.00057274 | 0.00022909 | 0.00057274 | 0.00022909 | 0.00057274 | 0.00022909 | 0.00057274 | 0.00022909 | 0.00057274 | 0.00022909 | 0.00057274 | 0.00022909 | 0.00057274 | 0.00022909 | 0.00057274 | 0.00022909 | 0.00057274 | 0.00022909 | 0.00057274 | 0.00022909 | 0.00057274 | 0.00022909 | 0.00057274 | 0.00022909 | 0.00057274 | 0.00022909 | 0.00057274 | 0.00022909 | 0.00057274 | 0.00022909 | 0.00057274 | 0.00022909 | 0.00057274 | 0.00022909 | 0.00057274 | 0.00022909 | 0.00057274 | 0.00022909 | 0.00057274 | 0.00019664 | 0.0004916 | 0.00019664 | 0.0004916 | 3.2837e-05 | 8.2092e-05 | 0.00019664 | 0.0004916 | 0.00019664 | 0.0004916 | 0.00022909 | 0.00057274 | 0.00022909 | 0.00057274 | 0.00022909 | 0.00057274 | 0.00022909 | 0.00057274 | 0.00022909 | 0.00057274 | 0.00022909 | 0.00057274 | 0.00022909 | 0.00057274 | 0.00022909 | 0.00057274
| Arsenic and Compounds | 7440-38-2 | 0.00027685 | (2) | 70 | (6) | 70 | (11) | 0.00017109 | 0.00042774 | 0.00017109 |  | 0.00042774 | 0.00014294 | 0.00035735 | 0.00017109 | 0.00042774 | 0.00017109 | 0.00042774 | 0.00017109 | 0.00042774 | 0.00014286 | 0.00035714 | 0.00014286 | 0.00035714 | 0.00014286 | 0.00035714 | 0.00019933 | 0.00049833 | 0.00019933 | 0.00049833 | 0.00019933 | 0.00049833 | 0.00019933 | 0.00049833 | 0.00019933 | 0.00049833 | 0.00019933 | 0.00049833 | 0.00019933 | 0.00049833 | 0.00019933 | 0.00049833 | 0.00019933 | 0.00049833 | 0.00019933 | 0.00049833 | 0.00019933 | 0.00049833 | 0.00019933 | 0.00049833 | 0.00019933 | 0.00049833 | 0.00019933 | 0.00049833 | 0.00019933 | 0.00049833 | 0.00019933 | 0.00049833 | 0.00019933 | 0.00049833 | 0.00019933 | 0.00049833 | 0.00019933 | 0.00049833 | 0.00019933 | 0.00049833 | 0.00019933 | 0.00049833 | 0.00017109 | 0.00042774 | 0.00017109 | 0.00042774 | 2.8571e-05 | 7.1428e-05 | 0.00017109 | 0.00042774 | 0.00017109 | 0.00042774 | 0.00019933 | 0.00049833 | 0.00019933 | 0.00049833 | 0.00019933 | 0.00049833 | 0.00019933 | 0.00049833 | 0.00019933 | 0.00049833 | 0.00019933 | 0.00049833 | 0.00019933 | 0.00049833 | 0.00019933 | 0.00049833
| Barium and Compounds | 7440-39-3 | 0.00037389 | (2) | 70 | (11) | 94.5 | (10) | 4.2362e-05 | 0.00010591 | 4.2362e-05 |  | 0.00010591 | 3.5391e-05 | 8.8477e-05 | 4.2362e-05 | 0.00010591 | 4.2362e-05 | 0.00010591 | 4.2362e-05 | 0.00010591 | 3.537e-05 | 8.8426e-05 | 3.537e-05 | 8.8426e-05 | 3.537e-05 | 8.8426e-05 | 4.9354e-05 | 0.00012338 | 4.9354e-05 | 0.00012338 | 4.9354e-05 | 0.00012338 | 4.9354e-05 | 0.00012338 | 4.9354e-05 | 0.00012338 | 4.9354e-05 | 0.00012338 | 4.9354e-05 | 0.00012338 | 4.9354e-05 | 0.00012338 | 4.9354e-05 | 0.00012338 | 4.9354e-05 | 0.00012338 | 4.9354e-05 | 0.00012338 | 4.9354e-05 | 0.00012338 | 4.9354e-05 | 0.00012338 | 4.9354e-05 | 0.00012338 | 4.9354e-05 | 0.00012338 | 4.9354e-05 | 0.00012338 | 4.9354e-05 | 0.00012338 | 4.9354e-05 | 0.00012338 | 4.9354e-05 | 0.00012338 | 4.9354e-05 | 0.00012338 | 4.9354e-05 | 0.00012338 | 4.2362e-05 | 0.00010591 | 4.2362e-05 | 0.00010591 | 3.8586e-05 | 9.6464e-05 | 4.2362e-05 | 0.00010591 | 4.2362e-05 | 0.00010591 | 4.9354e-05 | 0.00012338 | 4.9354e-05 | 0.00012338 | 4.9354e-05 | 0.00012338 | 4.9354e-05 | 0.00012338 | 4.9354e-05 | 0.00012338 | 4.9354e-05 | 0.00012338 | 4.9354e-05 | 0.00012338 | 4.9354e-05 | 0.00012338
| Beryllium and compounds | 7440-41-7 | 4.7708e-06 | (2) | 70 | (6) | 70 | (11) | 2.9484e-06 | 7.371e-06 | 2.9484e-06 |  | 7.371e-06 | 2.4632e-06 | 6.158e-06 | 2.9484e-06 | 7.371e-06 | 2.9484e-06 | 7.371e-06 | 2.9484e-06 | 7.371e-06 | 2.4618e-06 | 6.1544e-06 | 2.4618e-06 | 6.1544e-06 | 2.4618e-06 | 6.1544e-06 | 3.435e-06 | 8.5875e-06 | 3.435e-06 | 8.5875e-06 | 3.435e-06 | 8.5875e-06 | 3.435e-06 | 8.5875e-06 | 3.435e-06 | 8.5875e-06 | 3.435e-06 | 8.5875e-06 | 3.435e-06 | 8.5875e-06 | 3.435e-06 | 8.5875e-06 | 3.435e-06 | 8.5875e-06 | 3.435e-06 | 8.5875e-06 | 3.435e-06 | 8.5875e-06 | 3.435e-06 | 8.5875e-06 | 3.435e-06 | 8.5875e-06 | 3.435e-06 | 8.5875e-06 | 3.435e-06 | 8.5875e-06 | 3.435e-06 | 8.5875e-06 | 3.435e-06 | 8.5875e-06 | 3.435e-06 | 8.5875e-06 | 3.435e-06 | 8.5875e-06 | 3.435e-06 | 8.5875e-06 | 3.435e-06 | 8.5875e-06 | 2.9484e-06 | 7.371e-06 | 2.9484e-06 | 7.371e-06 | 4.9235e-07 | 1.2309e-06 | 2.9484e-06 | 7.371e-06 | 2.9484e-06 | 7.371e-06 | 3.435e-06 | 8.5875e-06 | 3.435e-06 | 8.5875e-06 | 3.435e-06 | 8.5875e-06 | 3.435e-06 | 8.5875e-06 | 3.435e-06 | 8.5875e-06 | 3.435e-06 | 8.5875e-06 | 3.435e-06 | 8.5875e-06 | 3.435e-06 | 8.5875e-06
| Cadmium and Compounds | 7440-43-9 | 8.0778e-05 | (2) | 70 | (6) | 70 | (10) | 4.9921e-05 | 0.0001248 | 4.9921e-05 |  | 0.0001248 | 4.1706e-05 | 0.00010426 | 4.9921e-05 | 0.0001248 | 4.9921e-05 | 0.0001248 | 4.9921e-05 | 0.0001248 | 4.1682e-05 | 0.0001042 | 4.1682e-05 | 0.0001042 | 4.1682e-05 | 0.0001042 | 5.816e-05 | 0.0001454 | 5.816e-05 | 0.0001454 | 5.816e-05 | 0.0001454 | 5.816e-05 | 0.0001454 | 5.816e-05 | 0.0001454 | 5.816e-05 | 0.0001454 | 5.816e-05 | 0.0001454 | 5.816e-05 | 0.0001454 | 5.816e-05 | 0.0001454 | 5.816e-05 | 0.0001454 | 5.816e-05 | 0.0001454 | 5.816e-05 | 0.0001454 | 5.816e-05 | 0.0001454 | 5.816e-05 | 0.0001454 | 5.816e-05 | 0.0001454 | 5.816e-05 | 0.0001454 | 5.816e-05 | 0.0001454 | 5.816e-05 | 0.0001454 | 5.816e-05 | 0.0001454 | 5.816e-05 | 0.0001454 | 5.816e-05 | 0.0001454 | 4.9921e-05 | 0.0001248 | 4.9921e-05 | 0.0001248 | 8.3363e-06 | 2.0841e-05 | 4.9921e-05 | 0.0001248 | 4.9921e-05 | 0.0001248 | 5.816e-05 | 0.0001454 | 5.816e-05 | 0.0001454 | 5.816e-05 | 0.0001454 | 5.816e-05 | 0.0001454 | 5.816e-05 | 0.0001454 | 5.816e-05 | 0.0001454 | 5.816e-05 | 0.0001454 | 5.816e-05 | 0.0001454
| Chromium VI | 18540-29-9 | 6.3144e-05 | (2) | 70 | (6) | 94.5 | (10) | 7.1543e-06 | 1.7886e-05 | 7.1543e-06 |  | 1.7886e-05 | 5.9769e-06 | 1.4942e-05 | 7.1543e-06 | 1.7886e-05 | 7.1543e-06 | 1.7886e-05 | 7.1543e-06 | 1.7886e-05 | 5.9735e-06 | 1.4934e-05 | 5.9735e-06 | 1.4934e-05 | 5.9735e-06 | 1.4934e-05 | 8.3351e-06 | 2.0838e-05 | 8.3351e-06 | 2.0838e-05 | 8.3351e-06 | 2.0838e-05 | 8.3351e-06 | 2.0838e-05 | 8.3351e-06 | 2.0838e-05 | 8.3351e-06 | 2.0838e-05 | 8.3351e-06 | 2.0838e-05 | 8.3351e-06 | 2.0838e-05 | 8.3351e-06 | 2.0838e-05 | 8.3351e-06 | 2.0838e-05 | 8.3351e-06 | 2.0838e-05 | 8.3351e-06 | 2.0838e-05 | 8.3351e-06 | 2.0838e-05 | 8.3351e-06 | 2.0838e-05 | 8.3351e-06 | 2.0838e-05 | 8.3351e-06 | 2.0838e-05 | 8.3351e-06 | 2.0838e-05 | 8.3351e-06 | 2.0838e-05 | 8.3351e-06 | 2.0838e-05 | 8.3351e-06 | 2.0838e-05 | 8.3351e-06 | 2.0838e-05 | 7.1543e-06 | 1.7886e-05 | 7.1543e-06 | 1.7886e-05 | 6.5165e-06 | 1.6291e-05 | 7.1543e-06 | 1.7886e-05 | 7.1543e-06 | 1.7886e-05 | 8.3351e-06 | 2.0838e-05 | 8.3351e-06 | 2.0838e-05 | 8.3351e-06 | 2.0838e-05 | 8.3351e-06 | 2.0838e-05 | 8.3351e-06 | 2.0838e-05 | 8.3351e-06 | 2.0838e-05 | 8.3351e-06 | 2.0838e-05 | 8.3351e-06 | 2.0838e-05
| Copper and Compounds | 7440-50-8 | 0.00050214 | (2) | 70 | (11) | 94.5 | (10) | 5.6892e-05 | 0.00014223 | 5.6892e-05 |  | 0.00014223 | 4.753e-05 | 0.00011882 | 5.6892e-05 | 0.00014223 | 5.6892e-05 | 0.00014223 | 5.6892e-05 | 0.00014223 | 4.7502e-05 | 0.00011875 | 4.7502e-05 | 0.00011875 | 4.7502e-05 | 0.00011875 | 6.6282e-05 | 0.0001657 | 6.6282e-05 | 0.0001657 | 6.6282e-05 | 0.0001657 | 6.6282e-05 | 0.0001657 | 6.6282e-05 | 0.0001657 | 6.6282e-05 | 0.0001657 | 6.6282e-05 | 0.0001657 | 6.6282e-05 | 0.0001657 | 6.6282e-05 | 0.0001657 | 6.6282e-05 | 0.0001657 | 6.6282e-05 | 0.0001657 | 6.6282e-05 | 0.0001657 | 6.6282e-05 | 0.0001657 | 6.6282e-05 | 0.0001657 | 6.6282e-05 | 0.0001657 | 6.6282e-05 | 0.0001657 | 6.6282e-05 | 0.0001657 | 6.6282e-05 | 0.0001657 | 6.6282e-05 | 0.0001657 | 6.6282e-05 | 0.0001657 | 6.6282e-05 | 0.0001657 | 5.6892e-05 | 0.00014223 | 5.6892e-05 | 0.00014223 | 5.182e-05 | 0.00012955 | 5.6892e-05 | 0.00014223 | 5.6892e-05 | 0.00014223 | 6.6282e-05 | 0.0001657 | 6.6282e-05 | 0.0001657 | 6.6282e-05 | 0.0001657 | 6.6282e-05 | 0.0001657 | 6.6282e-05 | 0.0001657 | 6.6282e-05 | 0.0001657 | 6.6282e-05 | 0.0001657 | 6.6282e-05 | 0.0001657
| Cobalt and compounds | 7440-48-4 | 1.5751e-05 | (2) | 70 | (6) | 70 | (11) | 9.7342e-06 | 2.4336e-05 | 9.7342e-06 |  | 2.4336e-05 | 8.1323e-06 | 2.0331e-05 | 9.7342e-06 | 2.4336e-05 | 9.7342e-06 | 2.4336e-05 | 9.7342e-06 | 2.4336e-05 | 8.1276e-06 | 2.0319e-05 | 8.1276e-06 | 2.0319e-05 | 8.1276e-06 | 2.0319e-05 | 1.1341e-05 | 2.8352e-05 | 1.1341e-05 | 2.8352e-05 | 1.1341e-05 | 2.8352e-05 | 1.1341e-05 | 2.8352e-05 | 1.1341e-05 | 2.8352e-05 | 1.1341e-05 | 2.8352e-05 | 1.1341e-05 | 2.8352e-05 | 1.1341e-05 | 2.8352e-05 | 1.1341e-05 | 2.8352e-05 | 1.1341e-05 | 2.8352e-05 | 1.1341e-05 | 2.8352e-05 | 1.1341e-05 | 2.8352e-05 | 1.1341e-05 | 2.8352e-05 | 1.1341e-05 | 2.8352e-05 | 1.1341e-05 | 2.8352e-05 | 1.1341e-05 | 2.8352e-05 | 1.1341e-05 | 2.8352e-05 | 1.1341e-05 | 2.8352e-05 | 1.1341e-05 | 2.8352e-05 | 1.1341e-05 | 2.8352e-05 | 1.1341e-05 | 2.8352e-05 | 9.7342e-06 | 2.4336e-05 | 9.7342e-06 | 2.4336e-05 | 1.6255e-06 | 4.0638e-06 | 9.7342e-06 | 2.4336e-05 | 9.7342e-06 | 2.4336e-05 | 1.1341e-05 | 2.8352e-05 | 1.1341e-05 | 2.8352e-05 | 1.1341e-05 | 2.8352e-05 | 1.1341e-05 | 2.8352e-05 | 1.1341e-05 | 2.8352e-05 | 1.1341e-05 | 2.8352e-05 | 1.1341e-05 | 2.8352e-05 | 1.1341e-05 | 2.8352e-05
| Lead and Compounds | 7439-92-1 | 0.00036367 | (2) | 70 | (6) | 70 | (10) | 0.00022475 | 0.00056187 | 0.00022475 |  | 0.00056187 | 0.00018776 | 0.00046941 | 0.00022475 | 0.00056187 | 0.00022475 | 0.00056187 | 0.00022475 | 0.00056187 | 0.00018765 | 0.00046914 | 0.00018765 | 0.00046914 | 0.00018765 | 0.00046914 | 0.00026184 | 0.00065461 | 0.00026184 | 0.00065461 | 0.00026184 | 0.00065461 | 0.00026184 | 0.00065461 | 0.00026184 | 0.00065461 | 0.00026184 | 0.00065461 | 0.00026184 | 0.00065461 | 0.00026184 | 0.00065461 | 0.00026184 | 0.00065461 | 0.00026184 | 0.00065461 | 0.00026184 | 0.00065461 | 0.00026184 | 0.00065461 | 0.00026184 | 0.00065461 | 0.00026184 | 0.00065461 | 0.00026184 | 0.00065461 | 0.00026184 | 0.00065461 | 0.00026184 | 0.00065461 | 0.00026184 | 0.00065461 | 0.00026184 | 0.00065461 | 0.00026184 | 0.00065461 | 0.00026184 | 0.00065461 | 0.00022475 | 0.00056187 | 0.00022475 | 0.00056187 | 3.7531e-05 | 9.3827e-05 | 0.00022475 | 0.00056187 | 0.00022475 | 0.00056187 | 0.00026184 | 0.00065461 | 0.00026184 | 0.00065461 | 0.00026184 | 0.00065461 | 0.00026184 | 0.00065461 | 0.00026184 | 0.00065461 | 0.00026184 | 0.00065461 | 0.00026184 | 0.00065461 | 0.00026184 | 0.00065461
| Manganese and Compounds | 7439-96-5 | 0.00041991 | (2) | 70 | (6) | 94.5 | (10) | 4.7576e-05 | 0.00011894 | 4.7576e-05 |  | 0.00011894 | 3.9747e-05 | 9.9367e-05 | 4.7576e-05 | 0.00011894 | 4.7576e-05 | 0.00011894 | 4.7576e-05 | 0.00011894 | 3.9724e-05 | 9.9309e-05 | 3.9724e-05 | 9.9309e-05 | 3.9724e-05 | 9.9309e-05 | 5.5428e-05 | 0.00013857 | 5.5428e-05 | 0.00013857 | 5.5428e-05 | 0.00013857 | 5.5428e-05 | 0.00013857 | 5.5428e-05 | 0.00013857 | 5.5428e-05 | 0.00013857 | 5.5428e-05 | 0.00013857 | 5.5428e-05 | 0.00013857 | 5.5428e-05 | 0.00013857 | 5.5428e-05 | 0.00013857 | 5.5428e-05 | 0.00013857 | 5.5428e-05 | 0.00013857 | 5.5428e-05 | 0.00013857 | 5.5428e-05 | 0.00013857 | 5.5428e-05 | 0.00013857 | 5.5428e-05 | 0.00013857 | 5.5428e-05 | 0.00013857 | 5.5428e-05 | 0.00013857 | 5.5428e-05 | 0.00013857 | 5.5428e-05 | 0.00013857 | 5.5428e-05 | 0.00013857 | 4.7576e-05 | 0.00011894 | 4.7576e-05 | 0.00011894 | 4.3335e-05 | 0.00010834 | 4.7576e-05 | 0.00011894 | 4.7576e-05 | 0.00011894 | 5.5428e-05 | 0.00013857 | 5.5428e-05 | 0.00013857 | 5.5428e-05 | 0.00013857 | 5.5428e-05 | 0.00013857 | 5.5428e-05 | 0.00013857 | 5.5428e-05 | 0.00013857 | 5.5428e-05 | 0.00013857 | 5.5428e-05 | 0.00013857
| Mercury and Compounds | 7439-97-6 | 1.5107e-05 | (2) | 70 | (6) | 40 | (10) | 1.8673e-05 | 4.6682e-05 | 1.8673e-05 |  | 4.6682e-05 | 1.56e-05 | 3.9e-05 | 1.8673e-05 | 4.6682e-05 | 1.8673e-05 | 4.6682e-05 | 1.8673e-05 | 4.6682e-05 | 1.5591e-05 | 3.8977e-05 | 1.5591e-05 | 3.8977e-05 | 1.5591e-05 | 3.8977e-05 | 2.1755e-05 | 5.4386e-05 | 2.1755e-05 | 5.4386e-05 | 2.1755e-05 | 5.4386e-05 | 2.1755e-05 | 5.4386e-05 | 2.1755e-05 | 5.4386e-05 | 2.1755e-05 | 5.4386e-05 | 2.1755e-05 | 5.4386e-05 | 2.1755e-05 | 5.4386e-05 | 2.1755e-05 | 5.4386e-05 | 2.1755e-05 | 5.4386e-05 | 2.1755e-05 | 5.4386e-05 | 2.1755e-05 | 5.4386e-05 | 2.1755e-05 | 5.4386e-05 | 2.1755e-05 | 5.4386e-05 | 2.1755e-05 | 5.4386e-05 | 2.1755e-05 | 5.4386e-05 | 2.1755e-05 | 5.4386e-05 | 2.1755e-05 | 5.4386e-05 | 2.1755e-05 | 5.4386e-05 | 2.1755e-05 | 5.4386e-05 | 2.1755e-05 | 5.4386e-05 | 1.8673e-05 | 4.6682e-05 | 1.8673e-05 | 4.6682e-05 | 1.5591e-06 | 3.8977e-06 | 1.8673e-05 | 4.6682e-05 | 1.8673e-05 | 4.6682e-05 | 2.1755e-05 | 5.4386e-05 | 2.1755e-05 | 5.4386e-05 | 2.1755e-05 | 5.4386e-05 | 2.1755e-05 | 5.4386e-05 | 2.1755e-05 | 5.4386e-05 | 2.1755e-05 | 5.4386e-05 | 2.1755e-05 | 5.4386e-05 | 2.1755e-05 | 5.4386e-05
| Nickel and Compounds | 7440-02-0 | 0.00018223 | (2) | 70 | (6) | 94.5 | (10) | 2.0647e-05 | 5.1616e-05 | 2.0647e-05 |  | 5.1616e-05 | 1.7249e-05 | 4.3122e-05 | 2.0647e-05 | 5.1616e-05 | 2.0647e-05 | 5.1616e-05 | 2.0647e-05 | 5.1616e-05 | 1.7239e-05 | 4.3097e-05 | 1.7239e-05 | 4.3097e-05 | 1.7239e-05 | 4.3097e-05 | 2.4054e-05 | 6.0136e-05 | 2.4054e-05 | 6.0136e-05 | 2.4054e-05 | 6.0136e-05 | 2.4054e-05 | 6.0136e-05 | 2.4054e-05 | 6.0136e-05 | 2.4054e-05 | 6.0136e-05 | 2.4054e-05 | 6.0136e-05 | 2.4054e-05 | 6.0136e-05 | 2.4054e-05 | 6.0136e-05 | 2.4054e-05 | 6.0136e-05 | 2.4054e-05 | 6.0136e-05 | 2.4054e-05 | 6.0136e-05 | 2.4054e-05 | 6.0136e-05 | 2.4054e-05 | 6.0136e-05 | 2.4054e-05 | 6.0136e-05 | 2.4054e-05 | 6.0136e-05 | 2.4054e-05 | 6.0136e-05 | 2.4054e-05 | 6.0136e-05 | 2.4054e-05 | 6.0136e-05 | 2.4054e-05 | 6.0136e-05 | 2.4054e-05 | 6.0136e-05 | 2.0647e-05 | 5.1616e-05 | 2.0647e-05 | 5.1616e-05 | 1.8806e-05 | 4.7015e-05 | 2.0647e-05 | 5.1616e-05 | 2.0647e-05 | 5.1616e-05 | 2.4054e-05 | 6.0136e-05 | 2.4054e-05 | 6.0136e-05 | 2.4054e-05 | 6.0136e-05 | 2.4054e-05 | 6.0136e-05 | 2.4054e-05 | 6.0136e-05 | 2.4054e-05 | 6.0136e-05 | 2.4054e-05 | 6.0136e-05 | 2.4054e-05 | 6.0136e-05
| Phosphorus and compounds | 504 | 0.008404 | (2) | 70 | (6) | 95 | (10) | 0.00086561 | 0.002164 | 0.00086561 |  | 0.002164 | 0.00072316 | 0.0018079 | 0.00086561 | 0.002164 | 0.00086561 | 0.002164 | 0.00086561 | 0.002164 | 0.00072274 | 0.0018069 | 0.00072274 | 0.0018069 | 0.00072274 | 0.0018069 | 0.0010085 | 0.0025212 | 0.0010085 | 0.0025212 | 0.0010085 | 0.0025212 | 0.0010085 | 0.0025212 | 0.0010085 | 0.0025212 | 0.0010085 | 0.0025212 | 0.0010085 | 0.0025212 | 0.0010085 | 0.0025212 | 0.0010085 | 0.0025212 | 0.0010085 | 0.0025212 | 0.0010085 | 0.0025212 | 0.0010085 | 0.0025212 | 0.0010085 | 0.0025212 | 0.0010085 | 0.0025212 | 0.0010085 | 0.0025212 | 0.0010085 | 0.0025212 | 0.0010085 | 0.0025212 | 0.0010085 | 0.0025212 | 0.0010085 | 0.0025212 | 0.0010085 | 0.0025212 | 0.0010085 | 0.0025212 | 0.00086561 | 0.002164 | 0.00086561 | 0.002164 | 0.00086729 | 0.0021682 | 0.00086561 | 0.002164 | 0.00086561 | 0.002164 | 0.0010085 | 0.0025212 | 0.0010085 | 0.0025212 | 0.0010085 | 0.0025212 | 0.0010085 | 0.0025212 | 0.0010085 | 0.0025212 | 0.0010085 | 0.0025212 | 0.0010085 | 0.0025212 | 0.0010085 | 0.0025212
| Selenium and Compounds | 7782-49-2 | 0.00037638 | (2) | 70 | (6) | 70 | (11) | 0.0002326 | 0.00058151 | 0.0002326 |  | 0.00058151 | 0.00019433 | 0.00048582 | 0.0002326 | 0.00058151 | 0.0002326 | 0.00058151 | 0.0002326 | 0.00058151 | 0.00019421 | 0.00048553 | 0.00019421 | 0.00048553 | 0.00019421 | 0.00048553 | 0.000271 | 0.00067749 | 0.000271 | 0.00067749 | 0.000271 | 0.00067749 | 0.000271 | 0.00067749 | 0.000271 | 0.00067749 | 0.000271 | 0.00067749 | 0.000271 | 0.00067749 | 0.000271 | 0.00067749 | 0.000271 | 0.00067749 | 0.000271 | 0.00067749 | 0.000271 | 0.00067749 | 0.000271 | 0.00067749 | 0.000271 | 0.00067749 | 0.000271 | 0.00067749 | 0.000271 | 0.00067749 | 0.000271 | 0.00067749 | 0.000271 | 0.00067749 | 0.000271 | 0.00067749 | 0.000271 | 0.00067749 | 0.000271 | 0.00067749 | 0.000271 | 0.00067749 | 0.0002326 | 0.00058151 | 0.0002326 | 0.00058151 | 3.8843e-05 | 9.7107e-05 | 0.0002326 | 0.00058151 | 0.0002326 | 0.00058151 | 0.000271 | 0.00067749 | 0.000271 | 0.00067749 | 0.000271 | 0.00067749 | 0.000271 | 0.00067749 | 0.000271 | 0.00067749 | 0.000271 | 0.00067749 | 0.000271 | 0.00067749 | 0.000271 | 0.00067749
| Silver and compounds | 7440-22-4 | 4.8013e-05 | (2) | 70 | (11) | 70 | (11) | 2.9672e-05 | 7.418e-05 | 2.9672e-05 |  | 7.418e-05 | 2.4789e-05 | 6.1973e-05 | 2.9672e-05 | 7.418e-05 | 2.9672e-05 | 7.418e-05 | 2.9672e-05 | 7.418e-05 | 2.4775e-05 | 6.1937e-05 | 2.4775e-05 | 6.1937e-05 | 2.4775e-05 | 6.1937e-05 | 3.4569e-05 | 8.6423e-05 | 3.4569e-05 | 8.6423e-05 | 3.4569e-05 | 8.6423e-05 | 3.4569e-05 | 8.6423e-05 | 3.4569e-05 | 8.6423e-05 | 3.4569e-05 | 8.6423e-05 | 3.4569e-05 | 8.6423e-05 | 3.4569e-05 | 8.6423e-05 | 3.4569e-05 | 8.6423e-05 | 3.4569e-05 | 8.6423e-05 | 3.4569e-05 | 8.6423e-05 | 3.4569e-05 | 8.6423e-05 | 3.4569e-05 | 8.6423e-05 | 3.4569e-05 | 8.6423e-05 | 3.4569e-05 | 8.6423e-05 | 3.4569e-05 | 8.6423e-05 | 3.4569e-05 | 8.6423e-05 | 3.4569e-05 | 8.6423e-05 | 3.4569e-05 | 8.6423e-05 | 3.4569e-05 | 8.6423e-05 | 3.4569e-05 | 8.6423e-05 | 2.9672e-05 | 7.418e-05 | 2.9672e-05 | 7.418e-05 | 4.9549e-06 | 1.2387e-05 | 2.9672e-05 | 7.418e-05 | 2.9672e-05 | 7.418e-05 | 3.4569e-05 | 8.6423e-05 | 3.4569e-05 | 8.6423e-05 | 3.4569e-05 | 8.6423e-05 | 3.4569e-05 | 8.6423e-05 | 3.4569e-05 | 8.6423e-05 | 3.4569e-05 | 8.6423e-05 | 3.4569e-05 | 8.6423e-05 | 3.4569e-05 | 8.6423e-05
| Thallium and compounds | 7440-28-0 | 0.00024009 | (2) | 70 | (11) | 70 | (11) | 0.00014838 | 0.00037094 | 0.00014838 |  | 0.00037094 | 0.00012396 | 0.0003099 | 0.00014838 | 0.00037094 | 0.00014838 | 0.00037094 | 0.00014838 | 0.00037094 | 0.00012389 | 0.00030972 | 0.00012389 | 0.00030972 | 0.00012389 | 0.00030972 | 0.00017287 | 0.00043217 | 0.00017287 | 0.00043217 | 0.00017287 | 0.00043217 | 0.00017287 | 0.00043217 | 0.00017287 | 0.00043217 | 0.00017287 | 0.00043217 | 0.00017287 | 0.00043217 | 0.00017287 | 0.00043217 | 0.00017287 | 0.00043217 | 0.00017287 | 0.00043217 | 0.00017287 | 0.00043217 | 0.00017287 | 0.00043217 | 0.00017287 | 0.00043217 | 0.00017287 | 0.00043217 | 0.00017287 | 0.00043217 | 0.00017287 | 0.00043217 | 0.00017287 | 0.00043217 | 0.00017287 | 0.00043217 | 0.00017287 | 0.00043217 | 0.00017287 | 0.00043217 | 0.00017287 | 0.00043217 | 0.00014838 | 0.00037094 | 0.00014838 | 0.00037094 | 2.4778e-05 | 6.1944e-05 | 0.00014838 | 0.00037094 | 0.00014838 | 0.00037094 | 0.00017287 | 0.00043217 | 0.00017287 | 0.00043217 | 0.00017287 | 0.00043217 | 0.00017287 | 0.00043217 | 0.00017287 | 0.00043217 | 0.00017287 | 0.00043217 | 0.00017287 | 0.00043217 | 0.00017287 | 0.00043217
| Zinc and compounds | 7440-66-6 | 0.0052262 | (2) | 70 | (11) | 95 | (10) | 0.0005383 | 0.0013457 | 0.0005383 |  | 0.0013457 | 0.00044971 | 0.0011243 | 0.0005383 | 0.0013457 | 0.0005383 | 0.0013457 | 0.0005383 | 0.0013457 | 0.00044945 | 0.0011236 | 0.00044945 | 0.0011236 | 0.00044945 | 0.0011236 | 0.00062714 | 0.0015679 | 0.00062714 | 0.0015679 | 0.00062714 | 0.0015679 | 0.00062714 | 0.0015679 | 0.00062714 | 0.0015679 | 0.00062714 | 0.0015679 | 0.00062714 | 0.0015679 | 0.00062714 | 0.0015679 | 0.00062714 | 0.0015679 | 0.00062714 | 0.0015679 | 0.00062714 | 0.0015679 | 0.00062714 | 0.0015679 | 0.00062714 | 0.0015679 | 0.00062714 | 0.0015679 | 0.00062714 | 0.0015679 | 0.00062714 | 0.0015679 | 0.00062714 | 0.0015679 | 0.00062714 | 0.0015679 | 0.00062714 | 0.0015679 | 0.00062714 | 0.0015679 | 0.00062714 | 0.0015679 | 0.0005383 | 0.0013457 | 0.0005383 | 0.0013457 | 0.00053934 | 0.0013484 | 0.0005383 | 0.0013457 | 0.0005383 | 0.0013457 | 0.00062714 | 0.0015679 | 0.00062714 | 0.0015679 | 0.00062714 | 0.0015679 | 0.00062714 | 0.0015679 | 0.00062714 | 0.0015679 | 0.00062714 | 0.0015679 | 0.00062714 | 0.0015679 | 0.00062714 | 0.0015679
ORGANIC COMPOUNDS
| 1,3-Butadiene | 106-99-0 | 0.2174 | (2) | 68 | (6) | 70 | (10) | 0.13509 | 0.34475 | 0.13509 |  | 0.34475 | 0.11286 | 0.28802 | 0.13509 | 0.34475 | 0.13509 | 0.34475 | 0.13509 | 0.34475 | 0.1128 | 0.28785 | 0.1128 | 0.28785 | 0.1128 | 0.28785 | 0.15739 | 0.40165 | 0.15739 | 0.40165 | 0.15739 | 0.40165 | 0.15739 | 0.40165 | 0.15739 | 0.40165 | 0.15739 | 0.40165 | 0.15739 | 0.40165 | 0.15739 | 0.40165 | 0.15739 | 0.40165 | 0.15739 | 0.40165 | 0.15739 | 0.40165 | 0.15739 | 0.40165 | 0.15739 | 0.40165 | 0.15739 | 0.40165 | 0.15739 | 0.40165 | 0.15739 | 0.40165 | 0.15739 | 0.40165 | 0.15739 | 0.40165 | 0.15739 | 0.40165 | 0.15739 | 0.40165 | 0.15739 | 0.40165 | 0.13509 | 0.34475 | 0.13509 | 0.34475 | 0.024063 | 0.061408 | 0.13435 | 0.33588 | 0.13435 | 0.33588 | 0.15739 | 0.40165 | 0.15739 | 0.40165 | 0.15739 | 0.40165 | 0.15739 | 0.40165 | 0.15739 | 0.40165 | 0.15739 | 0.40165 | 0.15739 | 0.40165 | 0.15739 | 0.40165
| 2-Methyl naphthalene | 91-57-6 | 0.012298 | (2) | 63 | (6) | 65 | (10) | 0.0089156 | 0.022752 | 0.0089156 |  | 0.022752 | 0.0074484 | 0.019008 | 0.0089156 | 0.022752 | 0.0089156 | 0.022752 | 0.0089156 | 0.022752 | 0.0074441 | 0.018997 | 0.0074441 | 0.018997 | 0.0074441 | 0.018997 | 0.010387 | 0.026507 | 0.010387 | 0.026507 | 0.010387 | 0.026507 | 0.010387 | 0.026507 | 0.010387 | 0.026507 | 0.010387 | 0.026507 | 0.010387 | 0.026507 | 0.010387 | 0.026507 | 0.010387 | 0.026507 | 0.010387 | 0.026507 | 0.010387 | 0.026507 | 0.010387 | 0.026507 | 0.010387 | 0.026507 | 0.010387 | 0.026507 | 0.010387 | 0.026507 | 0.010387 | 0.026507 | 0.010387 | 0.026507 | 0.010387 | 0.026507 | 0.010387 | 0.026507 | 0.010387 | 0.026507 | 0.010387 | 0.026507 | 0.0089156 | 0.022752 | 0.0089156 | 0.022752 | 0.0015739 | 0.0040165 | 0.0088668 | 0.022167 | 0.0088668 | 0.022167 | 0.010387 | 0.026507 | 0.010387 | 0.026507 | 0.010387 | 0.026507 | 0.010387 | 0.026507 | 0.010387 | 0.026507 | 0.010387 | 0.026507 | 0.010387 | 0.026507 | 0.010387 | 0.026507
| Acenaphthene | 83-32-9 | 0.00073461 | (2) | 63 | (6) | 66 | (10) | 0.00051735 | 0.0013203 | 0.00051735 |  | 0.0013203 | 0.00043222 | 0.001103 | 0.00051735 | 0.0013203 | 0.00051735 | 0.0013203 | 0.00051735 | 0.0013203 | 0.00043197 | 0.0011024 | 0.00043197 | 0.0011024 | 0.00043197 | 0.0011024 | 0.00060274 | 0.0015382 | 0.00060274 | 0.0015382 | 0.00060274 | 0.0015382 | 0.00060274 | 0.0015382 | 0.00060274 | 0.0015382 | 0.00060274 | 0.0015382 | 0.00060274 | 0.0015382 | 0.00060274 | 0.0015382 | 0.00060274 | 0.0015382 | 0.00060274 | 0.0015382 | 0.00060274 | 0.0015382 | 0.00060274 | 0.0015382 | 0.00060274 | 0.0015382 | 0.00060274 | 0.0015382 | 0.00060274 | 0.0015382 | 0.00060274 | 0.0015382 | 0.00060274 | 0.0015382 | 0.00060274 | 0.0015382 | 0.00060274 | 0.0015382 | 0.00060274 | 0.0015382 | 0.00060274 | 0.0015382 | 0.00051735 | 0.0013203 | 0.00051735 | 0.0013203 | 9.4016e-05 | 0.00023993 | 0.00051452 | 0.0012863 | 0.00051452 | 0.0012863 | 0.00060274 | 0.0015382 | 0.00060274 | 0.0015382 | 0.00060274 | 0.0015382 | 0.00060274 | 0.0015382 | 0.00060274 | 0.0015382 | 0.00060274 | 0.0015382 | 0.00060274 | 0.0015382 | 0.00060274 | 0.0015382
| Acenaphthylene | 208-96-8 | 0.00080982 | (2) | 63 | (6) | 63 | (10) | 0.00062064 | 0.0015838 | 0.00062064 |  | 0.0015838 | 0.0005185 | 0.0013232 | 0.00062064 | 0.0015838 | 0.00062064 | 0.0015838 | 0.00062064 | 0.0015838 | 0.0005182 | 0.0013224 | 0.0005182 | 0.0013224 | 0.0005182 | 0.0013224 | 0.00072307 | 0.0018453 | 0.00072307 | 0.0018453 | 0.00072307 | 0.0018453 | 0.00072307 | 0.0018453 | 0.00072307 | 0.0018453 | 0.00072307 | 0.0018453 | 0.00072307 | 0.0018453 | 0.00072307 | 0.0018453 | 0.00072307 | 0.0018453 | 0.00072307 | 0.0018453 | 0.00072307 | 0.0018453 | 0.00072307 | 0.0018453 | 0.00072307 | 0.0018453 | 0.00072307 | 0.0018453 | 0.00072307 | 0.0018453 | 0.00072307 | 0.0018453 | 0.00072307 | 0.0018453 | 0.00072307 | 0.0018453 | 0.00072307 | 0.0018453 | 0.00072307 | 0.0018453 | 0.00072307 | 0.0018453 | 0.00062064 | 0.0015838 | 0.00062064 | 0.0015838 | 0.00010364 | 0.00026449 | 0.00061724 | 0.0015431 | 0.00061724 | 0.0015431 | 0.00072307 | 0.0018453 | 0.00072307 | 0.0018453 | 0.00072307 | 0.0018453 | 0.00072307 | 0.0018453 | 0.00072307 | 0.0018453 | 0.00072307 | 0.0018453 | 0.00072307 | 0.0018453 | 0.00072307 | 0.0018453
| Acetaldehyde | 75-07-0 | 0.7833 | (2) | 59 | (6) | 63 | (10) | 0.60031 | 1.532 | 0.60031 |  | 1.532 | 0.50153 | 1.2799 | 0.60031 | 1.532 | 0.60031 | 1.532 | 0.60031 | 1.532 | 0.50123 | 1.2791 | 0.50123 | 1.2791 | 0.50123 | 1.2791 | 0.6994 | 1.7848 | 0.6994 | 1.7848 | 0.6994 | 1.7848 | 0.6994 | 1.7848 | 0.6994 | 1.7848 | 0.6994 | 1.7848 | 0.6994 | 1.7848 | 0.6994 | 1.7848 | 0.6994 | 1.7848 | 0.6994 | 1.7848 | 0.6994 | 1.7848 | 0.6994 | 1.7848 | 0.6994 | 1.7848 | 0.6994 | 1.7848 | 0.6994 | 1.7848 | 0.6994 | 1.7848 | 0.6994 | 1.7848 | 0.6994 | 1.7848 | 0.6994 | 1.7848 | 0.6994 | 1.7848 | 0.6994 | 1.7848 | 0.60031 | 1.532 | 0.60031 | 1.532 | 0.11108 | 0.28348 | 0.59703 | 1.4926 | 0.59703 | 1.4926 | 0.6994 | 1.7848 | 0.6994 | 1.7848 | 0.6994 | 1.7848 | 0.6994 | 1.7848 | 0.6994 | 1.7848 | 0.6994 | 1.7848 | 0.6994 | 1.7848 | 0.6994 | 1.7848
| Acrolein | 107-02-8 | 0.0339 | (2) | 66 | (6) | 70 | (10) | 0.021065 | 0.053758 | 0.021065 |  | 0.053758 | 0.017599 | 0.044912 | 0.021065 | 0.053758 | 0.021065 | 0.053758 | 0.021065 | 0.053758 | 0.017589 | 0.044885 | 0.017589 | 0.044885 | 0.017589 | 0.044885 | 0.024542 | 0.062631 | 0.024542 | 0.062631 | 0.024542 | 0.062631 | 0.024542 | 0.062631 | 0.024542 | 0.062631 | 0.024542 | 0.062631 | 0.024542 | 0.062631 | 0.024542 | 0.062631 | 0.024542 | 0.062631 | 0.024542 | 0.062631 | 0.024542 | 0.062631 | 0.024542 | 0.062631 | 0.024542 | 0.062631 | 0.024542 | 0.062631 | 0.024542 | 0.062631 | 0.024542 | 0.062631 | 0.024542 | 0.062631 | 0.024542 | 0.062631 | 0.024542 | 0.062631 | 0.024542 | 0.062631 | 0.024542 | 0.062631 | 0.021065 | 0.053758 | 0.021065 | 0.053758 | 0.0039868 | 0.010174 | 0.02095 | 0.052376 | 0.02095 | 0.052376 | 0.024542 | 0.062631 | 0.024542 | 0.062631 | 0.024542 | 0.062631 | 0.024542 | 0.062631 | 0.024542 | 0.062631 | 0.024542 | 0.062631 | 0.024542 | 0.062631 | 0.024542 | 0.062631
| Anthracene | 120-12-7 | 0.00045209 | (2) | 63 | (6) | 65 | (10) | 0.00032775 | 0.00083641 | 0.00032775 |  | 0.00083641 | 0.00027381 | 0.00069876 | 0.00032775 | 0.00083641 | 0.00032775 | 0.00083641 | 0.00032775 | 0.00083641 | 0.00027366 | 0.00069836 | 0.00027366 | 0.00069836 | 0.00027366 | 0.00069836 | 0.00038184 | 0.00097445 | 0.00038184 | 0.00097445 | 0.00038184 | 0.00097445 | 0.00038184 | 0.00097445 | 0.00038184 | 0.00097445 | 0.00038184 | 0.00097445 | 0.00038184 | 0.00097445 | 0.00038184 | 0.00097445 | 0.00038184 | 0.00097445 | 0.00038184 | 0.00097445 | 0.00038184 | 0.00097445 | 0.00038184 | 0.00097445 | 0.00038184 | 0.00097445 | 0.00038184 | 0.00097445 | 0.00038184 | 0.00097445 | 0.00038184 | 0.00097445 | 0.00038184 | 0.00097445 | 0.00038184 | 0.00097445 | 0.00038184 | 0.00097445 | 0.00038184 | 0.00097445 | 0.00038184 | 0.00097445 | 0.00032775 | 0.00083641 | 0.00032775 | 0.00083641 | 5.7858e-05 | 0.00014765 | 0.00032596 | 0.00081489 | 0.00032596 | 0.00081489 | 0.00038184 | 0.00097445 | 0.00038184 | 0.00097445 | 0.00038184 | 0.00097445 | 0.00038184 | 0.00097445 | 0.00038184 | 0.00097445 | 0.00038184 | 0.00097445 | 0.00038184 | 0.00097445 | 0.00038184 | 0.00097445
| Benzene | 71-43-2 | 0.1863 | (2) | 63 | (6) | 65 | (10) | 0.13506 | 0.34467 | 0.13506 |  | 0.34467 | 0.11284 | 0.28795 | 0.13506 | 0.34467 | 0.13506 | 0.34467 | 0.13506 | 0.34467 | 0.11277 | 0.28778 | 0.11277 | 0.28778 | 0.11277 | 0.28778 | 0.15735 | 0.40156 | 0.15735 | 0.40156 | 0.15735 | 0.40156 | 0.15735 | 0.40156 | 0.15735 | 0.40156 | 0.15735 | 0.40156 | 0.15735 | 0.40156 | 0.15735 | 0.40156 | 0.15735 | 0.40156 | 0.15735 | 0.40156 | 0.15735 | 0.40156 | 0.15735 | 0.40156 | 0.15735 | 0.40156 | 0.15735 | 0.40156 | 0.15735 | 0.40156 | 0.15735 | 0.40156 | 0.15735 | 0.40156 | 0.15735 | 0.40156 | 0.15735 | 0.40156 | 0.15735 | 0.40156 | 0.15735 | 0.40156 | 0.13506 | 0.34467 | 0.13506 | 0.34467 | 0.023843 | 0.060846 | 0.13432 | 0.33581 | 0.13432 | 0.33581 | 0.15735 | 0.40156 | 0.15735 | 0.40156 | 0.15735 | 0.40156 | 0.15735 | 0.40156 | 0.15735 | 0.40156 | 0.15735 | 0.40156 | 0.15735 | 0.40156 | 0.15735 | 0.40156
| Chlorobenzene | 108-90-7 | 0.0002 | (2) | 63 | (9) | 63 | (10) | 0.00015328 | 0.00039116 | 0.00015328 |  | 0.00039116 | 0.00012805 | 0.00032679 | 0.00015328 | 0.00039116 | 0.00015328 | 0.00039116 | 0.00015328 | 0.00039116 | 0.00012798 | 0.0003266 | 0.00012798 | 0.0003266 | 0.00012798 | 0.0003266 | 0.00017858 | 0.00045572 | 0.00017858 | 0.00045572 | 0.00017858 | 0.00045572 | 0.00017858 | 0.00045572 | 0.00017858 | 0.00045572 | 0.00017858 | 0.00045572 | 0.00017858 | 0.00045572 | 0.00017858 | 0.00045572 | 0.00017858 | 0.00045572 | 0.00017858 | 0.00045572 | 0.00017858 | 0.00045572 | 0.00017858 | 0.00045572 | 0.00017858 | 0.00045572 | 0.00017858 | 0.00045572 | 0.00017858 | 0.00045572 | 0.00017858 | 0.00045572 | 0.00017858 | 0.00045572 | 0.00017858 | 0.00045572 | 0.00017858 | 0.00045572 | 0.00017858 | 0.00045572 | 0.00017858 | 0.00045572 | 0.00015328 | 0.00039116 | 0.00015328 | 0.00039116 | 2.5596e-05 | 6.532e-05 | 0.00015244 | 0.0003811 | 0.00015244 | 0.0003811 | 0.00017858 | 0.00045572 | 0.00017858 | 0.00045572 | 0.00017858 | 0.00045572 | 0.00017858 | 0.00045572 | 0.00017858 | 0.00045572 | 0.00017858 | 0.00045572 | 0.00017858 | 0.00045572 | 0.00017858 | 0.00045572
| Ethylbenzene | 100-41-4 | 0.0109 | (2) | 63 | (6) | 67 | (10) | 0.0074506 | 0.019014 | 0.0074506 |  | 0.019014 | 0.0062245 | 0.015885 | 0.0074506 | 0.019014 | 0.0074506 | 0.019014 | 0.0074506 | 0.019014 | 0.0062209 | 0.015875 | 0.0062209 | 0.015875 | 0.0062209 | 0.015875 | 0.0086803 | 0.022152 | 0.0086803 | 0.022152 | 0.0086803 | 0.022152 | 0.0086803 | 0.022152 | 0.0086803 | 0.022152 | 0.0086803 | 0.022152 | 0.0086803 | 0.022152 | 0.0086803 | 0.022152 | 0.0086803 | 0.022152 | 0.0086803 | 0.022152 | 0.0086803 | 0.022152 | 0.0086803 | 0.022152 | 0.0086803 | 0.022152 | 0.0086803 | 0.022152 | 0.0086803 | 0.022152 | 0.0086803 | 0.022152 | 0.0086803 | 0.022152 | 0.0086803 | 0.022152 | 0.0086803 | 0.022152 | 0.0086803 | 0.022152 | 0.0086803 | 0.022152 | 0.0074506 | 0.019014 | 0.0074506 | 0.019014 | 0.001395 | 0.0035599 | 0.0074098 | 0.018525 | 0.0074098 | 0.018525 | 0.0086803 | 0.022152 | 0.0086803 | 0.022152 | 0.0086803 | 0.022152 | 0.0086803 | 0.022152 | 0.0086803 | 0.022152 | 0.0086803 | 0.022152 | 0.0086803 | 0.022152 | 0.0086803 | 0.022152
| Formaldehyde | 50-00-0 | 2.7131 | (2) | 59 | (6) | 65 | (10) | 1.9685 | 5.039 | 1.9685 |  | 5.039 | 1.6446 | 4.2097 | 1.9685 | 5.039 | 1.9685 | 5.039 | 1.9685 | 5.039 | 1.6436 | 4.2073 | 1.6436 | 4.2073 | 1.6436 | 4.2073 | 2.2934 | 5.8706 | 2.2934 | 5.8706 | 2.2934 | 5.8706 | 2.2934 | 5.8706 | 2.2934 | 5.8706 | 2.2934 | 5.8706 | 2.2934 | 5.8706 | 2.2934 | 5.8706 | 2.2934 | 5.8706 | 2.2934 | 5.8706 | 2.2934 | 5.8706 | 2.2934 | 5.8706 | 2.2934 | 5.8706 | 2.2934 | 5.8706 | 2.2934 | 5.8706 | 2.2934 | 5.8706 | 2.2934 | 5.8706 | 2.2934 | 5.8706 | 2.2934 | 5.8706 | 2.2934 | 5.8706 | 2.2934 | 5.8706 | 1.9685 | 5.039 | 1.9685 | 5.039 | 0.38507 | 0.98571 | 1.9561 | 4.8903 | 1.9561 | 4.8903 | 2.2934 | 5.8706 | 2.2934 | 5.8706 | 2.2934 | 5.8706 | 2.2934 | 5.8706 | 2.2934 | 5.8706 | 2.2934 | 5.8706 | 2.2934 | 5.8706 | 2.2934 | 5.8706
| Hexane | 110-54-3 | 0.0269 | (2) | 55 | (6) | 60 | (10) | 0.022288 | 0.056877 | 0.022288 |  | 0.056877 | 0.01862 | 0.047517 | 0.022288 | 0.056877 | 0.022288 | 0.056877 | 0.022288 | 0.056877 | 0.018609 | 0.047489 | 0.018609 | 0.047489 | 0.018609 | 0.047489 | 0.025966 | 0.066264 | 0.025966 | 0.066264 | 0.025966 | 0.066264 | 0.025966 | 0.066264 | 0.025966 | 0.066264 | 0.025966 | 0.066264 | 0.025966 | 0.066264 | 0.025966 | 0.066264 | 0.025966 | 0.066264 | 0.025966 | 0.066264 | 0.025966 | 0.066264 | 0.025966 | 0.066264 | 0.025966 | 0.066264 | 0.025966 | 0.066264 | 0.025966 | 0.066264 | 0.025966 | 0.066264 | 0.025966 | 0.066264 | 0.025966 | 0.066264 | 0.025966 | 0.066264 | 0.025966 | 0.066264 | 0.025966 | 0.066264 | 0.022288 | 0.056877 | 0.022288 | 0.056877 | 0.004187 | 0.010685 | 0.022166 | 0.055414 | 0.022166 | 0.055414 | 0.025966 | 0.066264 | 0.025966 | 0.066264 | 0.025966 | 0.066264 | 0.025966 | 0.066264 | 0.025966 | 0.066264 | 0.025966 | 0.066264 | 0.025966 | 0.066264 | 0.025966 | 0.066264
| Propylene | 115-07-1 | 0.47 | (2) | 63 | (9) | 63 | (10) | 0.3602 | 0.91923 | 0.3602 |  | 0.91923 | 0.30093 | 0.76796 | 0.3602 | 0.91923 | 0.3602 | 0.91923 | 0.3602 | 0.91923 | 0.30075 | 0.76751 | 0.30075 | 0.76751 | 0.30075 | 0.76751 | 0.41966 | 1.0709 | 0.41966 | 1.0709 | 0.41966 | 1.0709 | 0.41966 | 1.0709 | 0.41966 | 1.0709 | 0.41966 | 1.0709 | 0.41966 | 1.0709 | 0.41966 | 1.0709 | 0.41966 | 1.0709 | 0.41966 | 1.0709 | 0.41966 | 1.0709 | 0.41966 | 1.0709 | 0.41966 | 1.0709 | 0.41966 | 1.0709 | 0.41966 | 1.0709 | 0.41966 | 1.0709 | 0.41966 | 1.0709 | 0.41966 | 1.0709 | 0.41966 | 1.0709 | 0.41966 | 1.0709 | 0.41966 | 1.0709 | 0.3602 | 0.91923 | 0.3602 | 0.91923 | 0.060151 | 0.1535 | 0.35823 | 0.89559 | 0.35823 | 0.89559 | 0.41966 | 1.0709 | 0.41966 | 1.0709 | 0.41966 | 1.0709 | 0.41966 | 1.0709 | 0.41966 | 1.0709 | 0.41966 | 1.0709 | 0.41966 | 1.0709 | 0.41966 | 1.0709
| Toluene | 108-88-3 | 0.1054 | (2) | 63 | (6) | 73 | (10) | 0.058946 | 0.15043 | 0.058946 |  | 0.15043 | 0.049246 | 0.12567 | 0.058946 | 0.15043 | 0.058946 | 0.15043 | 0.058946 | 0.15043 | 0.049217 | 0.1256 | 0.049217 | 0.1256 | 0.049217 | 0.1256 | 0.068675 | 0.17526 | 0.068675 | 0.17526 | 0.068675 | 0.17526 | 0.068675 | 0.17526 | 0.068675 | 0.17526 | 0.068675 | 0.17526 | 0.068675 | 0.17526 | 0.068675 | 0.17526 | 0.068675 | 0.17526 | 0.068675 | 0.17526 | 0.068675 | 0.17526 | 0.068675 | 0.17526 | 0.068675 | 0.17526 | 0.068675 | 0.17526 | 0.068675 | 0.17526 | 0.068675 | 0.17526 | 0.068675 | 0.17526 | 0.068675 | 0.17526 | 0.068675 | 0.17526 | 0.068675 | 0.17526 | 0.068675 | 0.17526 | 0.058946 | 0.15043 | 0.058946 | 0.15043 | 0.013489 | 0.034424 | 0.058623 | 0.14656 | 0.058623 | 0.14656 | 0.068675 | 0.17526 | 0.068675 | 0.17526 | 0.068675 | 0.17526 | 0.068675 | 0.17526 | 0.068675 | 0.17526 | 0.068675 | 0.17526 | 0.068675 | 0.17526 | 0.068675 | 0.17526
| Xylene (mixed isomers) | 1330-20-7 | 0.0424 | (2) | 63 | (6) | 66 | (10) | 0.02986 | 0.076202 | 0.02986 |  | 0.076202 | 0.024946 | 0.063662 | 0.02986 | 0.076202 | 0.02986 | 0.076202 | 0.02986 | 0.076202 | 0.024932 | 0.063625 | 0.024932 | 0.063625 | 0.024932 | 0.063625 | 0.034789 | 0.088779 | 0.034789 | 0.088779 | 0.034789 | 0.088779 | 0.034789 | 0.088779 | 0.034789 | 0.088779 | 0.034789 | 0.088779 | 0.034789 | 0.088779 | 0.034789 | 0.088779 | 0.034789 | 0.088779 | 0.034789 | 0.088779 | 0.034789 | 0.088779 | 0.034789 | 0.088779 | 0.034789 | 0.088779 | 0.034789 | 0.088779 | 0.034789 | 0.088779 | 0.034789 | 0.088779 | 0.034789 | 0.088779 | 0.034789 | 0.088779 | 0.034789 | 0.088779 | 0.034789 | 0.088779 | 0.034789 | 0.088779 | 0.02986 | 0.076202 | 0.02986 | 0.076202 | 0.0054264 | 0.013848 | 0.029697 | 0.074242 | 0.029697 | 0.074242 | 0.034789 | 0.088779 | 0.034789 | 0.088779 | 0.034789 | 0.088779 | 0.034789 | 0.088779 | 0.034789 | 0.088779 | 0.034789 | 0.088779 | 0.034789 | 0.088779 | 0.034789 | 0.088779
INORGANIC COMPOUNDS
| Ammonia | 7664-41-7 | 0.8 | (2) | 0 |  | 0 |  | 1.6571 | 4.2288 | 1.6571 |  | 4.2288 | 1.3844 | 3.5329 | 1.6571 | 4.2288 | 1.6571 | 4.2288 | 1.6571 | 4.2288 | 1.3836 | 3.5308 | 1.3836 | 3.5308 | 1.3836 | 3.5308 | 1.9306 | 4.9267 | 1.9306 | 4.9267 | 1.9306 | 4.9267 | 1.9306 | 4.9267 | 1.9306 | 4.9267 | 1.9306 | 4.9267 | 1.9306 | 4.9267 | 1.9306 | 4.9267 | 1.9306 | 4.9267 | 1.9306 | 4.9267 | 1.9306 | 4.9267 | 1.9306 | 4.9267 | 1.9306 | 4.9267 | 1.9306 | 4.9267 | 1.9306 | 4.9267 | 1.9306 | 4.9267 | 1.9306 | 4.9267 | 1.9306 | 4.9267 | 1.9306 | 4.9267 | 1.9306 | 4.9267 | 1.9306 | 4.9267 | 1.6571 | 4.2288 | 1.6571 | 4.2288 | 0.27671 | 0.70616 | 1.648 | 4.12 | 1.648 | 4.12 | 1.9306 | 4.9267 | 1.9306 | 4.9267 | 1.9306 | 4.9267 | 1.9306 | 4.9267 | 1.9306 | 4.9267 | 1.9306 | 4.9267 | 1.9306 | 4.9267 | 1.9306 | 4.9267
| Hydrochloric Acid | 7647-01-0 | 0.1863 | (2) | 70 | (6) | 0 |  | 0.38589 | 0.98477 | 0.38589 |  | 0.98477 | 0.32239 | 0.82272 | 0.38589 | 0.98477 | 0.38589 | 0.98477 | 0.38589 | 0.98477 | 0.3222 | 0.82224 | 0.3222 | 0.82224 | 0.3222 | 0.82224 | 0.44958 | 1.1473 | 0.44958 | 1.1473 | 0.44958 | 1.1473 | 0.44958 | 1.1473 | 0.44958 | 1.1473 | 0.44958 | 1.1473 | 0.44958 | 1.1473 | 0.44958 | 1.1473 | 0.44958 | 1.1473 | 0.44958 | 1.1473 | 0.44958 | 1.1473 | 0.44958 | 1.1473 | 0.44958 | 1.1473 | 0.44958 | 1.1473 | 0.44958 | 1.1473 | 0.44958 | 1.1473 | 0.44958 | 1.1473 | 0.44958 | 1.1473 | 0.44958 | 1.1473 | 0.44958 | 1.1473 | 0.44958 | 1.1473 | 0.38589 | 0.98477 | 0.38589 | 0.98477 | 0.019332 | 0.049334 | 0.38378 | 0.95945 | 0.38378 | 0.95945 | 0.44958 | 1.1473 | 0.44958 | 1.1473 | 0.44958 | 1.1473 | 0.44958 | 1.1473 | 0.44958 | 1.1473 | 0.44958 | 1.1473 | 0.44958 | 1.1473 | 0.44958 | 1.1473
POLYCYCLIC AROMATIC HYDROCARBONS (PAH)
| Benz[a]anthracene | 56-55-3 | 4.8541e-05 | (2) | 63 | (6) | 63 | (10) | 3.7202e-05 | 9.4937e-05 | 3.7202e-05 |  | 9.4937e-05 | 3.108e-05 | 7.9314e-05 | 3.7202e-05 | 9.4937e-05 | 3.7202e-05 | 9.4937e-05 | 3.7202e-05 | 9.4937e-05 | 3.1062e-05 | 7.9268e-05 | 3.1062e-05 | 7.9268e-05 | 3.1062e-05 | 7.9268e-05 | 4.3342e-05 | 0.00011061 | 4.3342e-05 | 0.00011061 | 4.3342e-05 | 0.00011061 | 4.3342e-05 | 0.00011061 | 4.3342e-05 | 0.00011061 | 4.3342e-05 | 0.00011061 | 4.3342e-05 | 0.00011061 | 4.3342e-05 | 0.00011061 | 4.3342e-05 | 0.00011061 | 4.3342e-05 | 0.00011061 | 4.3342e-05 | 0.00011061 | 4.3342e-05 | 0.00011061 | 4.3342e-05 | 0.00011061 | 4.3342e-05 | 0.00011061 | 4.3342e-05 | 0.00011061 | 4.3342e-05 | 0.00011061 | 4.3342e-05 | 0.00011061 | 4.3342e-05 | 0.00011061 | 4.3342e-05 | 0.00011061 | 4.3342e-05 | 0.00011061 | 4.3342e-05 | 0.00011061 | 3.7202e-05 | 9.4937e-05 | 3.7202e-05 | 9.4937e-05 | 6.2123e-06 | 1.5854e-05 | 3.6998e-05 | 9.2495e-05 | 3.6998e-05 | 9.2495e-05 | 4.3342e-05 | 0.00011061 | 4.3342e-05 | 0.00011061 | 4.3342e-05 | 0.00011061 | 4.3342e-05 | 0.00011061 | 4.3342e-05 | 0.00011061 | 4.3342e-05 | 0.00011061 | 4.3342e-05 | 0.00011061 | 4.3342e-05 | 0.00011061
| Benzo[a]pyrene | 50-32-8 | 1.4385e-05 | (2) | 63 | (6) | 65 | (10) | 1.0429e-05 | 2.6614e-05 | 1.0429e-05 |  | 2.6614e-05 | 8.7126e-06 | 2.2234e-05 | 1.0429e-05 | 2.6614e-05 | 1.0429e-05 | 2.6614e-05 | 1.0429e-05 | 2.6614e-05 | 8.7075e-06 | 2.2221e-05 | 8.7075e-06 | 2.2221e-05 | 8.7075e-06 | 2.2221e-05 | 1.215e-05 | 3.1007e-05 | 1.215e-05 | 3.1007e-05 | 1.215e-05 | 3.1007e-05 | 1.215e-05 | 3.1007e-05 | 1.215e-05 | 3.1007e-05 | 1.215e-05 | 3.1007e-05 | 1.215e-05 | 3.1007e-05 | 1.215e-05 | 3.1007e-05 | 1.215e-05 | 3.1007e-05 | 1.215e-05 | 3.1007e-05 | 1.215e-05 | 3.1007e-05 | 1.215e-05 | 3.1007e-05 | 1.215e-05 | 3.1007e-05 | 1.215e-05 | 3.1007e-05 | 1.215e-05 | 3.1007e-05 | 1.215e-05 | 3.1007e-05 | 1.215e-05 | 3.1007e-05 | 1.215e-05 | 3.1007e-05 | 1.215e-05 | 3.1007e-05 | 1.215e-05 | 3.1007e-05 | 1.215e-05 | 3.1007e-05 | 1.0429e-05 | 2.6614e-05 | 1.0429e-05 | 2.6614e-05 | 1.841e-06 | 4.6982e-06 | 1.0372e-05 | 2.5929e-05 | 1.0372e-05 | 2.5929e-05 | 1.215e-05 | 3.1007e-05 | 1.215e-05 | 3.1007e-05 | 1.215e-05 | 3.1007e-05 | 1.215e-05 | 3.1007e-05 | 1.215e-05 | 3.1007e-05 | 1.215e-05 | 3.1007e-05 | 1.215e-05 | 3.1007e-05 | 1.215e-05 | 3.1007e-05
| Benzo[b]fluoranthene | 205-99-2 | 4.4354e-05 | (2) | 63 | (6) | 63 | (10) | 3.3992e-05 | 8.6747e-05 | 3.3992e-05 |  | 8.6747e-05 | 2.8398e-05 | 7.2472e-05 | 3.3992e-05 | 8.6747e-05 | 3.3992e-05 | 8.6747e-05 | 3.3992e-05 | 8.6747e-05 | 2.8382e-05 | 7.2429e-05 | 2.8382e-05 | 7.2429e-05 | 2.8382e-05 | 7.2429e-05 | 3.9603e-05 | 0.00010106 | 3.9603e-05 | 0.00010106 | 3.9603e-05 | 0.00010106 | 3.9603e-05 | 0.00010106 | 3.9603e-05 | 0.00010106 | 3.9603e-05 | 0.00010106 | 3.9603e-05 | 0.00010106 | 3.9603e-05 | 0.00010106 | 3.9603e-05 | 0.00010106 | 3.9603e-05 | 0.00010106 | 3.9603e-05 | 0.00010106 | 3.9603e-05 | 0.00010106 | 3.9603e-05 | 0.00010106 | 3.9603e-05 | 0.00010106 | 3.9603e-05 | 0.00010106 | 3.9603e-05 | 0.00010106 | 3.9603e-05 | 0.00010106 | 3.9603e-05 | 0.00010106 | 3.9603e-05 | 0.00010106 | 3.9603e-05 | 0.00010106 | 3.9603e-05 | 0.00010106 | 3.3992e-05 | 8.6747e-05 | 3.3992e-05 | 8.6747e-05 | 5.6764e-06 | 1.4486e-05 | 3.3806e-05 | 8.4516e-05 | 3.3806e-05 | 8.4516e-05 | 3.9603e-05 | 0.00010106 | 3.9603e-05 | 0.00010106 | 3.9603e-05 | 0.00010106 | 3.9603e-05 | 0.00010106 | 3.9603e-05 | 0.00010106 | 3.9603e-05 | 0.00010106 | 3.9603e-05 | 0.00010106 | 3.9603e-05 | 0.00010106
| Benzo[e]pyrene | 192-97-2 | 3.2868e-05 | (2) | 63 | (6) | 65 | (10) | 2.3828e-05 | 6.0809e-05 | 2.3828e-05 |  | 6.0809e-05 | 1.9907e-05 | 5.0802e-05 | 2.3828e-05 | 6.0809e-05 | 2.3828e-05 | 6.0809e-05 | 2.3828e-05 | 6.0809e-05 | 1.9896e-05 | 5.0773e-05 | 1.9896e-05 | 5.0773e-05 | 1.9896e-05 | 5.0773e-05 | 2.7761e-05 | 7.0846e-05 | 2.7761e-05 | 7.0846e-05 | 2.7761e-05 | 7.0846e-05 | 2.7761e-05 | 7.0846e-05 | 2.7761e-05 | 7.0846e-05 | 2.7761e-05 | 7.0846e-05 | 2.7761e-05 | 7.0846e-05 | 2.7761e-05 | 7.0846e-05 | 2.7761e-05 | 7.0846e-05 | 2.7761e-05 | 7.0846e-05 | 2.7761e-05 | 7.0846e-05 | 2.7761e-05 | 7.0846e-05 | 2.7761e-05 | 7.0846e-05 | 2.7761e-05 | 7.0846e-05 | 2.7761e-05 | 7.0846e-05 | 2.7761e-05 | 7.0846e-05 | 2.7761e-05 | 7.0846e-05 | 2.7761e-05 | 7.0846e-05 | 2.7761e-05 | 7.0846e-05 | 2.7761e-05 | 7.0846e-05 | 2.7761e-05 | 7.0846e-05 | 2.3828e-05 | 6.0809e-05 | 2.3828e-05 | 6.0809e-05 | 4.2065e-06 | 1.0735e-05 | 2.3698e-05 | 5.9245e-05 | 2.3698e-05 | 5.9245e-05 | 2.7761e-05 | 7.0846e-05 | 2.7761e-05 | 7.0846e-05 | 2.7761e-05 | 7.0846e-05 | 2.7761e-05 | 7.0846e-05 | 2.7761e-05 | 7.0846e-05 | 2.7761e-05 | 7.0846e-05 | 2.7761e-05 | 7.0846e-05 | 2.7761e-05 | 7.0846e-05
| Benzo[g,h,i]perylene | 191-24-2 | 2.1874e-05 | (2) | 63 | (6) | 63 | (10) | 1.6764e-05 | 4.2782e-05 | 1.6764e-05 |  | 4.2782e-05 | 1.4006e-05 | 3.5742e-05 | 1.6764e-05 | 4.2782e-05 | 1.6764e-05 | 4.2782e-05 | 1.6764e-05 | 4.2782e-05 | 1.3997e-05 | 3.5721e-05 | 1.3997e-05 | 3.5721e-05 | 1.3997e-05 | 3.5721e-05 | 1.9531e-05 | 4.9843e-05 | 1.9531e-05 | 4.9843e-05 | 1.9531e-05 | 4.9843e-05 | 1.9531e-05 | 4.9843e-05 | 1.9531e-05 | 4.9843e-05 | 1.9531e-05 | 4.9843e-05 | 1.9531e-05 | 4.9843e-05 | 1.9531e-05 | 4.9843e-05 | 1.9531e-05 | 4.9843e-05 | 1.9531e-05 | 4.9843e-05 | 1.9531e-05 | 4.9843e-05 | 1.9531e-05 | 4.9843e-05 | 1.9531e-05 | 4.9843e-05 | 1.9531e-05 | 4.9843e-05 | 1.9531e-05 | 4.9843e-05 | 1.9531e-05 | 4.9843e-05 | 1.9531e-05 | 4.9843e-05 | 1.9531e-05 | 4.9843e-05 | 1.9531e-05 | 4.9843e-05 | 1.9531e-05 | 4.9843e-05 | 1.9531e-05 | 4.9843e-05 | 1.6764e-05 | 4.2782e-05 | 1.6764e-05 | 4.2782e-05 | 2.7995e-06 | 7.1442e-06 | 1.6673e-05 | 4.1681e-05 | 1.6673e-05 | 4.1681e-05 | 1.9531e-05 | 4.9843e-05 | 1.9531e-05 | 4.9843e-05 | 1.9531e-05 | 4.9843e-05 | 1.9531e-05 | 4.9843e-05 | 1.9531e-05 | 4.9843e-05 | 1.9531e-05 | 4.9843e-05 | 1.9531e-05 | 4.9843e-05 | 1.9531e-05 | 4.9843e-05
| Benzo[k]fluoranthene | 207-08-9 | 1.3054e-05 | (2) | 63 | (6) | 63 | (10) | 1.0005e-05 | 2.5532e-05 | 1.0005e-05 |  | 2.5532e-05 | 8.3583e-06 | 2.133e-05 | 1.0005e-05 | 2.5532e-05 | 1.0005e-05 | 2.5532e-05 | 1.0005e-05 | 2.5532e-05 | 8.3535e-06 | 2.1318e-05 | 8.3535e-06 | 2.1318e-05 | 8.3535e-06 | 2.1318e-05 | 1.1656e-05 | 2.9746e-05 | 1.1656e-05 | 2.9746e-05 | 1.1656e-05 | 2.9746e-05 | 1.1656e-05 | 2.9746e-05 | 1.1656e-05 | 2.9746e-05 | 1.1656e-05 | 2.9746e-05 | 1.1656e-05 | 2.9746e-05 | 1.1656e-05 | 2.9746e-05 | 1.1656e-05 | 2.9746e-05 | 1.1656e-05 | 2.9746e-05 | 1.1656e-05 | 2.9746e-05 | 1.1656e-05 | 2.9746e-05 | 1.1656e-05 | 2.9746e-05 | 1.1656e-05 | 2.9746e-05 | 1.1656e-05 | 2.9746e-05 | 1.1656e-05 | 2.9746e-05 | 1.1656e-05 | 2.9746e-05 | 1.1656e-05 | 2.9746e-05 | 1.1656e-05 | 2.9746e-05 | 1.1656e-05 | 2.9746e-05 | 1.1656e-05 | 2.9746e-05 | 1.0005e-05 | 2.5532e-05 | 1.0005e-05 | 2.5532e-05 | 1.6707e-06 | 4.2636e-06 | 9.95e-06 | 2.4875e-05 | 9.95e-06 | 2.4875e-05 | 1.1656e-05 | 2.9746e-05 | 1.1656e-05 | 2.9746e-05 | 1.1656e-05 | 2.9746e-05 | 1.1656e-05 | 2.9746e-05 | 1.1656e-05 | 2.9746e-05 | 1.1656e-05 | 2.9746e-05 | 1.1656e-05 | 2.9746e-05 | 1.1656e-05 | 2.9746e-05
| Chrysene | 218-01-9 | 6.7e-05 | (2) | 63 | (6) | 65 | (10) | 4.8573e-05 | 0.00012396 | 4.8573e-05 |  | 0.00012396 | 4.0579e-05 | 0.00010356 | 4.8573e-05 | 0.00012396 | 4.8573e-05 | 0.00012396 | 4.8573e-05 | 0.00012396 | 4.0556e-05 | 0.0001035 | 4.0556e-05 | 0.0001035 | 4.0556e-05 | 0.0001035 | 5.6589e-05 | 0.00014441 | 5.6589e-05 | 0.00014441 | 5.6589e-05 | 0.00014441 | 5.6589e-05 | 0.00014441 | 5.6589e-05 | 0.00014441 | 5.6589e-05 | 0.00014441 | 5.6589e-05 | 0.00014441 | 5.6589e-05 | 0.00014441 | 5.6589e-05 | 0.00014441 | 5.6589e-05 | 0.00014441 | 5.6589e-05 | 0.00014441 | 5.6589e-05 | 0.00014441 | 5.6589e-05 | 0.00014441 | 5.6589e-05 | 0.00014441 | 5.6589e-05 | 0.00014441 | 5.6589e-05 | 0.00014441 | 5.6589e-05 | 0.00014441 | 5.6589e-05 | 0.00014441 | 5.6589e-05 | 0.00014441 | 5.6589e-05 | 0.00014441 | 5.6589e-05 | 0.00014441 | 4.8573e-05 | 0.00012396 | 4.8573e-05 | 0.00012396 | 8.5747e-06 | 2.1882e-05 | 4.8307e-05 | 0.00012077 | 4.8307e-05 | 0.00012077 | 5.6589e-05 | 0.00014441 | 5.6589e-05 | 0.00014441 | 5.6589e-05 | 0.00014441 | 5.6589e-05 | 0.00014441 | 5.6589e-05 | 0.00014441 | 5.6589e-05 | 0.00014441 | 5.6589e-05 | 0.00014441 | 5.6589e-05 | 0.00014441
| Dibenz[a,h]anthracene | 53-70-3 | 1.037e-06 | (2) | 63 | (6) | 65 | (10) | 7.5178e-07 | 1.9185e-06 | 7.5178e-07 |  | 1.9185e-06 | 6.2806e-07 | 1.6028e-06 | 7.5178e-07 | 1.9185e-06 | 7.5178e-07 | 1.9185e-06 | 7.5178e-07 | 1.9185e-06 | 6.277e-07 | 1.6019e-06 | 6.277e-07 | 1.6019e-06 | 6.277e-07 | 1.6019e-06 | 8.7586e-07 | 2.2352e-06 | 8.7586e-07 | 2.2352e-06 | 8.7586e-07 | 2.2352e-06 | 8.7586e-07 | 2.2352e-06 | 8.7586e-07 | 2.2352e-06 | 8.7586e-07 | 2.2352e-06 | 8.7586e-07 | 2.2352e-06 | 8.7586e-07 | 2.2352e-06 | 8.7586e-07 | 2.2352e-06 | 8.7586e-07 | 2.2352e-06 | 8.7586e-07 | 2.2352e-06 | 8.7586e-07 | 2.2352e-06 | 8.7586e-07 | 2.2352e-06 | 8.7586e-07 | 2.2352e-06 | 8.7586e-07 | 2.2352e-06 | 8.7586e-07 | 2.2352e-06 | 8.7586e-07 | 2.2352e-06 | 8.7586e-07 | 2.2352e-06 | 8.7586e-07 | 2.2352e-06 | 8.7586e-07 | 2.2352e-06 | 8.7586e-07 | 2.2352e-06 | 7.5178e-07 | 1.9185e-06 | 7.5178e-07 | 1.9185e-06 | 1.3271e-07 | 3.3868e-07 | 7.4767e-07 | 1.8692e-06 | 7.4767e-07 | 1.8692e-06 | 8.7586e-07 | 2.2352e-06 | 8.7586e-07 | 2.2352e-06 | 8.7586e-07 | 2.2352e-06 | 8.7586e-07 | 2.2352e-06 | 8.7586e-07 | 2.2352e-06 | 8.7586e-07 | 2.2352e-06 | 8.7586e-07 | 2.2352e-06 | 8.7586e-07 | 2.2352e-06
| Fluoranthene | 206-44-0 | 0.00036995 | (2) | 63 | (6) | 68 | (10) | 0.00024521 | 0.00062578 | 0.00024521 |  | 0.00062578 | 0.00020486 | 0.0005228 | 0.00024521 | 0.00062578 | 0.00024521 | 0.00062578 | 0.00024521 | 0.00062578 | 0.00020474 | 0.00052249 | 0.00020474 | 0.00052249 | 0.00020474 | 0.00052249 | 0.00028569 | 0.00072906 | 0.00028569 | 0.00072906 | 0.00028569 | 0.00072906 | 0.00028569 | 0.00072906 | 0.00028569 | 0.00072906 | 0.00028569 | 0.00072906 | 0.00028569 | 0.00072906 | 0.00028569 | 0.00072906 | 0.00028569 | 0.00072906 | 0.00028569 | 0.00072906 | 0.00028569 | 0.00072906 | 0.00028569 | 0.00072906 | 0.00028569 | 0.00072906 | 0.00028569 | 0.00072906 | 0.00028569 | 0.00072906 | 0.00028569 | 0.00072906 | 0.00028569 | 0.00072906 | 0.00028569 | 0.00072906 | 0.00028569 | 0.00072906 | 0.00028569 | 0.00072906 | 0.00028569 | 0.00072906 | 0.00024521 | 0.00062578 | 0.00024521 | 0.00062578 | 4.7347e-05 | 0.00012083 | 0.00024387 | 0.00060968 | 0.00024387 | 0.00060968 | 0.00028569 | 0.00072906 | 0.00028569 | 0.00072906 | 0.00028569 | 0.00072906 | 0.00028569 | 0.00072906 | 0.00028569 | 0.00072906 | 0.00028569 | 0.00072906 | 0.00028569 | 0.00072906 | 0.00028569 | 0.00072906
| Fluorene | 86-73-7 | 0.0021844 | (2) | 63 | (6) | 68 | (10) | 0.0014479 | 0.0036949 | 0.0014479 |  | 0.0036949 | 0.0012096 | 0.0030869 | 0.0014479 | 0.0036949 | 0.0014479 | 0.0036949 | 0.0014479 | 0.0036949 | 0.0012089 | 0.0030851 | 0.0012089 | 0.0030851 | 0.0012089 | 0.0030851 | 0.0016868 | 0.0043048 | 0.0016868 | 0.0043048 | 0.0016868 | 0.0043048 | 0.0016868 | 0.0043048 | 0.0016868 | 0.0043048 | 0.0016868 | 0.0043048 | 0.0016868 | 0.0043048 | 0.0016868 | 0.0043048 | 0.0016868 | 0.0043048 | 0.0016868 | 0.0043048 | 0.0016868 | 0.0043048 | 0.0016868 | 0.0043048 | 0.0016868 | 0.0043048 | 0.0016868 | 0.0043048 | 0.0016868 | 0.0043048 | 0.0016868 | 0.0043048 | 0.0016868 | 0.0043048 | 0.0016868 | 0.0043048 | 0.0016868 | 0.0043048 | 0.0016868 | 0.0043048 | 0.0016868 | 0.0043048 | 0.0014479 | 0.0036949 | 0.0014479 | 0.0036949 | 0.00027956 | 0.00071343 | 0.00144 | 0.0035999 | 0.00144 | 0.0035999 | 0.0016868 | 0.0043048 | 0.0016868 | 0.0043048 | 0.0016868 | 0.0043048 | 0.0016868 | 0.0043048 | 0.0016868 | 0.0043048 | 0.0016868 | 0.0043048 | 0.0016868 | 0.0043048 | 0.0016868 | 0.0043048
| Indeno[1,2,3-cd]pyrene | 193-39-5 | 1.0711e-05 | (2) | 63 | (6) | 70 | (10) | 6.6558e-06 | 1.6985e-05 | 6.6558e-06 |  | 1.6985e-05 | 5.5605e-06 | 1.419e-05 | 6.6558e-06 | 1.6985e-05 | 6.6558e-06 | 1.6985e-05 | 6.6558e-06 | 1.6985e-05 | 5.5573e-06 | 1.4182e-05 | 5.5573e-06 | 1.4182e-05 | 5.5573e-06 | 1.4182e-05 | 7.7543e-06 | 1.9789e-05 | 7.7543e-06 | 1.9789e-05 | 7.7543e-06 | 1.9789e-05 | 7.7543e-06 | 1.9789e-05 | 7.7543e-06 | 1.9789e-05 | 7.7543e-06 | 1.9789e-05 | 7.7543e-06 | 1.9789e-05 | 7.7543e-06 | 1.9789e-05 | 7.7543e-06 | 1.9789e-05 | 7.7543e-06 | 1.9789e-05 | 7.7543e-06 | 1.9789e-05 | 7.7543e-06 | 1.9789e-05 | 7.7543e-06 | 1.9789e-05 | 7.7543e-06 | 1.9789e-05 | 7.7543e-06 | 1.9789e-05 | 7.7543e-06 | 1.9789e-05 | 7.7543e-06 | 1.9789e-05 | 7.7543e-06 | 1.9789e-05 | 7.7543e-06 | 1.9789e-05 | 7.7543e-06 | 1.9789e-05 | 7.7543e-06 | 1.9789e-05 | 6.6558e-06 | 1.6985e-05 | 6.6558e-06 | 1.6985e-05 | 1.3708e-06 | 3.4982e-06 | 6.6194e-06 | 1.6548e-05 | 6.6194e-06 | 1.6548e-05 | 7.7543e-06 | 1.9789e-05 | 7.7543e-06 | 1.9789e-05 | 7.7543e-06 | 1.9789e-05 | 7.7543e-06 | 1.9789e-05 | 7.7543e-06 | 1.9789e-05 | 7.7543e-06 | 1.9789e-05 | 7.7543e-06 | 1.9789e-05 | 7.7543e-06 | 1.9789e-05
| Naphthalene | 91-20-3 | 0.026352 | (2) | 63 | (6) | 65 | (10) | 0.019105 | 0.048754 | 0.019105 |  | 0.048754 | 0.015961 | 0.040731 | 0.019105 | 0.048754 | 0.019105 | 0.048754 | 0.019105 | 0.048754 | 0.015951 | 0.040707 | 0.015951 | 0.040707 | 0.015951 | 0.040707 | 0.022258 | 0.056801 | 0.022258 | 0.056801 | 0.022258 | 0.056801 | 0.022258 | 0.056801 | 0.022258 | 0.056801 | 0.022258 | 0.056801 | 0.022258 | 0.056801 | 0.022258 | 0.056801 | 0.022258 | 0.056801 | 0.022258 | 0.056801 | 0.022258 | 0.056801 | 0.022258 | 0.056801 | 0.022258 | 0.056801 | 0.022258 | 0.056801 | 0.022258 | 0.056801 | 0.022258 | 0.056801 | 0.022258 | 0.056801 | 0.022258 | 0.056801 | 0.022258 | 0.056801 | 0.022258 | 0.056801 | 0.022258 | 0.056801 | 0.019105 | 0.048754 | 0.019105 | 0.048754 | 0.0033726 | 0.0086067 | 0.019 | 0.0475 | 0.019 | 0.0475 | 0.022258 | 0.056801 | 0.022258 | 0.056801 | 0.022258 | 0.056801 | 0.022258 | 0.056801 | 0.022258 | 0.056801 | 0.022258 | 0.056801 | 0.022258 | 0.056801 | 0.022258 | 0.056801
| Perylene | 198-55-0 | 1.1782e-06 | (2) | 63 | (6) | 63 | (10) | 9.03e-07 | 2.3044e-06 | 9.03e-07 |  | 2.3044e-06 | 7.544e-07 | 1.9252e-06 | 9.03e-07 | 2.3044e-06 | 9.03e-07 | 2.3044e-06 | 9.03e-07 | 2.3044e-06 | 7.5396e-07 | 1.9241e-06 | 7.5396e-07 | 1.9241e-06 | 7.5396e-07 | 1.9241e-06 | 1.052e-06 | 2.6848e-06 | 1.052e-06 | 2.6848e-06 | 1.052e-06 | 2.6848e-06 | 1.052e-06 | 2.6848e-06 | 1.052e-06 | 2.6848e-06 | 1.052e-06 | 2.6848e-06 | 1.052e-06 | 2.6848e-06 | 1.052e-06 | 2.6848e-06 | 1.052e-06 | 2.6848e-06 | 1.052e-06 | 2.6848e-06 | 1.052e-06 | 2.6848e-06 | 1.052e-06 | 2.6848e-06 | 1.052e-06 | 2.6848e-06 | 1.052e-06 | 2.6848e-06 | 1.052e-06 | 2.6848e-06 | 1.052e-06 | 2.6848e-06 | 1.052e-06 | 2.6848e-06 | 1.052e-06 | 2.6848e-06 | 1.052e-06 | 2.6848e-06 | 1.052e-06 | 2.6848e-06 | 1.052e-06 | 2.6848e-06 | 9.03e-07 | 2.3044e-06 | 9.03e-07 | 2.3044e-06 | 1.5079e-07 | 3.8482e-07 | 8.9806e-07 | 2.2451e-06 | 8.9806e-07 | 2.2451e-06 | 1.052e-06 | 2.6848e-06 | 1.052e-06 | 2.6848e-06 | 1.052e-06 | 2.6848e-06 | 1.052e-06 | 2.6848e-06 | 1.052e-06 | 2.6848e-06 | 1.052e-06 | 2.6848e-06 | 1.052e-06 | 2.6848e-06 | 1.052e-06 | 2.6848e-06
| Phenanthrene | 85-01-8 | 0.0045419 | (2) | 63 | (6) | 63 | (10) | 0.0034809 | 0.0088832 | 0.0034809 |  | 0.0088832 | 0.0029081 | 0.0074213 | 0.0034809 | 0.0088832 | 0.0034809 | 0.0088832 | 0.0034809 | 0.0088832 | 0.0029064 | 0.007417 | 0.0029064 | 0.007417 | 0.0029064 | 0.007417 | 0.0040554 | 0.010349 | 0.0040554 | 0.010349 | 0.0040554 | 0.010349 | 0.0040554 | 0.010349 | 0.0040554 | 0.010349 | 0.0040554 | 0.010349 | 0.0040554 | 0.010349 | 0.0040554 | 0.010349 | 0.0040554 | 0.010349 | 0.0040554 | 0.010349 | 0.0040554 | 0.010349 | 0.0040554 | 0.010349 | 0.0040554 | 0.010349 | 0.0040554 | 0.010349 | 0.0040554 | 0.010349 | 0.0040554 | 0.010349 | 0.0040554 | 0.010349 | 0.0040554 | 0.010349 | 0.0040554 | 0.010349 | 0.0040554 | 0.010349 | 0.0040554 | 0.010349 | 0.0034809 | 0.0088832 | 0.0034809 | 0.0088832 | 0.00058128 | 0.0014834 | 0.0034619 | 0.0086547 | 0.0034619 | 0.0086547 | 0.0040554 | 0.010349 | 0.0040554 | 0.010349 | 0.0040554 | 0.010349 | 0.0040554 | 0.010349 | 0.0040554 | 0.010349 | 0.0040554 | 0.010349 | 0.0040554 | 0.010349 | 0.0040554 | 0.010349
| Pyrene | 129-00-0 | 0.00125 | (2) | 63 | (6) | 63 | (10) | 0.00095799 | 0.0024448 | 0.00095799 |  | 0.0024448 | 0.00080034 | 0.0020424 | 0.00095799 | 0.0024448 | 0.00095799 | 0.0024448 | 0.00095799 | 0.0024448 | 0.00079988 | 0.0020413 | 0.00079988 | 0.0020413 | 0.00079988 | 0.0020413 | 0.0011161 | 0.0028483 | 0.0011161 | 0.0028483 | 0.0011161 | 0.0028483 | 0.0011161 | 0.0028483 | 0.0011161 | 0.0028483 | 0.0011161 | 0.0028483 | 0.0011161 | 0.0028483 | 0.0011161 | 0.0028483 | 0.0011161 | 0.0028483 | 0.0011161 | 0.0028483 | 0.0011161 | 0.0028483 | 0.0011161 | 0.0028483 | 0.0011161 | 0.0028483 | 0.0011161 | 0.0028483 | 0.0011161 | 0.0028483 | 0.0011161 | 0.0028483 | 0.0011161 | 0.0028483 | 0.0011161 | 0.0028483 | 0.0011161 | 0.0028483 | 0.0011161 | 0.0028483 | 0.0011161 | 0.0028483 | 0.00095799 | 0.0024448 | 0.00095799 | 0.0024448 | 0.00015998 | 0.00040825 | 0.00095275 | 0.0023819 | 0.00095275 | 0.0023819 | 0.0011161 | 0.0028483 | 0.0011161 | 0.0028483 | 0.0011161 | 0.0028483 | 0.0011161 | 0.0028483 | 0.0011161 | 0.0028483 | 0.0011161 | 0.0028483 | 0.0011161 | 0.0028483 | 0.0011161 | 0.0028483
DIESEL PARTICULATE MATTER (DPM)
| DPM | 200 | 16.9752 | (2) | 90 | (7) | 93 | (8) | 2.4613 | 6.2811 | 2.4613 |  | 6.2811 | 2.0563 | 5.2475 | 2.4613 | 6.2811 | 2.4613 | 6.2811 | 2.4613 | 6.2811 | 2.0551 | 5.2444 | 2.0551 | 5.2444 | 2.0551 | 5.2444 | 2.8675 | 7.3178 | 2.8675 | 7.3178 | 2.8675 | 7.3178 | 2.8675 | 7.3178 | 2.8675 | 7.3178 | 2.8675 | 7.3178 | 2.8675 | 7.3178 | 2.8675 | 7.3178 | 2.8675 | 7.3178 | 2.8675 | 7.3178 | 2.8675 | 7.3178 | 2.8675 | 7.3178 | 2.8675 | 7.3178 | 2.8675 | 7.3178 | 2.8675 | 7.3178 | 2.8675 | 7.3178 | 2.8675 | 7.3178 | 2.8675 | 7.3178 | 2.8675 | 7.3178 | 2.8675 | 7.3178 | 2.8675 | 7.3178 | 2.4613 | 6.2811 | 2.4613 | 6.2811 | 0.58716 | 1.4984 | 2.4478 | 6.1196 | 2.4478 | 6.1196 | 2.8675 | 7.3178 | 2.8675 | 7.3178 | 2.8675 | 7.3178 | 2.8675 | 7.3178 | 2.8675 | 7.3178 | 2.8675 | 7.3178 | 2.8675 | 7.3178 | 2.8675 | 7.3178
Notes
DPF = Diesel Particulate Filter; HAP = Hazardous Air Pollutant; Mgal = 1,000 gallons; TAC = Toxic Air Contaminant.
(a) | Daily emissions estimate (lb/day) = ([emission factor {lb/Mgal}] x [fuel consumption {gal/hr}] x [daily hours of operation {hrs/day}] x [Mgal/1,000 gal] | [10 empty] | (b), (c)
+ [cold start emissions {lb/minute}] x [number of cold starts per day] - [emissions per minute, normal operation {lb/minute}] x [number of cold starts per day])
| x (1 - [DPF control efficiency {%}] / 100)) | [8 empty] | (3)
|  | Cold start adjustment factor = | 4.3 | (4)
|  | Cold start adjustment factor (formaldehyde) = | 4.8 | (4)
|  | Number of cold starts per day = | 1 | (5)
(b) | Cold start emissions (lb/minute) = (emission factor [lb/Mgal]) x (cold start adjustment factor) x (hourly fuel consumption [Mgal/hr]) / 60
(c) | Emissions per minute, normal operation (lb/minute) = (emission factor [lb/Mgal]) x (hourly fuel consumption [Mgal/hr]) / 60
(d) | Annual emissions estimate (lb/yr) = ([emission factor {lb/Mgal}] x [fuel consumption {gal/hr}] x [annual hours of operation {hrs/yr}] x [Mgal/1,000 gal] | [10 empty] | (b), (c)
+ [cold start emissions {lb/minute}] x [number of cold starts per year] - [emissions per minute, normal operation {lb/minute}] x [number of cold starts per year])
| x (1 - [DPF control efficiency {%}] / 100)) | [8 empty] | (3)
|  | Cold start adjustment factor = | 4.3 | (4)
|  | Cold start adjustment factor (formaldehyde) = | 4.8 | (4)
|  | Number of cold starts per year = | 12 | (5)
References
(1) | Permit conditions limit Intel to operate 10 EGENs for 10 hours a day and all EGENs for 25 hours a year.
(2) | Emission Factors from the Oregon Department of Environmental Quality, AQ104B, diesel internal combustion, greater
than 750 hp. Ammonia emission factor assumes value for no SNCR or SCR control. DEQ reference CAO Diesel RICE (b).
(3) | Time allotted for cold stats was omitted from the daily/annual operating capacity in emission calculations. Cold start adjustments are not required for metals.
(4) | Cold start adjustment factors provided by the Oregon Department of Environmental Quality. All applicable pollutants, except
formaldehyde, share the same adjustment factor. Cold start adjustments are not required for metals.
(5) | Based on one cold start per month per engine for Preventative Maintenance activities.
(6) | Information provided by Rypos, Inc.
(7) | Value based on filterable PM efficiency provided by Rypos.
(8) | Value based on filterable PM efficiency provided by Johnson Matthey.
(9) | Value based on similar TAC.
(10) | Information provided by Johnson Matthey.
(11) | Per DEQ guidance, assumed 70%

## EGENnoDPF_a_RONLER
TESU ID |  |  |  |  | RA1-ELEC-CPS-GEN01 |  | RA1-ELEC-CPS-GEN02 |  | RA1-ELEC-CPS-GEN03 |  |  | RA1-ELEC-CPS-GEN04 |  | D1C-CPS-GEN01 |  | D1C-CPS-GEN02 |  | D1C-CPS-GEN03 |  | D1C-EPS-GEN01 |  | D1C-EPS-GEN02 |  | RB1-EPS-GEN01 |  | RP1-EPS-GEN01 |  | EPS-GEN01 |  | EPS-GEN02 |  | EPS-GEN03 |  | EPS-GEN04 |  | EPS-GEN05 |  | EPS-GEN06 |  | RS4-ELEC-EG-4-1 |  | RS6-ELEC-EG-6-1 |  | F20-CPS-1 |  | MAX-EGEN
Fuel Consumption (gal/hr) |  |  |  |  | 113.51 |  | 113.51 |  | 113.51 |  |  | 113.51 |  | 89.71 |  | 89.71 |  | 89.71 |  | 208 |  | 208 |  | 137.5 |  | 145.4 |  | 147.46 |  | 147.46 |  | 147.46 |  | 147.46 |  | 147.46 |  | 147.46 |  | 22.9 |  | 22.9 |  | 46.4 |  | 19.4
Daily Hours of Operation (hrs/day) |  |  |  | (1) | 10 |  | 10 |  | 10 |  |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10
Annual Hours of Operation (hrs/yr) |  |  |  | (1) | 25 |  | 25 |  | 25 |  |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25
Pollutant |  | CAS | Emission Factor (2) (lb/Mgal) |  | Emissions Estimate (a) | [34 empty] | Emissions Estimate (a)
[5 empty] | RA1-ELEC-CPS-GEN01 |  | RA1-ELEC-CPS-GEN02 |  | RA1-ELEC-CPS-GEN03 |  |  | RA1-ELEC-CPS-GEN04 |  | D1C-CPS-GEN01 |  | D1C-CPS-GEN02 |  | D1C-CPS-GEN03 |  | D1C-EPS-GEN01 |  | D1C-EPS-GEN02 |  | RB1-EPS-GEN01 |  | RP1-EPS-GEN01 |  | EPS-GEN01 |  | EPS-GEN02 |  | EPS-GEN03 |  | EPS-GEN04 |  | EPS-GEN05 |  | EPS-GEN06 |  | RS4-ELEC-EG-4-1 |  | RS6-ELEC-EG-6-1 |  | F20-CPS-1 |  | MAX-EGEN
[5 empty] | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) |  | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr)
METALS
| Antimony and Compounds | 7440-36-0 | 0.00031819 |  | 0.00036117 | 0.00090294 | 0.00036117 | 0.00090294 | 0.00036117 | 0.00090294 |  | 0.00036117 | 0.00090294 | 0.00028545 | 0.00071361 | 0.00028545 | 0.00071361 | 0.00028545 | 0.00071361 | 0.00066183 | 0.0016546 | 0.00066183 | 0.0016546 | 0.00043751 | 0.0010938 | 0.00046264 | 0.0011566 | 0.0004692 | 0.001173 | 0.0004692 | 0.001173 | 0.0004692 | 0.001173 | 0.0004692 | 0.001173 | 0.0004692 | 0.001173 | 0.0004692 | 0.001173 | 7.2865e-05 | 0.00018216 | 7.2865e-05 | 0.00018216 | 0.00014764 | 0.0003691 | 6.1728e-05 | 0.00015432
| Arsenic and Compounds | 7440-38-2 | 0.0016 |  | 0.0018162 | 0.0045404 | 0.0018162 | 0.0045404 | 0.0018162 | 0.0045404 |  | 0.0018162 | 0.0045404 | 0.0014354 | 0.0035884 | 0.0014354 | 0.0035884 | 0.0014354 | 0.0035884 | 0.003328 | 0.00832 | 0.003328 | 0.00832 | 0.0022 | 0.0055 | 0.0023264 | 0.005816 | 0.0023594 | 0.0058984 | 0.0023594 | 0.0058984 | 0.0023594 | 0.0058984 | 0.0023594 | 0.0058984 | 0.0023594 | 0.0058984 | 0.0023594 | 0.0058984 | 0.0003664 | 0.000916 | 0.0003664 | 0.000916 | 0.0007424 | 0.001856 | 0.0003104 | 0.000776
| Barium and Compounds | 7440-39-3 | 0.00037389 |  | 0.00042441 | 0.001061 | 0.00042441 | 0.001061 | 0.00042441 | 0.001061 |  | 0.00042441 | 0.001061 | 0.00033542 | 0.00083855 | 0.00033542 | 0.00083855 | 0.00033542 | 0.00083855 | 0.0007777 | 0.0019442 | 0.0007777 | 0.0019442 | 0.0005141 | 0.0012853 | 0.00054364 | 0.0013591 | 0.00055134 | 0.0013784 | 0.00055134 | 0.0013784 | 0.00055134 | 0.0013784 | 0.00055134 | 0.0013784 | 0.00055134 | 0.0013784 | 0.00055134 | 0.0013784 | 8.5622e-05 | 0.00021405 | 8.5622e-05 | 0.00021405 | 0.00017349 | 0.00043372 | 7.2535e-05 | 0.00018134
| Beryllium and compounds | 7440-41-7 | 4.7708e-06 |  | 5.4154e-06 | 1.3538e-05 | 5.4154e-06 | 1.3538e-05 | 5.4154e-06 | 1.3538e-05 |  | 5.4154e-06 | 1.3538e-05 | 4.2799e-06 | 1.07e-05 | 4.2799e-06 | 1.07e-05 | 4.2799e-06 | 1.07e-05 | 9.9234e-06 | 2.4808e-05 | 9.9234e-06 | 2.4808e-05 | 6.5599e-06 | 1.64e-05 | 6.9368e-06 | 1.7342e-05 | 7.0351e-06 | 1.7588e-05 | 7.0351e-06 | 1.7588e-05 | 7.0351e-06 | 1.7588e-05 | 7.0351e-06 | 1.7588e-05 | 7.0351e-06 | 1.7588e-05 | 7.0351e-06 | 1.7588e-05 | 1.0925e-06 | 2.7313e-06 | 1.0925e-06 | 2.7313e-06 | 2.2137e-06 | 5.5342e-06 | 9.2554e-07 | 2.3139e-06
| Cadmium and Compounds | 7440-43-9 | 0.0015 |  | 0.0017026 | 0.0042566 | 0.0017026 | 0.0042566 | 0.0017026 | 0.0042566 |  | 0.0017026 | 0.0042566 | 0.0013457 | 0.0033641 | 0.0013457 | 0.0033641 | 0.0013457 | 0.0033641 | 0.00312 | 0.0078 | 0.00312 | 0.0078 | 0.0020625 | 0.0051563 | 0.002181 | 0.0054525 | 0.0022119 | 0.0055298 | 0.0022119 | 0.0055298 | 0.0022119 | 0.0055298 | 0.0022119 | 0.0055298 | 0.0022119 | 0.0055298 | 0.0022119 | 0.0055298 | 0.0003435 | 0.00085875 | 0.0003435 | 0.00085875 | 0.000696 | 0.00174 | 0.000291 | 0.0007275
| Chromium VI | 18540-29-9 | 0.0001 |  | 0.00011351 | 0.00028378 | 0.00011351 | 0.00028378 | 0.00011351 | 0.00028378 |  | 0.00011351 | 0.00028378 | 8.971e-05 | 0.00022427 | 8.971e-05 | 0.00022427 | 8.971e-05 | 0.00022427 | 0.000208 | 0.00052 | 0.000208 | 0.00052 | 0.0001375 | 0.00034375 | 0.0001454 | 0.0003635 | 0.00014746 | 0.00036865 | 0.00014746 | 0.00036865 | 0.00014746 | 0.00036865 | 0.00014746 | 0.00036865 | 0.00014746 | 0.00036865 | 0.00014746 | 0.00036865 | 2.29e-05 | 5.725e-05 | 2.29e-05 | 5.725e-05 | 4.64e-05 | 0.000116 | 1.94e-05 | 4.85e-05
| Copper and Compounds | 7440-50-8 | 0.0041 |  | 0.0046539 | 0.011635 | 0.0046539 | 0.011635 | 0.0046539 | 0.011635 |  | 0.0046539 | 0.011635 | 0.0036781 | 0.0091953 | 0.0036781 | 0.0091953 | 0.0036781 | 0.0091953 | 0.008528 | 0.02132 | 0.008528 | 0.02132 | 0.0056375 | 0.014094 | 0.0059614 | 0.014904 | 0.0060459 | 0.015115 | 0.0060459 | 0.015115 | 0.0060459 | 0.015115 | 0.0060459 | 0.015115 | 0.0060459 | 0.015115 | 0.0060459 | 0.015115 | 0.0009389 | 0.0023472 | 0.0009389 | 0.0023472 | 0.0019024 | 0.004756 | 0.0007954 | 0.0019885
| Cobalt and compounds | 7440-48-4 | 1.5751e-05 |  | 1.7879e-05 | 4.4698e-05 | 1.7879e-05 | 4.4698e-05 | 1.7879e-05 | 4.4698e-05 |  | 1.7879e-05 | 4.4698e-05 | 1.413e-05 | 3.5326e-05 | 1.413e-05 | 3.5326e-05 | 1.413e-05 | 3.5326e-05 | 3.2762e-05 | 8.1906e-05 | 3.2762e-05 | 8.1906e-05 | 2.1658e-05 | 5.4145e-05 | 2.2902e-05 | 5.7255e-05 | 2.3227e-05 | 5.8067e-05 | 2.3227e-05 | 5.8067e-05 | 2.3227e-05 | 5.8067e-05 | 2.3227e-05 | 5.8067e-05 | 2.3227e-05 | 5.8067e-05 | 2.3227e-05 | 5.8067e-05 | 3.607e-06 | 9.0175e-06 | 3.607e-06 | 9.0175e-06 | 7.3085e-06 | 1.8271e-05 | 3.0557e-06 | 7.6393e-06
| Lead and Compounds | 7439-92-1 | 0.0083 |  | 0.0094213 | 0.023553 | 0.0094213 | 0.023553 | 0.0094213 | 0.023553 |  | 0.0094213 | 0.023553 | 0.0074459 | 0.018615 | 0.0074459 | 0.018615 | 0.0074459 | 0.018615 | 0.017264 | 0.04316 | 0.017264 | 0.04316 | 0.011413 | 0.028531 | 0.012068 | 0.03017 | 0.012239 | 0.030598 | 0.012239 | 0.030598 | 0.012239 | 0.030598 | 0.012239 | 0.030598 | 0.012239 | 0.030598 | 0.012239 | 0.030598 | 0.0019007 | 0.0047517 | 0.0019007 | 0.0047517 | 0.0038512 | 0.009628 | 0.0016102 | 0.0040255
| Manganese and Compounds | 7439-96-5 | 0.0031 |  | 0.0035188 | 0.008797 | 0.0035188 | 0.008797 | 0.0035188 | 0.008797 |  | 0.0035188 | 0.008797 | 0.002781 | 0.0069525 | 0.002781 | 0.0069525 | 0.002781 | 0.0069525 | 0.006448 | 0.01612 | 0.006448 | 0.01612 | 0.0042625 | 0.010656 | 0.0045074 | 0.011269 | 0.0045713 | 0.011428 | 0.0045713 | 0.011428 | 0.0045713 | 0.011428 | 0.0045713 | 0.011428 | 0.0045713 | 0.011428 | 0.0045713 | 0.011428 | 0.0007099 | 0.0017748 | 0.0007099 | 0.0017748 | 0.0014384 | 0.003596 | 0.0006014 | 0.0015035
| Mercury and Compounds | 7439-97-6 | 0.002 |  | 0.0022702 | 0.0056755 | 0.0022702 | 0.0056755 | 0.0022702 | 0.0056755 |  | 0.0022702 | 0.0056755 | 0.0017942 | 0.0044855 | 0.0017942 | 0.0044855 | 0.0017942 | 0.0044855 | 0.00416 | 0.0104 | 0.00416 | 0.0104 | 0.00275 | 0.006875 | 0.002908 | 0.00727 | 0.0029492 | 0.007373 | 0.0029492 | 0.007373 | 0.0029492 | 0.007373 | 0.0029492 | 0.007373 | 0.0029492 | 0.007373 | 0.0029492 | 0.007373 | 0.000458 | 0.001145 | 0.000458 | 0.001145 | 0.000928 | 0.00232 | 0.000388 | 0.00097
| Nickel and Compounds | 7440-02-0 | 0.0039 |  | 0.0044269 | 0.011067 | 0.0044269 | 0.011067 | 0.0044269 | 0.011067 |  | 0.0044269 | 0.011067 | 0.0034987 | 0.0087467 | 0.0034987 | 0.0087467 | 0.0034987 | 0.0087467 | 0.008112 | 0.02028 | 0.008112 | 0.02028 | 0.0053625 | 0.013406 | 0.0056706 | 0.014177 | 0.0057509 | 0.014377 | 0.0057509 | 0.014377 | 0.0057509 | 0.014377 | 0.0057509 | 0.014377 | 0.0057509 | 0.014377 | 0.0057509 | 0.014377 | 0.0008931 | 0.0022327 | 0.0008931 | 0.0022327 | 0.0018096 | 0.004524 | 0.0007566 | 0.0018915
| Phosphorus and compounds | 504 | 0.008404 |  | 0.0095394 | 0.023848 | 0.0095394 | 0.023848 | 0.0095394 | 0.023848 |  | 0.0095394 | 0.023848 | 0.0075392 | 0.018848 | 0.0075392 | 0.018848 | 0.0075392 | 0.018848 | 0.01748 | 0.043701 | 0.01748 | 0.043701 | 0.011555 | 0.028889 | 0.012219 | 0.030548 | 0.012393 | 0.030981 | 0.012393 | 0.030981 | 0.012393 | 0.030981 | 0.012393 | 0.030981 | 0.012393 | 0.030981 | 0.012393 | 0.030981 | 0.0019245 | 0.0048113 | 0.0019245 | 0.0048113 | 0.0038994 | 0.0097486 | 0.0016304 | 0.0040759
| Selenium and Compounds | 7782-49-2 | 0.0022 |  | 0.0024972 | 0.0062431 | 0.0024972 | 0.0062431 | 0.0024972 | 0.0062431 |  | 0.0024972 | 0.0062431 | 0.0019736 | 0.004934 | 0.0019736 | 0.004934 | 0.0019736 | 0.004934 | 0.004576 | 0.01144 | 0.004576 | 0.01144 | 0.003025 | 0.0075625 | 0.0031988 | 0.007997 | 0.0032441 | 0.0081103 | 0.0032441 | 0.0081103 | 0.0032441 | 0.0081103 | 0.0032441 | 0.0081103 | 0.0032441 | 0.0081103 | 0.0032441 | 0.0081103 | 0.0005038 | 0.0012595 | 0.0005038 | 0.0012595 | 0.0010208 | 0.002552 | 0.0004268 | 0.001067
| Silver and compounds | 7440-22-4 | 4.8013e-05 |  | 5.45e-05 | 0.00013625 | 5.45e-05 | 0.00013625 | 5.45e-05 | 0.00013625 |  | 5.45e-05 | 0.00013625 | 4.3072e-05 | 0.00010768 | 4.3072e-05 | 0.00010768 | 4.3072e-05 | 0.00010768 | 9.9867e-05 | 0.00024967 | 9.9867e-05 | 0.00024967 | 6.6018e-05 | 0.00016504 | 6.9811e-05 | 0.00017453 | 7.08e-05 | 0.000177 | 7.08e-05 | 0.000177 | 7.08e-05 | 0.000177 | 7.08e-05 | 0.000177 | 7.08e-05 | 0.000177 | 7.08e-05 | 0.000177 | 1.0995e-05 | 2.7487e-05 | 1.0995e-05 | 2.7487e-05 | 2.2278e-05 | 5.5695e-05 | 9.3145e-06 | 2.3286e-05
| Thallium and compounds | 7440-28-0 | 0.00024009 |  | 0.00027253 | 0.00068133 | 0.00027253 | 0.00068133 | 0.00027253 | 0.00068133 |  | 0.00027253 | 0.00068133 | 0.00021539 | 0.00053847 | 0.00021539 | 0.00053847 | 0.00021539 | 0.00053847 | 0.00049939 | 0.0012485 | 0.00049939 | 0.0012485 | 0.00033013 | 0.00082532 | 0.0003491 | 0.00087274 | 0.00035404 | 0.00088511 | 0.00035404 | 0.00088511 | 0.00035404 | 0.00088511 | 0.00035404 | 0.00088511 | 0.00035404 | 0.00088511 | 0.00035404 | 0.00088511 | 5.4981e-05 | 0.00013745 | 5.4981e-05 | 0.00013745 | 0.0001114 | 0.00027851 | 4.6578e-05 | 0.00011645
| Zinc and compounds | 7440-66-6 | 0.0052262 |  | 0.0059322 | 0.014831 | 0.0059322 | 0.014831 | 0.0059322 | 0.014831 |  | 0.0059322 | 0.014831 | 0.0046884 | 0.011721 | 0.0046884 | 0.011721 | 0.0046884 | 0.011721 | 0.01087 | 0.027176 | 0.01087 | 0.027176 | 0.007186 | 0.017965 | 0.0075989 | 0.018997 | 0.0077065 | 0.019266 | 0.0077065 | 0.019266 | 0.0077065 | 0.019266 | 0.0077065 | 0.019266 | 0.0077065 | 0.019266 | 0.0077065 | 0.019266 | 0.0011968 | 0.002992 | 0.0011968 | 0.002992 | 0.0024249 | 0.0060624 | 0.0010139 | 0.0025347
ORGANIC COMPOUNDS
| 1,3-Butadiene | 106-99-0 | 0.2174 |  | 0.24813 | 0.63321 | 0.24813 | 0.63321 | 0.24813 | 0.63321 |  | 0.24813 | 0.63321 | 0.1961 | 0.50045 | 0.1961 | 0.50045 | 0.1961 | 0.50045 | 0.45468 | 1.1603 | 0.45468 | 1.1603 | 0.30057 | 0.76704 | 0.31784 | 0.81111 | 0.32234 | 0.8226 | 0.32234 | 0.8226 | 0.32234 | 0.8226 | 0.32234 | 0.8226 | 0.32234 | 0.8226 | 0.32234 | 0.8226 | 0.050058 | 0.12775 | 0.050058 | 0.12775 | 0.10143 | 0.25884 | 0.042408 | 0.10822
| Acetaldehyde | 75-07-0 | 0.7833 |  | 0.89401 | 2.2815 | 0.89401 | 2.2815 | 0.89401 | 2.2815 |  | 0.89401 | 2.2815 | 0.70656 | 1.8031 | 0.70656 | 1.8031 | 0.70656 | 1.8031 | 1.6382 | 4.1807 | 1.6382 | 4.1807 | 1.083 | 2.7637 | 1.1452 | 2.9225 | 1.1614 | 2.9639 | 1.1614 | 2.9639 | 1.1614 | 2.9639 | 1.1614 | 2.9639 | 1.1614 | 2.9639 | 1.1614 | 2.9639 | 0.18036 | 0.46028 | 0.18036 | 0.46028 | 0.36545 | 0.93262 | 0.1528 | 0.38993
| Acrolein | 107-02-8 | 0.0339 |  | 0.038692 | 0.098739 | 0.038692 | 0.098739 | 0.038692 | 0.098739 |  | 0.038692 | 0.098739 | 0.030579 | 0.078036 | 0.030579 | 0.078036 | 0.030579 | 0.078036 | 0.0709 | 0.18093 | 0.0709 | 0.18093 | 0.046869 | 0.11961 | 0.049562 | 0.12648 | 0.050264 | 0.12827 | 0.050264 | 0.12827 | 0.050264 | 0.12827 | 0.050264 | 0.12827 | 0.050264 | 0.12827 | 0.050264 | 0.12827 | 0.0078058 | 0.01992 | 0.0078058 | 0.01992 | 0.015816 | 0.040362 | 0.0066128 | 0.016876
| Benzene | 71-43-2 | 0.1863 |  | 0.21263 | 0.54263 | 0.21263 | 0.54263 | 0.21263 | 0.54263 |  | 0.21263 | 0.54263 | 0.16805 | 0.42885 | 0.16805 | 0.42885 | 0.16805 | 0.42885 | 0.38964 | 0.99434 | 0.38964 | 0.99434 | 0.25757 | 0.65731 | 0.27237 | 0.69508 | 0.27623 | 0.70493 | 0.27623 | 0.70493 | 0.27623 | 0.70493 | 0.27623 | 0.70493 | 0.27623 | 0.70493 | 0.27623 | 0.70493 | 0.042897 | 0.10947 | 0.042897 | 0.10947 | 0.086919 | 0.22181 | 0.036341 | 0.092741
| Chlorobenzene | 108-90-7 | 0.0002 |  | 0.00022827 | 0.00058253 | 0.00022827 | 0.00058253 | 0.00022827 | 0.00058253 |  | 0.00022827 | 0.00058253 | 0.00018041 | 0.00046039 | 0.00018041 | 0.00046039 | 0.00018041 | 0.00046039 | 0.00041829 | 0.0010675 | 0.00041829 | 0.0010675 | 0.00027651 | 0.00070565 | 0.0002924 | 0.00074619 | 0.00029654 | 0.00075676 | 0.00029654 | 0.00075676 | 0.00029654 | 0.00075676 | 0.00029654 | 0.00075676 | 0.00029654 | 0.00075676 | 0.00029654 | 0.00075676 | 4.6052e-05 | 0.00011752 | 4.6052e-05 | 0.00011752 | 9.331e-05 | 0.00023812 | 3.9013e-05 | 9.9561e-05
| Ethylbenzene | 100-41-4 | 0.0109 |  | 0.012441 | 0.031748 | 0.012441 | 0.031748 | 0.012441 | 0.031748 |  | 0.012441 | 0.031748 | 0.0098322 | 0.025091 | 0.0098322 | 0.025091 | 0.0098322 | 0.025091 | 0.022797 | 0.058176 | 0.022797 | 0.058176 | 0.01507 | 0.038458 | 0.015936 | 0.040668 | 0.016162 | 0.041244 | 0.016162 | 0.041244 | 0.016162 | 0.041244 | 0.016162 | 0.041244 | 0.016162 | 0.041244 | 0.016162 | 0.041244 | 0.0025098 | 0.006405 | 0.0025098 | 0.006405 | 0.0050854 | 0.012978 | 0.0021262 | 0.0054261
| Formaldehyde | 50-00-0 | 1.7261 |  | 1.9717 | 5.0471 | 1.9717 | 5.0471 | 1.9717 | 5.0471 |  | 1.9717 | 5.0471 | 1.5583 | 3.9889 | 1.5583 | 3.9889 | 1.5583 | 3.9889 | 3.613 | 9.2486 | 3.613 | 9.2486 | 2.3884 | 6.1138 | 2.5256 | 6.4651 | 2.5614 | 6.5567 | 2.5614 | 6.5567 | 2.5614 | 6.5567 | 2.5614 | 6.5567 | 2.5614 | 6.5567 | 2.5614 | 6.5567 | 0.39778 | 1.0182 | 0.39778 | 1.0182 | 0.80598 | 2.0631 | 0.33698 | 0.86261
| Hexane | 110-54-3 | 0.0269 |  | 0.030702 | 0.078351 | 0.030702 | 0.078351 | 0.030702 | 0.078351 |  | 0.030702 | 0.078351 | 0.024265 | 0.061923 | 0.024265 | 0.061923 | 0.024265 | 0.061923 | 0.05626 | 0.14357 | 0.05626 | 0.14357 | 0.037191 | 0.09491 | 0.039328 | 0.10036 | 0.039885 | 0.10178 | 0.039885 | 0.10178 | 0.039885 | 0.10178 | 0.039885 | 0.10178 | 0.039885 | 0.10178 | 0.039885 | 0.10178 | 0.006194 | 0.015807 | 0.006194 | 0.015807 | 0.01255 | 0.032028 | 0.0052473 | 0.013391
| Propylene | 115-07-1 | 0.47 |  | 0.53643 | 1.369 | 0.53643 | 1.369 | 0.53643 | 1.369 |  | 0.53643 | 1.369 | 0.42396 | 1.0819 | 0.42396 | 1.0819 | 0.42396 | 1.0819 | 0.98298 | 2.5085 | 0.98298 | 2.5085 | 0.6498 | 1.6583 | 0.68714 | 1.7536 | 0.69687 | 1.7784 | 0.69687 | 1.7784 | 0.69687 | 1.7784 | 0.69687 | 1.7784 | 0.69687 | 1.7784 | 0.69687 | 1.7784 | 0.10822 | 0.27618 | 0.10822 | 0.27618 | 0.21928 | 0.55959 | 0.091681 | 0.23397
| Toluene | 108-88-3 | 0.1054 |  | 0.1203 | 0.307 | 0.1203 | 0.307 | 0.1203 | 0.307 |  | 0.1203 | 0.307 | 0.095074 | 0.24263 | 0.095074 | 0.24263 | 0.095074 | 0.24263 | 0.22044 | 0.56255 | 0.22044 | 0.56255 | 0.14572 | 0.37188 | 0.15409 | 0.39324 | 0.15628 | 0.39882 | 0.15628 | 0.39882 | 0.15628 | 0.39882 | 0.15628 | 0.39882 | 0.15628 | 0.39882 | 0.15628 | 0.39882 | 0.024269 | 0.061935 | 0.024269 | 0.061935 | 0.049175 | 0.12549 | 0.02056 | 0.052469
| Xylene (mixed isomers) | 1330-20-7 | 0.0424 |  | 0.048393 | 0.1235 | 0.048393 | 0.1235 | 0.048393 | 0.1235 |  | 0.048393 | 0.1235 | 0.038246 | 0.097603 | 0.038246 | 0.097603 | 0.038246 | 0.097603 | 0.088677 | 0.2263 | 0.088677 | 0.2263 | 0.058621 | 0.1496 | 0.061989 | 0.15819 | 0.062867 | 0.16043 | 0.062867 | 0.16043 | 0.062867 | 0.16043 | 0.062867 | 0.16043 | 0.062867 | 0.16043 | 0.062867 | 0.16043 | 0.009763 | 0.024915 | 0.009763 | 0.024915 | 0.019782 | 0.050482 | 0.0082708 | 0.021107
INORGANIC COMPOUNDS
| Ammonia | 7664-41-7 | 0.8 |  | 0.91307 | 2.3301 | 0.91307 | 2.3301 | 0.91307 | 2.3301 |  | 0.91307 | 2.3301 | 0.72163 | 1.8416 | 0.72163 | 1.8416 | 0.72163 | 1.8416 | 1.6732 | 4.2698 | 1.6732 | 4.2698 | 1.106 | 2.8226 | 1.1696 | 2.9848 | 1.1862 | 3.0271 | 1.1862 | 3.0271 | 1.1862 | 3.0271 | 1.1862 | 3.0271 | 1.1862 | 3.0271 | 1.1862 | 3.0271 | 0.18421 | 0.47009 | 0.18421 | 0.47009 | 0.37324 | 0.9525 | 0.15605 | 0.39824
| Hydrochloric Acid | 7647-01-0 | 0.1863 |  | 0.21263 | 0.54263 | 0.21263 | 0.54263 | 0.21263 | 0.54263 |  | 0.21263 | 0.54263 | 0.16805 | 0.42885 | 0.16805 | 0.42885 | 0.16805 | 0.42885 | 0.38964 | 0.99434 | 0.38964 | 0.99434 | 0.25757 | 0.65731 | 0.27237 | 0.69508 | 0.27623 | 0.70493 | 0.27623 | 0.70493 | 0.27623 | 0.70493 | 0.27623 | 0.70493 | 0.27623 | 0.70493 | 0.27623 | 0.70493 | 0.042897 | 0.10947 | 0.042897 | 0.10947 | 0.086919 | 0.22181 | 0.036341 | 0.092741
POLYCYCLIC AROMATIC HYDROCARBONS (PAH)
| Benzo[a]pyrene | 50-32-8 | 3.52e-05 |  | 4.0175e-05 | 0.00010253 | 4.0175e-05 | 0.00010253 | 4.0175e-05 | 0.00010253 |  | 4.0175e-05 | 0.00010253 | 3.1752e-05 | 8.1029e-05 | 3.1752e-05 | 8.1029e-05 | 3.1752e-05 | 8.1029e-05 | 7.3619e-05 | 0.00018787 | 7.3619e-05 | 0.00018787 | 4.8666e-05 | 0.00012419 | 5.1462e-05 | 0.00013133 | 5.2191e-05 | 0.00013319 | 5.2191e-05 | 0.00013319 | 5.2191e-05 | 0.00013319 | 5.2191e-05 | 0.00013319 | 5.2191e-05 | 0.00013319 | 5.2191e-05 | 0.00013319 | 8.1051e-06 | 2.0684e-05 | 8.1051e-06 | 2.0684e-05 | 1.6423e-05 | 4.191e-05 | 6.8664e-06 | 1.7523e-05
| Naphthalene | 91-20-3 | 0.0197 |  | 0.022484 | 0.05738 | 0.022484 | 0.05738 | 0.022484 | 0.05738 |  | 0.022484 | 0.05738 | 0.01777 | 0.045349 | 0.01777 | 0.045349 | 0.01777 | 0.045349 | 0.041201 | 0.10514 | 0.041201 | 0.10514 | 0.027236 | 0.069507 | 0.028801 | 0.0735 | 0.029209 | 0.074541 | 0.029209 | 0.074541 | 0.029209 | 0.074541 | 0.029209 | 0.074541 | 0.029209 | 0.074541 | 0.029209 | 0.074541 | 0.0045361 | 0.011576 | 0.0045361 | 0.011576 | 0.0091911 | 0.023455 | 0.0038428 | 0.0098067
| PAH | 401 | 0.0362 |  | 0.041317 | 0.10544 | 0.041317 | 0.10544 | 0.041317 | 0.10544 |  | 0.041317 | 0.10544 | 0.032654 | 0.083331 | 0.032654 | 0.083331 | 0.032654 | 0.083331 | 0.07571 | 0.19321 | 0.07571 | 0.19321 | 0.050049 | 0.12772 | 0.052924 | 0.13506 | 0.053674 | 0.13697 | 0.053674 | 0.13697 | 0.053674 | 0.13697 | 0.053674 | 0.13697 | 0.053674 | 0.13697 | 0.053674 | 0.13697 | 0.0083354 | 0.021272 | 0.0083354 | 0.021272 | 0.016889 | 0.043101 | 0.0070614 | 0.018021
DIESEL PARTICULATE MATTER (DPM)
| DPM | 200 | 33.5 |  | 38.235 | 97.5743 | 38.235 | 97.5743 | 38.235 | 97.5743 |  | 38.235 | 97.5743 | 30.2181 | 77.1156 | 30.2181 | 77.1156 | 30.2181 | 77.1156 | 70.0632 | 178.7989 | 70.0632 | 178.7989 | 46.3158 | 118.1964 | 48.9769 | 124.9873 | 49.6708 | 126.7581 | 49.6708 | 126.7581 | 49.6708 | 126.7581 | 49.6708 | 126.7581 | 49.6708 | 126.7581 | 49.6708 | 126.7581 | 7.7137 | 19.6851 | 7.7137 | 19.6851 | 15.6295 | 39.8859 | 6.5347 | 16.6764
Notes
DPF = Diesel Particulate Filter; HAP = Hazardous Air Pollutant; Mgal = 1,000 gallons; TAC = Toxic Air Contaminant.
(a) | Daily emissions estimate (lb/day) = (emission factor [lb/Mgal]) x (fuel consumption [gal/hr]) x (daily hours of operation [hrs/day]) x (Mgal/1,000 gal) | [9 empty] | (b), (c)
| + (cold start emissions [lb/minute]) x (number of cold starts per day) - (emissions per minute, normal operation [lb/minute]) x (number of cold starts per day) | [9 empty] | (3)
|  | Cold start adjustment factor = | 4.3 | (4)
|  | Cold start adjustment factor (formaldehyde) = | 4.8 | (4)
|  | Number of cold starts per day = | 1 | (5)
(b) | Cold start emissions (lb/minute) = (emission factor [lb/Mgal]) x (cold start adjustment factor) x (hourly fuel consumption [Mgal/hr]) / 60
(c) | Emissions per minute, normal operation (lb/minute) = (emission factor [lb/Mgal]) x (hourly fuel consumption [Mgal/hr]) / 60
(d) | Annual emissions estimate (lb/yr) = (emission factor [lb/Mgal]) x (fuel consumption [gal/hr]) x (annual hours of operation [hrs/yr]) x (Mgal/1,000 gal) | [9 empty] | (b), (c)
| + (cold start emissions [lb/minute]) x (number of cold starts per year) - (emissions per minute, normal operation [lb/minute]) x (number of cold starts per year) | [9 empty] | (3)
|  | Cold start adjustment factor = | 4.3 | (4)
|  | Cold start adjustment factor (formaldehyde) = | 4.8 | (4)
|  | Number of cold starts per year = | 12 | (5)
References
(1) | Permit conditions limit Intel to operate 10 EGENs for 10 hours a day and all EGENs for 25 hours a year.
(2) | Emission Factors from the Oregon Department of Environmental Quality, AQ104B, diesel internal combustion, pre-2006, less than
750 hp. Ammonia emission factor assumes value for no SNCR or SCR control. DEQ reference CAO Diesel RICE (a).
(3) | Time allotted for cold stats was omitted from the daily/annual operating capacity in emission calculations. Cold start adjustments are not required for metals.
(4) | Cold start adjustment factors provided by the Oregon Department of Environmental Quality. All applicable pollutants, except
formaldehyde, share the same adjustment factor. Cold start adjustments are not required for metals.
(5) | Based on one cold start per month per engine for Preventative Maintenance activities.

## EGENnoDPF_b_RONLER
TESU ID |  |  |  |  | RP1-GEN-2 |  | D1D-GEN-7 |  | RS6-GEN-2 |  |  | D1X-GEN-1A |  | D1X-GEN-1B |  | D1X-GEN-1C |  | D1X-GEN-2A |  | D1X-GEN-2B |  | D1X-GEN-2C |  | D1X-GEN-3A |  | D1X-GEN-3B |  | D1X-GEN-3C |  | D1X-GEN-4A |  | D1X-GEN-4B |  | D1X-GEN-5C
Fuel Consumption (gal/hr) |  |  |  |  | 145.4 |  | 147.5 |  | 147.5 |  |  | 176 |  | 172.1 |  | 176 |  | 176 |  | 176 |  | 176 |  | 172.1 |  | 176 |  | 172.1 |  | 172.1 |  | 172.1 |  | 206
Daily Hours of Operation (hrs/day) |  |  |  | (1) | 10 |  | 10 |  | 10 |  |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10 |  | 10
Annual Hours of Operation (hrs/yr) |  |  |  | (1) | 25 |  | 25 |  | 25 |  |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25 |  | 25
Pollutant |  | CAS | Emission Factor (2) (lb/Mgal) |  | Emissions Estimate
[5 empty] | RP1-GEN-2 |  | D1D-GEN-7 |  | RS6-GEN-2 |  |  | D1X-GEN-1A |  | D1X-GEN-1B |  | D1X-GEN-1C |  | D1X-GEN-2A |  | D1X-GEN-2B |  | D1X-GEN-2C |  | D1X-GEN-3A |  | D1X-GEN-3B |  | D1X-GEN-3C |  | D1X-GEN-4A |  | D1X-GEN-4B |  | D1X-GEN-5C
[5 empty] | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) |  | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr)
METALS
| Antimony and Compounds | 7440-36-0 | 0.00031819 |  | 0.00046264 | 0.0011566 | 0.00046933 | 0.0011733 | 0.00046933 | 0.0011733 |  | 0.00056001 | 0.0014 | 0.0005476 | 0.001369 | 0.00056001 | 0.0014 | 0.00056001 | 0.0014 | 0.00056001 | 0.0014 | 0.00056001 | 0.0014 | 0.0005476 | 0.001369 | 0.00056001 | 0.0014 | 0.0005476 | 0.001369 | 0.0005476 | 0.001369 | 0.0005476 | 0.001369 | 0.00065547 | 0.0016387
| Arsenic and Compounds | 7440-38-2 | 0.00027685 |  | 0.00040254 | 0.0010064 | 0.00040836 | 0.0010209 | 0.00040836 | 0.0010209 |  | 0.00048726 | 0.0012182 | 0.00047646 | 0.0011912 | 0.00048726 | 0.0012182 | 0.00048726 | 0.0012182 | 0.00048726 | 0.0012182 | 0.00048726 | 0.0012182 | 0.00047646 | 0.0011912 | 0.00048726 | 0.0012182 | 0.00047646 | 0.0011912 | 0.00047646 | 0.0011912 | 0.00047646 | 0.0011912 | 0.00057032 | 0.0014258
| Barium and Compounds | 7440-39-3 | 0.00037389 |  | 0.00054364 | 0.0013591 | 0.00055149 | 0.0013787 | 0.00055149 | 0.0013787 |  | 0.00065805 | 0.0016451 | 0.00064347 | 0.0016087 | 0.00065805 | 0.0016451 | 0.00065805 | 0.0016451 | 0.00065805 | 0.0016451 | 0.00065805 | 0.0016451 | 0.00064347 | 0.0016087 | 0.00065805 | 0.0016451 | 0.00064347 | 0.0016087 | 0.00064347 | 0.0016087 | 0.00064347 | 0.0016087 | 0.00077022 | 0.0019256
| Beryllium and compounds | 7440-41-7 | 4.7708e-06 |  | 6.9368e-06 | 1.7342e-05 | 7.037e-06 | 1.7592e-05 | 7.037e-06 | 1.7592e-05 |  | 8.3967e-06 | 2.0992e-05 | 8.2106e-06 | 2.0527e-05 | 8.3967e-06 | 2.0992e-05 | 8.3967e-06 | 2.0992e-05 | 8.3967e-06 | 2.0992e-05 | 8.3967e-06 | 2.0992e-05 | 8.2106e-06 | 2.0527e-05 | 8.3967e-06 | 2.0992e-05 | 8.2106e-06 | 2.0527e-05 | 8.2106e-06 | 2.0527e-05 | 8.2106e-06 | 2.0527e-05 | 9.8279e-06 | 2.457e-05
| Cadmium and Compounds | 7440-43-9 | 8.0778e-05 |  | 0.00011745 | 0.00029363 | 0.00011915 | 0.00029787 | 0.00011915 | 0.00029787 |  | 0.00014217 | 0.00035542 | 0.00013902 | 0.00034755 | 0.00014217 | 0.00035542 | 0.00014217 | 0.00035542 | 0.00014217 | 0.00035542 | 0.00014217 | 0.00035542 | 0.00013902 | 0.00034755 | 0.00014217 | 0.00035542 | 0.00013902 | 0.00034755 | 0.00013902 | 0.00034755 | 0.00013902 | 0.00034755 | 0.0001664 | 0.00041601
| Chromium VI | 18540-29-9 | 6.3144e-05 |  | 9.1812e-05 | 0.00022953 | 9.3138e-05 | 0.00023285 | 9.3138e-05 | 0.00023285 |  | 0.00011113 | 0.00027784 | 0.00010867 | 0.00027168 | 0.00011113 | 0.00027784 | 0.00011113 | 0.00027784 | 0.00011113 | 0.00027784 | 0.00011113 | 0.00027784 | 0.00010867 | 0.00027168 | 0.00011113 | 0.00027784 | 0.00010867 | 0.00027168 | 0.00010867 | 0.00027168 | 0.00010867 | 0.00027168 | 0.00013008 | 0.00032519
| Copper and Compounds | 7440-50-8 | 0.00050214 |  | 0.0007301 | 0.0018253 | 0.00074065 | 0.0018516 | 0.00074065 | 0.0018516 |  | 0.00088376 | 0.0022094 | 0.00086417 | 0.0021604 | 0.00088376 | 0.0022094 | 0.00088376 | 0.0022094 | 0.00088376 | 0.0022094 | 0.00088376 | 0.0022094 | 0.00086417 | 0.0021604 | 0.00088376 | 0.0022094 | 0.00086417 | 0.0021604 | 0.00086417 | 0.0021604 | 0.00086417 | 0.0021604 | 0.0010344 | 0.002586
| Cobalt and compounds | 7440-48-4 | 1.5751e-05 |  | 2.2902e-05 | 5.7255e-05 | 2.3233e-05 | 5.8082e-05 | 2.3233e-05 | 5.8082e-05 |  | 2.7722e-05 | 6.9305e-05 | 2.7108e-05 | 6.7769e-05 | 2.7722e-05 | 6.9305e-05 | 2.7722e-05 | 6.9305e-05 | 2.7722e-05 | 6.9305e-05 | 2.7722e-05 | 6.9305e-05 | 2.7108e-05 | 6.7769e-05 | 2.7722e-05 | 6.9305e-05 | 2.7108e-05 | 6.7769e-05 | 2.7108e-05 | 6.7769e-05 | 2.7108e-05 | 6.7769e-05 | 3.2447e-05 | 8.1118e-05
| Lead and Compounds | 7439-92-1 | 0.00036367 |  | 0.00052878 | 0.0013219 | 0.00053642 | 0.001341 | 0.00053642 | 0.001341 |  | 0.00064006 | 0.0016002 | 0.00062588 | 0.0015647 | 0.00064006 | 0.0016002 | 0.00064006 | 0.0016002 | 0.00064006 | 0.0016002 | 0.00064006 | 0.0016002 | 0.00062588 | 0.0015647 | 0.00064006 | 0.0016002 | 0.00062588 | 0.0015647 | 0.00062588 | 0.0015647 | 0.00062588 | 0.0015647 | 0.00074916 | 0.0018729
| Manganese and Compounds | 7439-96-5 | 0.00041991 |  | 0.00061055 | 0.0015264 | 0.00061937 | 0.0015484 | 0.00061937 | 0.0015484 |  | 0.00073905 | 0.0018476 | 0.00072267 | 0.0018067 | 0.00073905 | 0.0018476 | 0.00073905 | 0.0018476 | 0.00073905 | 0.0018476 | 0.00073905 | 0.0018476 | 0.00072267 | 0.0018067 | 0.00073905 | 0.0018476 | 0.00072267 | 0.0018067 | 0.00072267 | 0.0018067 | 0.00072267 | 0.0018067 | 0.00086502 | 0.0021626
| Mercury and Compounds | 7439-97-6 | 1.5107e-05 |  | 2.1966e-05 | 5.4915e-05 | 2.2283e-05 | 5.5708e-05 | 2.2283e-05 | 5.5708e-05 |  | 2.6589e-05 | 6.6472e-05 | 2.6e-05 | 6.4999e-05 | 2.6589e-05 | 6.6472e-05 | 2.6589e-05 | 6.6472e-05 | 2.6589e-05 | 6.6472e-05 | 2.6589e-05 | 6.6472e-05 | 2.6e-05 | 6.4999e-05 | 2.6589e-05 | 6.6472e-05 | 2.6e-05 | 6.4999e-05 | 2.6e-05 | 6.4999e-05 | 2.6e-05 | 6.4999e-05 | 3.1121e-05 | 7.7803e-05
| Nickel and Compounds | 7440-02-0 | 0.00018223 |  | 0.00026496 | 0.0006624 | 0.00026879 | 0.00067197 | 0.00026879 | 0.00067197 |  | 0.00032072 | 0.00080181 | 0.00031362 | 0.00078404 | 0.00032072 | 0.00080181 | 0.00032072 | 0.00080181 | 0.00032072 | 0.00080181 | 0.00032072 | 0.00080181 | 0.00031362 | 0.00078404 | 0.00032072 | 0.00080181 | 0.00031362 | 0.00078404 | 0.00031362 | 0.00078404 | 0.00031362 | 0.00078404 | 0.00037539 | 0.00093848
| Phosphorus and compounds | 504 | 0.008404 |  | 0.012219 | 0.030548 | 0.012396 | 0.03099 | 0.012396 | 0.03099 |  | 0.014791 | 0.036978 | 0.014463 | 0.036158 | 0.014791 | 0.036978 | 0.014791 | 0.036978 | 0.014791 | 0.036978 | 0.014791 | 0.036978 | 0.014463 | 0.036158 | 0.014791 | 0.036978 | 0.014463 | 0.036158 | 0.014463 | 0.036158 | 0.014463 | 0.036158 | 0.017312 | 0.043281
| Selenium and Compounds | 7782-49-2 | 0.00037638 |  | 0.00054726 | 0.0013682 | 0.00055516 | 0.0013879 | 0.00055516 | 0.0013879 |  | 0.00066243 | 0.0016561 | 0.00064775 | 0.0016194 | 0.00066243 | 0.0016561 | 0.00066243 | 0.0016561 | 0.00066243 | 0.0016561 | 0.00066243 | 0.0016561 | 0.00064775 | 0.0016194 | 0.00066243 | 0.0016561 | 0.00064775 | 0.0016194 | 0.00064775 | 0.0016194 | 0.00064775 | 0.0016194 | 0.00077535 | 0.0019384
| Silver and compounds | 7440-22-4 | 4.8013e-05 |  | 6.9811e-05 | 0.00017453 | 7.0819e-05 | 0.00017705 | 7.0819e-05 | 0.00017705 |  | 8.4503e-05 | 0.00021126 | 8.263e-05 | 0.00020658 | 8.4503e-05 | 0.00021126 | 8.4503e-05 | 0.00021126 | 8.4503e-05 | 0.00021126 | 8.4503e-05 | 0.00021126 | 8.263e-05 | 0.00020658 | 8.4503e-05 | 0.00021126 | 8.263e-05 | 0.00020658 | 8.263e-05 | 0.00020658 | 8.263e-05 | 0.00020658 | 9.8907e-05 | 0.00024727
| Thallium and compounds | 7440-28-0 | 0.00024009 |  | 0.0003491 | 0.00087274 | 0.00035414 | 0.00088535 | 0.00035414 | 0.00088535 |  | 0.00042256 | 0.0010564 | 0.0004132 | 0.001033 | 0.00042256 | 0.0010564 | 0.00042256 | 0.0010564 | 0.00042256 | 0.0010564 | 0.00042256 | 0.0010564 | 0.0004132 | 0.001033 | 0.00042256 | 0.0010564 | 0.0004132 | 0.001033 | 0.0004132 | 0.001033 | 0.0004132 | 0.001033 | 0.00049459 | 0.0012365
| Zinc and compounds | 7440-66-6 | 0.0052262 |  | 0.0075989 | 0.018997 | 0.0077086 | 0.019272 | 0.0077086 | 0.019272 |  | 0.0091981 | 0.022995 | 0.0089943 | 0.022486 | 0.0091981 | 0.022995 | 0.0091981 | 0.022995 | 0.0091981 | 0.022995 | 0.0091981 | 0.022995 | 0.0089943 | 0.022486 | 0.0091981 | 0.022995 | 0.0089943 | 0.022486 | 0.0089943 | 0.022486 | 0.0089943 | 0.022486 | 0.010766 | 0.026915
ORGANIC COMPOUNDS
| 1,3-Butadiene | 106-99-0 | 0.2174 |  | 0.31784 | 0.81111 | 0.32243 | 0.82283 | 0.32243 | 0.82283 |  | 0.38473 | 0.98181 | 0.3762 | 0.96006 | 0.38473 | 0.98181 | 0.38473 | 0.98181 | 0.38473 | 0.98181 | 0.38473 | 0.98181 | 0.3762 | 0.96006 | 0.38473 | 0.98181 | 0.3762 | 0.96006 | 0.3762 | 0.96006 | 0.3762 | 0.96006 | 0.45031 | 1.1492
| 2-Methyl naphthalene | 91-57-6 | 0.012298 |  | 0.01798 | 0.045883 | 0.018239 | 0.046546 | 0.018239 | 0.046546 |  | 0.021763 | 0.055539 | 0.021281 | 0.054309 | 0.021763 | 0.055539 | 0.021763 | 0.055539 | 0.021763 | 0.055539 | 0.021763 | 0.055539 | 0.021281 | 0.054309 | 0.021763 | 0.055539 | 0.021281 | 0.054309 | 0.021281 | 0.054309 | 0.021281 | 0.054309 | 0.025473 | 0.065006
| Acenaphthene | 83-32-9 | 0.00073461 |  | 0.001074 | 0.0027408 | 0.0010895 | 0.0027804 | 0.0010895 | 0.0027804 |  | 0.0013 | 0.0033176 | 0.0012712 | 0.0032441 | 0.0013 | 0.0033176 | 0.0013 | 0.0033176 | 0.0013 | 0.0033176 | 0.0013 | 0.0033176 | 0.0012712 | 0.0032441 | 0.0013 | 0.0033176 | 0.0012712 | 0.0032441 | 0.0012712 | 0.0032441 | 0.0012712 | 0.0032441 | 0.0015216 | 0.0038831
| Acenaphthylene | 208-96-8 | 0.00080982 |  | 0.0011839 | 0.0030214 | 0.001201 | 0.003065 | 0.001201 | 0.003065 |  | 0.0014331 | 0.0036573 | 0.0014014 | 0.0035762 | 0.0014331 | 0.0036573 | 0.0014331 | 0.0036573 | 0.0014331 | 0.0036573 | 0.0014331 | 0.0036573 | 0.0014014 | 0.0035762 | 0.0014331 | 0.0036573 | 0.0014014 | 0.0035762 | 0.0014014 | 0.0035762 | 0.0014014 | 0.0035762 | 0.0016774 | 0.0042807
| Acetaldehyde | 75-07-0 | 0.7833 |  | 1.1452 | 2.9225 | 1.1617 | 2.9647 | 1.1617 | 2.9647 |  | 1.3862 | 3.5375 | 1.3555 | 3.4591 | 1.3862 | 3.5375 | 1.3862 | 3.5375 | 1.3862 | 3.5375 | 1.3862 | 3.5375 | 1.3555 | 3.4591 | 1.3862 | 3.5375 | 1.3555 | 3.4591 | 1.3555 | 3.4591 | 1.3555 | 3.4591 | 1.6225 | 4.1405
| Acrolein | 107-02-8 | 0.0339 |  | 0.049562 | 0.12648 | 0.050278 | 0.12831 | 0.050278 | 0.12831 |  | 0.059992 | 0.1531 | 0.058663 | 0.14971 | 0.059992 | 0.1531 | 0.059992 | 0.1531 | 0.059992 | 0.1531 | 0.059992 | 0.1531 | 0.058663 | 0.14971 | 0.059992 | 0.1531 | 0.058663 | 0.14971 | 0.058663 | 0.14971 | 0.058663 | 0.14971 | 0.070218 | 0.17919
| Anthracene | 120-12-7 | 0.00045209 |  | 0.00066095 | 0.0016867 | 0.0006705 | 0.0017111 | 0.0006705 | 0.0017111 |  | 0.00080005 | 0.0020417 | 0.00078233 | 0.0019965 | 0.00080005 | 0.0020417 | 0.00080005 | 0.0020417 | 0.00080005 | 0.0020417 | 0.00080005 | 0.0020417 | 0.00078233 | 0.0019965 | 0.00080005 | 0.0020417 | 0.00078233 | 0.0019965 | 0.00078233 | 0.0019965 | 0.00078233 | 0.0019965 | 0.00093643 | 0.0023897
| Benzene | 71-43-2 | 0.1863 |  | 0.27237 | 0.69508 | 0.2763 | 0.70512 | 0.2763 | 0.70512 |  | 0.32969 | 0.84136 | 0.32239 | 0.82272 | 0.32969 | 0.84136 | 0.32969 | 0.84136 | 0.32969 | 0.84136 | 0.32969 | 0.84136 | 0.32239 | 0.82272 | 0.32969 | 0.84136 | 0.32239 | 0.82272 | 0.32239 | 0.82272 | 0.32239 | 0.82272 | 0.38589 | 0.98477
| Chlorobenzene | 108-90-7 | 0.0002 |  | 0.0002924 | 0.00074619 | 0.00029662 | 0.00075697 | 0.00029662 | 0.00075697 |  | 0.00035394 | 0.00090323 | 0.00034609 | 0.00088322 | 0.00035394 | 0.00090323 | 0.00035394 | 0.00090323 | 0.00035394 | 0.00090323 | 0.00035394 | 0.00090323 | 0.00034609 | 0.00088322 | 0.00035394 | 0.00090323 | 0.00034609 | 0.00088322 | 0.00034609 | 0.00088322 | 0.00034609 | 0.00088322 | 0.00041427 | 0.0010572
| Ethylbenzene | 100-41-4 | 0.0109 |  | 0.015936 | 0.040668 | 0.016166 | 0.041255 | 0.016166 | 0.041255 |  | 0.01929 | 0.049226 | 0.018862 | 0.048135 | 0.01929 | 0.049226 | 0.01929 | 0.049226 | 0.01929 | 0.049226 | 0.01929 | 0.049226 | 0.018862 | 0.048135 | 0.01929 | 0.049226 | 0.018862 | 0.048135 | 0.018862 | 0.048135 | 0.018862 | 0.048135 | 0.022577 | 0.057617
| Formaldehyde | 50-00-0 | 2.7131 |  | 3.9698 | 10.1618 | 4.0271 | 10.3086 | 4.0271 | 10.3086 |  | 4.8052 | 12.3004 | 4.6988 | 12.0278 | 4.8052 | 12.3004 | 4.8052 | 12.3004 | 4.8052 | 12.3004 | 4.8052 | 12.3004 | 4.6988 | 12.0278 | 4.8052 | 12.3004 | 4.6988 | 12.0278 | 4.6988 | 12.0278 | 4.6988 | 12.0278 | 5.6243 | 14.397
| Hexane | 110-54-3 | 0.0269 |  | 0.039328 | 0.10036 | 0.039896 | 0.10181 | 0.039896 | 0.10181 |  | 0.047604 | 0.12148 | 0.04655 | 0.11879 | 0.047604 | 0.12148 | 0.047604 | 0.12148 | 0.047604 | 0.12148 | 0.047604 | 0.12148 | 0.04655 | 0.11879 | 0.047604 | 0.12148 | 0.04655 | 0.11879 | 0.04655 | 0.11879 | 0.04655 | 0.11879 | 0.055719 | 0.14219
| Propylene | 115-07-1 | 0.47 |  | 0.68714 | 1.7536 | 0.69706 | 1.7789 | 0.69706 | 1.7789 |  | 0.83175 | 2.1226 | 0.81332 | 2.0756 | 0.83175 | 2.1226 | 0.83175 | 2.1226 | 0.83175 | 2.1226 | 0.83175 | 2.1226 | 0.81332 | 2.0756 | 0.83175 | 2.1226 | 0.81332 | 2.0756 | 0.81332 | 2.0756 | 0.81332 | 2.0756 | 0.97353 | 2.4844
| Toluene | 108-88-3 | 0.1054 |  | 0.15409 | 0.39324 | 0.15632 | 0.39892 | 0.15632 | 0.39892 |  | 0.18652 | 0.476 | 0.18239 | 0.46546 | 0.18652 | 0.476 | 0.18652 | 0.476 | 0.18652 | 0.476 | 0.18652 | 0.476 | 0.18239 | 0.46546 | 0.18652 | 0.476 | 0.18239 | 0.46546 | 0.18239 | 0.46546 | 0.18239 | 0.46546 | 0.21832 | 0.55714
| Xylene (mixed isomers) | 1330-20-7 | 0.0424 |  | 0.061989 | 0.15819 | 0.062884 | 0.16048 | 0.062884 | 0.16048 |  | 0.075034 | 0.19149 | 0.073372 | 0.18724 | 0.075034 | 0.19149 | 0.075034 | 0.19149 | 0.075034 | 0.19149 | 0.075034 | 0.19149 | 0.073372 | 0.18724 | 0.075034 | 0.19149 | 0.073372 | 0.18724 | 0.073372 | 0.18724 | 0.073372 | 0.18724 | 0.087824 | 0.22412
INORGANIC COMPOUNDS
| Ammonia | 7664-41-7 | 0.8 |  | 1.1696 | 2.9848 | 1.1865 | 3.0279 | 1.1865 | 3.0279 |  | 1.4157 | 3.6129 | 1.3844 | 3.5329 | 1.4157 | 3.6129 | 1.4157 | 3.6129 | 1.4157 | 3.6129 | 1.4157 | 3.6129 | 1.3844 | 3.5329 | 1.4157 | 3.6129 | 1.3844 | 3.5329 | 1.3844 | 3.5329 | 1.3844 | 3.5329 | 1.6571 | 4.2288
| Hydrochloric Acid | 7647-01-0 | 0.1863 |  | 0.27237 | 0.69508 | 0.2763 | 0.70512 | 0.2763 | 0.70512 |  | 0.32969 | 0.84136 | 0.32239 | 0.82272 | 0.32969 | 0.84136 | 0.32969 | 0.84136 | 0.32969 | 0.84136 | 0.32969 | 0.84136 | 0.32239 | 0.82272 | 0.32969 | 0.84136 | 0.32239 | 0.82272 | 0.32239 | 0.82272 | 0.32239 | 0.82272 | 0.38589 | 0.98477
POLYCYCLIC AROMATIC HYDROCARBONS (PAH)
| Benz[a]anthracene | 56-55-3 | 4.8541e-05 |  | 7.0967e-05 | 0.00018111 | 7.1992e-05 | 0.00018372 | 7.1992e-05 | 0.00018372 |  | 8.5903e-05 | 0.00021922 | 8.3999e-05 | 0.00021436 | 8.5903e-05 | 0.00021922 | 8.5903e-05 | 0.00021922 | 8.5903e-05 | 0.00021922 | 8.5903e-05 | 0.00021922 | 8.3999e-05 | 0.00021436 | 8.5903e-05 | 0.00021922 | 8.3999e-05 | 0.00021436 | 8.3999e-05 | 0.00021436 | 8.3999e-05 | 0.00021436 | 0.00010055 | 0.00025659
| Benzo[a]pyrene | 50-32-8 | 1.4385e-05 |  | 2.1031e-05 | 5.3671e-05 | 2.1335e-05 | 5.4446e-05 | 2.1335e-05 | 5.4446e-05 |  | 2.5457e-05 | 6.4966e-05 | 2.4893e-05 | 6.3526e-05 | 2.5457e-05 | 6.4966e-05 | 2.5457e-05 | 6.4966e-05 | 2.5457e-05 | 6.4966e-05 | 2.5457e-05 | 6.4966e-05 | 2.4893e-05 | 6.3526e-05 | 2.5457e-05 | 6.4966e-05 | 2.4893e-05 | 6.3526e-05 | 2.4893e-05 | 6.3526e-05 | 2.4893e-05 | 6.3526e-05 | 2.9797e-05 | 7.604e-05
| Benzo[b]fluoranthene | 205-99-2 | 4.4354e-05 |  | 6.4845e-05 | 0.00016548 | 6.5781e-05 | 0.00016787 | 6.5781e-05 | 0.00016787 |  | 7.8492e-05 | 0.00020031 | 7.6752e-05 | 0.00019587 | 7.8492e-05 | 0.00020031 | 7.8492e-05 | 0.00020031 | 7.8492e-05 | 0.00020031 | 7.8492e-05 | 0.00020031 | 7.6752e-05 | 0.00019587 | 7.8492e-05 | 0.00020031 | 7.6752e-05 | 0.00019587 | 7.6752e-05 | 0.00019587 | 7.6752e-05 | 0.00019587 | 9.1871e-05 | 0.00023445
| Benzo[e]pyrene | 192-97-2 | 3.2868e-05 |  | 4.8053e-05 | 0.00012263 | 4.8747e-05 | 0.0001244 | 4.8747e-05 | 0.0001244 |  | 5.8166e-05 | 0.00014844 | 5.6877e-05 | 0.00014515 | 5.8166e-05 | 0.00014844 | 5.8166e-05 | 0.00014844 | 5.8166e-05 | 0.00014844 | 5.8166e-05 | 0.00014844 | 5.6877e-05 | 0.00014515 | 5.8166e-05 | 0.00014844 | 5.6877e-05 | 0.00014515 | 5.6877e-05 | 0.00014515 | 5.6877e-05 | 0.00014515 | 6.8081e-05 | 0.00017374
| Benzo[g,h,i]perylene | 191-24-2 | 2.1874e-05 |  | 3.198e-05 | 8.1612e-05 | 3.2442e-05 | 8.2791e-05 | 3.2442e-05 | 8.2791e-05 |  | 3.8711e-05 | 9.8788e-05 | 3.7853e-05 | 9.6599e-05 | 3.8711e-05 | 9.8788e-05 | 3.8711e-05 | 9.8788e-05 | 3.8711e-05 | 9.8788e-05 | 3.8711e-05 | 9.8788e-05 | 3.7853e-05 | 9.6599e-05 | 3.8711e-05 | 9.8788e-05 | 3.7853e-05 | 9.6599e-05 | 3.7853e-05 | 9.6599e-05 | 3.7853e-05 | 9.6599e-05 | 4.5309e-05 | 0.00011563
| Benzo[k]fluoranthene | 207-08-9 | 1.3054e-05 |  | 1.9085e-05 | 4.8705e-05 | 1.9361e-05 | 4.9409e-05 | 1.9361e-05 | 4.9409e-05 |  | 2.3102e-05 | 5.8956e-05 | 2.259e-05 | 5.7649e-05 | 2.3102e-05 | 5.8956e-05 | 2.3102e-05 | 5.8956e-05 | 2.3102e-05 | 5.8956e-05 | 2.3102e-05 | 5.8956e-05 | 2.259e-05 | 5.7649e-05 | 2.3102e-05 | 5.8956e-05 | 2.259e-05 | 5.7649e-05 | 2.259e-05 | 5.7649e-05 | 2.259e-05 | 5.7649e-05 | 2.704e-05 | 6.9005e-05
| Chrysene | 218-01-9 | 6.7e-05 |  | 9.7954e-05 | 0.00024997 | 9.9368e-05 | 0.00025358 | 9.9368e-05 | 0.00025358 |  | 0.00011857 | 0.00030258 | 0.00011594 | 0.00029588 | 0.00011857 | 0.00030258 | 0.00011857 | 0.00030258 | 0.00011857 | 0.00030258 | 0.00011857 | 0.00030258 | 0.00011594 | 0.00029588 | 0.00011857 | 0.00030258 | 0.00011594 | 0.00029588 | 0.00011594 | 0.00029588 | 0.00011594 | 0.00029588 | 0.00013878 | 0.00035416
| Dibenz[a,h]anthracene | 53-70-3 | 1.037e-06 |  | 1.5161e-06 | 3.869e-06 | 1.538e-06 | 3.9248e-06 | 1.538e-06 | 3.9248e-06 |  | 1.8351e-06 | 4.6832e-06 | 1.7945e-06 | 4.5794e-06 | 1.8351e-06 | 4.6832e-06 | 1.8351e-06 | 4.6832e-06 | 1.8351e-06 | 4.6832e-06 | 1.8351e-06 | 4.6832e-06 | 1.7945e-06 | 4.5794e-06 | 1.8351e-06 | 4.6832e-06 | 1.7945e-06 | 4.5794e-06 | 1.7945e-06 | 4.5794e-06 | 1.7945e-06 | 4.5794e-06 | 2.1479e-06 | 5.4815e-06
| Fluoranthene | 206-44-0 | 0.00036995 |  | 0.00054087 | 0.0013803 | 0.00054868 | 0.0014002 | 0.00054868 | 0.0014002 |  | 0.0006547 | 0.0016708 | 0.00064019 | 0.0016337 | 0.0006547 | 0.0016708 | 0.0006547 | 0.0016708 | 0.0006547 | 0.0016708 | 0.0006547 | 0.0016708 | 0.00064019 | 0.0016337 | 0.0006547 | 0.0016708 | 0.00064019 | 0.0016337 | 0.00064019 | 0.0016337 | 0.00064019 | 0.0016337 | 0.0007663 | 0.0019556
| Fluorene | 86-73-7 | 0.0021844 |  | 0.0031936 | 0.0081499 | 0.0032397 | 0.0082676 | 0.0032397 | 0.0082676 |  | 0.0038657 | 0.0098651 | 0.00378 | 0.0096465 | 0.0038657 | 0.0098651 | 0.0038657 | 0.0098651 | 0.0038657 | 0.0098651 | 0.0038657 | 0.0098651 | 0.00378 | 0.0096465 | 0.0038657 | 0.0098651 | 0.00378 | 0.0096465 | 0.00378 | 0.0096465 | 0.00378 | 0.0096465 | 0.0045246 | 0.011547
| Indeno[1,2,3-cd]pyrene | 193-39-5 | 1.0711e-05 |  | 1.5659e-05 | 3.9962e-05 | 1.5886e-05 | 4.0539e-05 | 1.5886e-05 | 4.0539e-05 |  | 1.8955e-05 | 4.8372e-05 | 1.8535e-05 | 4.7301e-05 | 1.8955e-05 | 4.8372e-05 | 1.8955e-05 | 4.8372e-05 | 1.8955e-05 | 4.8372e-05 | 1.8955e-05 | 4.8372e-05 | 1.8535e-05 | 4.7301e-05 | 1.8955e-05 | 4.8372e-05 | 1.8535e-05 | 4.7301e-05 | 1.8535e-05 | 4.7301e-05 | 1.8535e-05 | 4.7301e-05 | 2.2186e-05 | 5.6618e-05
| Naphthalene | 91-20-3 | 0.026352 |  | 0.038527 | 0.09832 | 0.039084 | 0.09974 | 0.039084 | 0.09974 |  | 0.046635 | 0.11901 | 0.045602 | 0.11637 | 0.046635 | 0.11901 | 0.046635 | 0.11901 | 0.046635 | 0.11901 | 0.046635 | 0.11901 | 0.045602 | 0.11637 | 0.046635 | 0.11901 | 0.045602 | 0.11637 | 0.045602 | 0.11637 | 0.045602 | 0.11637 | 0.054584 | 0.1393
| Perylene | 198-55-0 | 1.1782e-06 |  | 1.7226e-06 | 4.396e-06 | 1.7475e-06 | 4.4595e-06 | 1.7475e-06 | 4.4595e-06 |  | 2.0851e-06 | 5.3211e-06 | 2.0389e-06 | 5.2032e-06 | 2.0851e-06 | 5.3211e-06 | 2.0851e-06 | 5.3211e-06 | 2.0851e-06 | 5.3211e-06 | 2.0851e-06 | 5.3211e-06 | 2.0389e-06 | 5.2032e-06 | 2.0851e-06 | 5.3211e-06 | 2.0389e-06 | 5.2032e-06 | 2.0389e-06 | 5.2032e-06 | 2.0389e-06 | 5.2032e-06 | 2.4405e-06 | 6.2282e-06
| Phenanthrene | 85-01-8 | 0.0045419 |  | 0.0066403 | 0.016946 | 0.0067362 | 0.017191 | 0.0067362 | 0.017191 |  | 0.0080378 | 0.020512 | 0.0078597 | 0.020058 | 0.0080378 | 0.020512 | 0.0080378 | 0.020512 | 0.0080378 | 0.020512 | 0.0080378 | 0.020512 | 0.0078597 | 0.020058 | 0.0080378 | 0.020512 | 0.0078597 | 0.020058 | 0.0078597 | 0.020058 | 0.0078597 | 0.020058 | 0.0094079 | 0.024009
| Pyrene | 129-00-0 | 0.00125 |  | 0.0018275 | 0.0046637 | 0.0018539 | 0.0047311 | 0.0018539 | 0.0047311 |  | 0.0022121 | 0.0056452 | 0.0021631 | 0.0055201 | 0.0022121 | 0.0056452 | 0.0022121 | 0.0056452 | 0.0022121 | 0.0056452 | 0.0022121 | 0.0056452 | 0.0021631 | 0.0055201 | 0.0022121 | 0.0056452 | 0.0021631 | 0.0055201 | 0.0021631 | 0.0055201 | 0.0021631 | 0.0055201 | 0.0025892 | 0.0066074
DIESEL PARTICULATE MATTER (DPM)
| DPM | 200 | 16.9752 |  | 24.8178 | 63.334 | 25.1762 | 64.2488 | 25.1762 | 64.2488 |  | 30.0408 | 76.6629 | 29.3751 | 74.9641 | 30.0408 | 76.6629 | 30.0408 | 76.6629 | 30.0408 | 76.6629 | 30.0408 | 76.6629 | 29.3751 | 74.9641 | 30.0408 | 76.6629 | 29.3751 | 74.9641 | 29.3751 | 74.9641 | 29.3751 | 74.9641 | 35.1613 | 89.7305
Notes
DPF = Diesel Particulate Filter; HAP = Hazardous Air Pollutant; Mgal = 1,000 gallons; TAC = Toxic Air Contaminant.
(a) | Daily emissions estimate (lb/day) = (emission factor [lb/Mgal]) x (fuel consumption [gal/hr]) x (daily hours of operation [hrs/day]) x (Mgal/1,000 gal) | [9 empty] | (b), (c)
| + (cold start emissions [lb/minute]) x (number of cold starts per day) - (emissions per minute, normal operation [lb/minute]) x (number of cold starts per day) | [9 empty] | (3)
|  | Cold start adjustment factor = | 4.3 | (4)
|  | Cold start adjustment factor (formaldehyde) = | 4.8 | (4)
|  | Number of cold starts per day = | 1 | (5)
(b) | Cold start emissions (lb/minute) = (emission factor [lb/Mgal]) x (cold start adjustment factor) x (hourly fuel consumption [Mgal/hr]) / 60
(c) | Emissions per minute, normal operation (lb/minute) = (emission factor [lb/Mgal]) x (hourly fuel consumption [Mgal/hr]) / 60
(d) | Annual emissions estimate (lb/yr) = (emission factor [lb/Mgal]) x (fuel consumption [gal/hr]) x (annual hours of operation [hrs/yr]) x (Mgal/1,000 gal) | [9 empty] | (b), (c)
| + (cold start emissions [lb/minute]) x (number of cold starts per year) - (emissions per minute, normal operation [lb/minute]) x (number of cold starts per year) | [9 empty] | (3)
|  | Cold start adjustment factor = | 4.3 | (4)
|  | Cold start adjustment factor (formaldehyde) = | 4.8 | (4)
|  | Number of cold starts per year = | 12 | (5)
References
(1) | Permit conditions limit Intel to operate 10 EGENs for 10 hours a day and all EGENs for 25 hours a year.
(2) | Emission Factors from the Oregon Department of Environmental Quality, AQ104B, diesel internal combustion, greater
than 750 hp. Ammonia emission factor assumes value for no SNCR or SCR control. DEQ reference CAO Diesel RICE (b).
(3) | Time allotted for cold stats was omitted from the daily/annual operating capacity in emission calculations. Cold start adjustments are not required for metals.
(4) | Cold start adjustment factors provided by the Oregon Department of Environmental Quality. All applicable pollutants, except
formaldehyde, share the same adjustment factor. Cold start adjustments are not required for metals.
(5) | Based on one cold start per month per engine for Preventative Maintenance activities.

## FirePump_RONLER
TESU ID |  |  |  |  | PH #1 |  | PH #2 |  | PH #3 |  |  | PH #4
Fuel Consumption (gal/hr) |  |  |  |  | 10.4 |  | 11.3 |  | 6.6 |  |  | 6.1
Daily Hours of Operation (hrs/day) |  |  |  | (1) | 10 |  | 10 |  | 10 |  |  | 10
Annual Hours of Operation (hrs/yr) |  |  |  | (1) | 50 |  | 50 |  | 50 |  |  | 50
Pollutant |  | CAS | Emission Factor (2) (lb/Mgal) |  | Emissions Estimate (a)
[5 empty] | PH #1 |  | PH #2 |  | PH #3 |  |  | PH #4
[5 empty] | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) |  | Daily (a) (lb/day) | Annual (d) (lb/yr)
METALS
| Antimony and Compounds | 7440-36-0 | 0.00031819 |  | 3.3091e-05 | 0.00016546 | 3.5955e-05 | 0.00017978 | 2.1e-05 | 0.000105 |  | 1.9409e-05 | 9.7047e-05
| Arsenic and Compounds | 7440-38-2 | 0.0016 |  | 0.0001664 | 0.000832 | 0.0001808 | 0.000904 | 0.0001056 | 0.000528 |  | 9.76e-05 | 0.000488
| Barium and Compounds | 7440-39-3 | 0.00037389 |  | 3.8885e-05 | 0.00019442 | 4.225e-05 | 0.00021125 | 2.4677e-05 | 0.00012338 |  | 2.2807e-05 | 0.00011404
| Beryllium and compounds | 7440-41-7 | 4.7708e-06 |  | 4.9617e-07 | 2.4808e-06 | 5.3911e-07 | 2.6955e-06 | 3.1488e-07 | 1.5744e-06 |  | 2.9102e-07 | 1.4551e-06
| Cadmium and Compounds | 7440-43-9 | 0.0015 |  | 0.000156 | 0.00078 | 0.0001695 | 0.0008475 | 9.9e-05 | 0.000495 |  | 9.15e-05 | 0.0004575
| Chromium VI | 18540-29-9 | 0.0001 |  | 1.04e-05 | 5.2e-05 | 1.13e-05 | 5.65e-05 | 6.6e-06 | 3.3e-05 |  | 6.1e-06 | 3.05e-05
| Copper and Compounds | 7440-50-8 | 0.0041 |  | 0.0004264 | 0.002132 | 0.0004633 | 0.0023165 | 0.0002706 | 0.001353 |  | 0.0002501 | 0.0012505
| Cobalt and compounds | 7440-48-4 | 1.5751e-05 |  | 1.6381e-06 | 8.1906e-06 | 1.7799e-06 | 8.8994e-06 | 1.0396e-06 | 5.1979e-06 |  | 9.6082e-07 | 4.8041e-06
| Lead and Compounds | 7439-92-1 | 0.0083 |  | 0.0008632 | 0.004316 | 0.0009379 | 0.0046895 | 0.0005478 | 0.002739 |  | 0.0005063 | 0.0025315
| Manganese and Compounds | 7439-96-5 | 0.0031 |  | 0.0003224 | 0.001612 | 0.0003503 | 0.0017515 | 0.0002046 | 0.001023 |  | 0.0001891 | 0.0009455
| Mercury and Compounds | 7439-97-6 | 0.002 |  | 0.000208 | 0.00104 | 0.000226 | 0.00113 | 0.000132 | 0.00066 |  | 0.000122 | 0.00061
| Nickel and Compounds | 7440-02-0 | 0.0039 |  | 0.0004056 | 0.002028 | 0.0004407 | 0.0022035 | 0.0002574 | 0.001287 |  | 0.0002379 | 0.0011895
| Phosphorus and compounds | 504 | 0.008404 |  | 0.00087401 | 0.0043701 | 0.00094965 | 0.0047483 | 0.00055466 | 0.0027733 |  | 0.00051264 | 0.0025632
| Selenium and Compounds | 7782-49-2 | 0.0022 |  | 0.0002288 | 0.001144 | 0.0002486 | 0.001243 | 0.0001452 | 0.000726 |  | 0.0001342 | 0.000671
| Silver and compounds | 7440-22-4 | 4.8013e-05 |  | 4.9934e-06 | 2.4967e-05 | 5.4255e-06 | 2.7127e-05 | 3.1689e-06 | 1.5844e-05 |  | 2.9288e-06 | 1.4644e-05
| Thallium and compounds | 7440-28-0 | 0.00024009 |  | 2.497e-05 | 0.00012485 | 2.7131e-05 | 0.00013565 | 1.5846e-05 | 7.9231e-05 |  | 1.4646e-05 | 7.3229e-05
| Zinc and compounds | 7440-66-6 | 0.0052262 |  | 0.00054352 | 0.0027176 | 0.00059056 | 0.0029528 | 0.00034493 | 0.0017246 |  | 0.0003188 | 0.001594
ORGANIC COMPOUNDS
| 1,3-Butadiene | 106-99-0 | 0.2174 |  | 0.022734 | 0.11951 | 0.024701 | 0.12986 | 0.014427 | 0.075846 |  | 0.013334 | 0.0701
| Acetaldehyde | 75-07-0 | 0.7833 |  | 0.081911 | 0.43061 | 0.089 | 0.46788 | 0.051982 | 0.27327 |  | 0.048044 | 0.25257
| Acrolein | 107-02-8 | 0.0339 |  | 0.003545 | 0.018636 | 0.0038518 | 0.020249 | 0.0022497 | 0.011827 |  | 0.0020793 | 0.010931
| Benzene | 71-43-2 | 0.1863 |  | 0.019482 | 0.10242 | 0.021168 | 0.11128 | 0.012363 | 0.064996 |  | 0.011427 | 0.060072
| Chlorobenzene | 108-90-7 | 0.0002 |  | 2.0914e-05 | 0.00010995 | 2.2724e-05 | 0.00011946 | 1.3273e-05 | 6.9775e-05 |  | 1.2267e-05 | 6.4489e-05
| Ethylbenzene | 100-41-4 | 0.0109 |  | 0.0011398 | 0.0059922 | 0.0012385 | 0.0065108 | 0.00072336 | 0.0038027 |  | 0.00066856 | 0.0035147
| Formaldehyde | 50-00-0 | 1.7261 |  | 0.18065 | 0.95669 | 0.19628 | 1.0395 | 0.11464 | 0.60713 |  | 0.10596 | 0.56114
| Hexane | 110-54-3 | 0.0269 |  | 0.002813 | 0.014788 | 0.0030564 | 0.016068 | 0.0017852 | 0.0093848 |  | 0.0016499 | 0.0086738
| Propylene | 115-07-1 | 0.47 |  | 0.049149 | 0.25838 | 0.053402 | 0.28074 | 0.031191 | 0.16397 |  | 0.028828 | 0.15155
| Toluene | 108-88-3 | 0.1054 |  | 0.011022 | 0.057943 | 0.011976 | 0.062957 | 0.0069947 | 0.036772 |  | 0.0064648 | 0.033986
| Xylene (mixed isomers) | 1330-20-7 | 0.0424 |  | 0.0044339 | 0.023309 | 0.0048176 | 0.025326 | 0.0028138 | 0.014792 |  | 0.0026006 | 0.013672
INORGANIC COMPOUNDS
| Ammonia | 7664-41-7 | 0.8 |  | 0.083658 | 0.4398 | 0.090897 | 0.47785 | 0.05309 | 0.2791 |  | 0.049068 | 0.25796
| Hydrochloric Acid | 7647-01-0 | 0.1863 |  | 0.019482 | 0.10242 | 0.021168 | 0.11128 | 0.012363 | 0.064996 |  | 0.011427 | 0.060072
POLYCYCLIC AROMATIC HYDROCARBONS (PAH)
| Benzo[a]pyrene | 50-32-8 | 3.52e-05 |  | 3.6809e-06 | 1.9351e-05 | 3.9995e-06 | 2.1026e-05 | 2.336e-06 | 1.228e-05 |  | 2.159e-06 | 1.135e-05
| Naphthalene | 91-20-3 | 0.0197 |  | 0.0020601 | 0.01083 | 0.0022383 | 0.011767 | 0.0013074 | 0.0068729 |  | 0.0012083 | 0.0063522
| PAH | 401 | 0.0362 |  | 0.0037855 | 0.019901 | 0.0041131 | 0.021623 | 0.0024023 | 0.012629 |  | 0.0022203 | 0.011673
DIESEL PARTICULATE MATTER (DPM)
| DPM | 200 | 33.5 |  | 3.5032 | 18.4164 | 3.8063 | 20.0102 | 2.2232 | 11.6873 |  | 2.0547 | 10.8019
Notes
HAP = Hazardous Air Pollutant; Mgal = 1,000 gallons; TAC = Toxic Air Contaminant.
(a) | Daily emissions estimate (lb/day) = (emission factor [lb/Mgal]) x (fuel consumption [gal/hr]) x (daily hours of operation [hrs/day]) x (Mgal/1,000 gal) | [9 empty] | (b), (c)
| + (cold start emissions [lb/minute]) x (number of cold starts per day) - (emissions per minute, normal operation [lb/minute]) x (number of cold starts per day) | [9 empty] | (3)
|  | Cold start adjustment factor = | 4.3 | (4)
|  | Cold start adjustment factor (formaldehyde) = | 4.8 | (4)
|  | Number of cold starts per day = | 1 | (5)
(b) | Cold start emissions (lb/minute) = (emission factor [lb/Mgal]) x (cold start adjustment factor) x (hourly fuel consumption [Mgal/hr]) / 60
(c) | Emissions per minute, normal operation (lb/minute) = (emission factor [lb/Mgal]) x (hourly fuel consumption [Mgal/hr]) / 60
(d) | Annual emissions estimate (lb/yr) = (emission factor [lb/Mgal]) x (fuel consumption [gal/hr]) x (annual hours of operation [hrs/yr]) x (Mgal/1,000 gal) | [9 empty] | (b), (c)
| + (cold start emissions [lb/minute]) x (number of cold starts per year) - (emissions per minute, normal operation [lb/minute]) x (number of cold starts per year) | [9 empty] | (3)
|  | Cold start adjustment factor = | 4.3 | (4)
|  | Cold start adjustment factor (formaldehyde) = | 4.8 | (4)
|  | Number of cold starts per year = | 52 | (5)
References
(1) | Permit conditions limit Intel to operate 10 EGENs for 10 hours a day and all EGENs for 25 hours a year.
(2) | Emission Factors from the Oregon Department of Environmental Quality, AQ104B, diesel internal combustion, less than
750 hp. Ammonia emission factor assumes value for no SNCR or SCR control. DEQ reference CAO Diesel RICE (a).
(3) | Time allotted for cold stats was omitted from the daily/annual operating capacity in emission calculations. Cold start adjustments are not required for metals.
(4) | Cold start adjustment factors provided by the Oregon Department of Environmental Quality. All applicable pollutants, except
formaldehyde, share the same adjustment factor. Cold start adjustments are not required for metals.
(5) | Based on one cold start per month per engine for Preventative Maintenance activities.

## EGEN_ALOHA
TESU ID |  |  |  |  | F15-EG01 |  | F15-EG02 |  | F15-EG03 |  |  | F15.5-EG01 |  | F15.5-EG02
Fuel Consumption (gal/hr) |  |  |  |  | 107.8 |  | 107.8 |  | 107.8 |  |  | 107.86 |  | 107.28
Daily Hours of Operation (hrs/day) |  |  |  | (1) | 10 |  | 10 |  | 10 |  |  | 10 |  | 10
Annual Hours of Operation (hrs/yr) |  |  |  | (1) | 25 |  | 25 |  | 25 |  |  | 25 |  | 25
Pollutant |  | CAS | Emission Factor (2) (lb/Mgal) |  | Emissions Estimate (a)
[5 empty] | F15-EG01 |  | F15-EG02 |  | F15-EG03 |  |  | F15.5-EG01 |  | F15.5-EG02
[5 empty] | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr) |  | Daily (a) (lb/day) | Annual (d) (lb/yr) | Daily (a) (lb/day) | Annual (d) (lb/yr)
METALS
| Antimony and Compounds | 7440-36-0 | 0.00031819 |  | 0.00034301 | 0.00085751 | 0.00034301 | 0.00085751 | 0.00034301 | 0.00085751 |  | 0.0003432 | 0.00085799 | 0.00034135 | 0.00085338
| Arsenic and Compounds | 7440-38-2 | 0.0016 |  | 0.0017248 | 0.004312 | 0.0017248 | 0.004312 | 0.0017248 | 0.004312 |  | 0.0017258 | 0.0043144 | 0.0017165 | 0.0042912
| Barium and Compounds | 7440-39-3 | 0.00037389 |  | 0.00040306 | 0.0010076 | 0.00040306 | 0.0010076 | 0.00040306 | 0.0010076 |  | 0.00040328 | 0.0010082 | 0.00040111 | 0.0010028
| Beryllium and compounds | 7440-41-7 | 4.7708e-06 |  | 5.143e-06 | 1.2857e-05 | 5.143e-06 | 1.2857e-05 | 5.143e-06 | 1.2857e-05 |  | 5.1458e-06 | 1.2865e-05 | 5.1182e-06 | 1.2795e-05
| Cadmium and Compounds | 7440-43-9 | 0.0015 |  | 0.001617 | 0.0040425 | 0.001617 | 0.0040425 | 0.001617 | 0.0040425 |  | 0.0016179 | 0.0040447 | 0.0016092 | 0.004023
| Chromium VI | 18540-29-9 | 0.0001 |  | 0.0001078 | 0.0002695 | 0.0001078 | 0.0002695 | 0.0001078 | 0.0002695 |  | 0.00010786 | 0.00026965 | 0.00010728 | 0.0002682
| Copper and Compounds | 7440-50-8 | 0.0041 |  | 0.0044198 | 0.01105 | 0.0044198 | 0.01105 | 0.0044198 | 0.01105 |  | 0.0044223 | 0.011056 | 0.0043985 | 0.010996
| Cobalt and compounds | 7440-48-4 | 1.5751e-05 |  | 1.698e-05 | 4.2449e-05 | 1.698e-05 | 4.2449e-05 | 1.698e-05 | 4.2449e-05 |  | 1.6989e-05 | 4.2473e-05 | 1.6898e-05 | 4.2245e-05
| Lead and Compounds | 7439-92-1 | 0.0083 |  | 0.0089474 | 0.022368 | 0.0089474 | 0.022368 | 0.0089474 | 0.022368 |  | 0.0089524 | 0.022381 | 0.0089042 | 0.022261
| Manganese and Compounds | 7439-96-5 | 0.0031 |  | 0.0033418 | 0.0083545 | 0.0033418 | 0.0083545 | 0.0033418 | 0.0083545 |  | 0.0033437 | 0.0083591 | 0.0033257 | 0.0083142
| Mercury and Compounds | 7439-97-6 | 0.002 |  | 0.002156 | 0.00539 | 0.002156 | 0.00539 | 0.002156 | 0.00539 |  | 0.0021572 | 0.005393 | 0.0021456 | 0.005364
| Nickel and Compounds | 7440-02-0 | 0.0039 |  | 0.0042042 | 0.01051 | 0.0042042 | 0.01051 | 0.0042042 | 0.01051 |  | 0.0042065 | 0.010516 | 0.0041839 | 0.01046
| Phosphorus and compounds | 504 | 0.008404 |  | 0.0090595 | 0.022649 | 0.0090595 | 0.022649 | 0.0090595 | 0.022649 |  | 0.0090645 | 0.022661 | 0.0090158 | 0.022539
| Selenium and Compounds | 7782-49-2 | 0.0022 |  | 0.0023716 | 0.005929 | 0.0023716 | 0.005929 | 0.0023716 | 0.005929 |  | 0.0023729 | 0.0059323 | 0.0023602 | 0.0059004
| Silver and compounds | 7440-22-4 | 4.8013e-05 |  | 5.1758e-05 | 0.0001294 | 5.1758e-05 | 0.0001294 | 5.1758e-05 | 0.0001294 |  | 5.1787e-05 | 0.00012947 | 5.1508e-05 | 0.00012877
| Thallium and compounds | 7440-28-0 | 0.00024009 |  | 0.00025882 | 0.00064705 | 0.00025882 | 0.00064705 | 0.00025882 | 0.00064705 |  | 0.00025897 | 0.00064741 | 0.00025757 | 0.00064393
| Zinc and compounds | 7440-66-6 | 0.0052262 |  | 0.0056338 | 0.014085 | 0.0056338 | 0.014085 | 0.0056338 | 0.014085 |  | 0.005637 | 0.014092 | 0.0056066 | 0.014017
ORGANIC COMPOUNDS
| 1,3-Butadiene | 106-99-0 | 0.2174 |  | 0.23565 | 0.60136 | 0.23565 | 0.60136 | 0.23565 | 0.60136 |  | 0.23578 | 0.6017 | 0.23451 | 0.59846
| Acetaldehyde | 75-07-0 | 0.7833 |  | 0.84904 | 2.1667 | 0.84904 | 2.1667 | 0.84904 | 2.1667 |  | 0.84951 | 2.1679 | 0.84495 | 2.1563
| Acrolein | 107-02-8 | 0.0339 |  | 0.036745 | 0.093772 | 0.036745 | 0.093772 | 0.036745 | 0.093772 |  | 0.036766 | 0.093825 | 0.036568 | 0.09332
| Benzene | 71-43-2 | 0.1863 |  | 0.20194 | 0.51533 | 0.20194 | 0.51533 | 0.20194 | 0.51533 |  | 0.20205 | 0.51562 | 0.20096 | 0.51285
| Chlorobenzene | 108-90-7 | 0.0002 |  | 0.00021679 | 0.00055323 | 0.00021679 | 0.00055323 | 0.00021679 | 0.00055323 |  | 0.00021691 | 0.00055354 | 0.00021574 | 0.00055056
| Ethylbenzene | 100-41-4 | 0.0109 |  | 0.011815 | 0.030151 | 0.011815 | 0.030151 | 0.011815 | 0.030151 |  | 0.011821 | 0.030168 | 0.011758 | 0.030006
| Formaldehyde | 50-00-0 | 1.7261 |  | 1.8725 | 4.7933 | 1.8725 | 4.7933 | 1.8725 | 4.7933 |  | 1.8736 | 4.7959 | 1.8635 | 4.7701
| Hexane | 110-54-3 | 0.0269 |  | 0.029158 | 0.074409 | 0.029158 | 0.074409 | 0.029158 | 0.074409 |  | 0.029174 | 0.074451 | 0.029017 | 0.07405
| Propylene | 115-07-1 | 0.47 |  | 0.50945 | 1.3001 | 0.50945 | 1.3001 | 0.50945 | 1.3001 |  | 0.50973 | 1.3008 | 0.50699 | 1.2938
| Toluene | 108-88-3 | 0.1054 |  | 0.11425 | 0.29155 | 0.11425 | 0.29155 | 0.11425 | 0.29155 |  | 0.11431 | 0.29171 | 0.1137 | 0.29015
| Xylene (mixed isomers) | 1330-20-7 | 0.0424 |  | 0.045959 | 0.11728 | 0.045959 | 0.11728 | 0.045959 | 0.11728 |  | 0.045984 | 0.11735 | 0.045737 | 0.11672
INORGANIC COMPOUNDS
| Ammonia | 7664-41-7 | 0.8 |  | 0.86714 | 2.2129 | 0.86714 | 2.2129 | 0.86714 | 2.2129 |  | 0.86763 | 2.2142 | 0.86296 | 2.2022
| Hydrochloric Acid | 7647-01-0 | 0.1863 |  | 0.20194 | 0.51533 | 0.20194 | 0.51533 | 0.20194 | 0.51533 |  | 0.20205 | 0.51562 | 0.20096 | 0.51285
POLYCYCLIC AROMATIC HYDROCARBONS (PAH)
| Benzo[a]pyrene | 50-32-8 | 3.52e-05 |  | 3.8154e-05 | 9.7368e-05 | 3.8154e-05 | 9.7368e-05 | 3.8154e-05 | 9.7368e-05 |  | 3.8176e-05 | 9.7423e-05 | 3.797e-05 | 9.6899e-05
| Naphthalene | 91-20-3 | 0.0197 |  | 0.021353 | 0.054493 | 0.021353 | 0.054493 | 0.021353 | 0.054493 |  | 0.021365 | 0.054523 | 0.02125 | 0.05423
| PAH | 401 | 0.0362 |  | 0.039238 | 0.10013 | 0.039238 | 0.10013 | 0.039238 | 0.10013 |  | 0.03926 | 0.10019 | 0.039049 | 0.099652
DIESEL PARTICULATE MATTER (DPM)
| DPM | 200 | 33.5 |  | 36.3116 | 92.666 | 36.3116 | 92.666 | 36.3116 | 92.666 |  | 36.3318 | 92.7175 | 36.1365 | 92.219
Notes
HAP = Hazardous Air Pollutant; Mgal = 1,000 gallons; TAC = Toxic Air Contaminant.
(a) | Daily emissions estimate (lb/day) = (emission factor [lb/Mgal]) x (fuel consumption [gal/hr]) x (daily hours of operation [hrs/day]) x (Mgal/1,000 gal) | [9 empty] | (b), (c)
| + (cold start emissions [lb/minute]) x (number of cold starts per day) - (emissions per minute, normal operation [lb/minute]) x (number of cold starts per day) | [9 empty] | (3)
|  | Cold start adjustment factor = | 4.3 | (4)
|  | Cold start adjustment factor (formaldehyde) = | 4.8 | (4)
|  | Number of cold starts per day = | 1 | (5)
(b) | Cold start emissions (lb/minute) = (emission factor [lb/Mgal]) x (cold start adjustment factor) x (hourly fuel consumption [Mgal/hr]) / 60
(c) | Emissions per minute, normal operation (lb/minute) = (emission factor [lb/Mgal]) x (hourly fuel consumption [Mgal/hr]) / 60
(d) | Annual emissions estimate (lb/yr) = (emission factor [lb/Mgal]) x (fuel consumption [gal/hr]) x (annual hours of operation [hrs/yr]) x (Mgal/1,000 gal) | [9 empty] | (b), (c)
| + (cold start emissions [lb/minute]) x (number of cold starts per year) - (emissions per minute, normal operation [lb/minute]) x (number of cold starts per year) | [9 empty] | (3)
|  | Cold start adjustment factor = | 4.3 | (4)
|  | Cold start adjustment factor (formaldehyde) = | 4.8 | (4)
|  | Number of cold starts per year = | 12 | (5)
References
(1) | Permit conditions limit Intel to operate 10 EGENs for 10 hours a day and all EGENs for 25 hours a year.
(2) | Emission Factors from the Oregon Department of Environmental Quality, AQ104B, diesel internal combustion, less than
750 hp. Ammonia emission factor assumes value for no SNCR or SCR control. DEQ reference CAO Diesel RICE (a).
(3) | Time allotted for cold stats was omitted from the daily/annual operating capacity in emission calculations. Cold start adjustments are not required for metals.
(4) | Cold start adjustment factors provided by the Oregon Department of Environmental Quality. All applicable pollutants, except
formaldehyde, share the same adjustment factor. Cold start adjustments are not required for metals.
(5) | Based on one cold start per month per engine for Preventative Maintenance activities.