## TOC
Table of Contents
Intel Corporation
Table | Name
Table 1 | Input Emergency Generator Rates and Parameters
Ronler Acres
Table 2 | Emergency Generator with DPF, Pre-2006 and <750 hp TAC Emission Estimates—Ronler Campus
Table 3 | Emergency Generator—DPF, Post 2006, > 750 hp TAC Emission Estimates—Ronler Acres
Table 4 | Emergency Generator—No DPF, Pre-2006, or < 750 hp TAC Emission Estimates—Ronler Acres
Table 5 | Emergency Generator—No DPF, Post 2006, > 750 hp TAC Emission Estimates—Ronler Acres
Table 6 | Fire Pumps TAC Emission Estimates—Ronler Acres
Aloha
Table 7 | Emergency Generator TAC Emission Estimates—Aloha Campus
Facility
Table 8 | Daily TAC Emission Estimate Summary—Emergency Generators
Table 9 | Annual TAC Emission Estimate Summary—Emergency Generators

## Input_EGEN
Table 1
Input Emergency Generator Rates and Parameters
Intel Corporation
Toxics Emissions Sub-Unit (TESU) ID |  | Site | Building | Install Date | Size (hp) | Diesel Particulate Filter (Yes/No) | Fuel Consumption (1) (gal/hr) | Daily Hours of Operation (hrs/day) | Annual Hours of Operation (3) (hrs/yr) | Stack ID
RA1-ELEC-CPS-GEN01 |  | Ronler Acres | RA1 | 1996 | 2155 | No | 113.51 | 10 | 25 | EGR1_01
RA1-ELEC-CPS-GEN02 |  | Ronler Acres | RA1 | 1996 | 2155 | No | 113.51 | 10 | 25 | EGR1_02
RA1-ELEC-CPS-GEN03 |  | Ronler Acres | RA1 | 1996 | 2155 | No | 113.51 | 10 | 25 | EGR1_03
RA1-ELEC-CPS-GEN04 |  | Ronler Acres | RA1 | 1996 | 2155 | No | 113.51 | 10 | 25 | EGR1_04
D1C-CPS-GEN01 |  | Ronler Acres | D1C | 1998 | 1818 | No | 89.71 | 10 | 25 | EGDC_01
D1C-CPS-GEN02 |  | Ronler Acres | D1C | 1998 | 1818 | No | 89.71 | 10 | 25 | EGDC_02
D1C-CPS-GEN03 |  | Ronler Acres | D1C | 1998 | 1818 | No | 89.71 | 10 | 25 | EGDC_03
D1C-EPS-GEN01 |  | Ronler Acres | D1C | 1998 | 2561 | No | 123 | 10 | 25 | EGDC_04
D1C-EPS-GEN02 |  | Ronler Acres | D1C | 1998 | 2561 | No | 123 | 10 | 25 | EGDC_05
RB1-EPS-GEN01 |  | Ronler Acres | RB1 | 1998 | 2836 | No | 137.5 | 10 | 25 | EGRB1_01
RP1-EPS-GEN01 |  | Ronler Acres | RP1 | 2000 | 2848 | No | 145.4 | 10 | 25 | EGRP1_01
RP1-GEN-2 |  | Ronler Acres | RP1 | Future - TBD | 2848 | No | 145.4 | 10 | 25 | EGRP1_02
EPS-GEN01 |  | Ronler Acres | D1D EGEN | 2002 | 2885 | No | 147.46 | 10 | 25 | EGDD_01
EPS-GEN02 |  | Ronler Acres | D1D EGEN | 2002 | 2885 | No | 147.46 | 10 | 25 | EGDD_02
EPS-GEN03 |  | Ronler Acres | D1D EGEN | 2002 | 2885 | No | 147.46 | 10 | 25 | EGDD_03
EPS-GEN04 |  | Ronler Acres | D1D EGEN | 2002 | 2885 | No | 147.46 | 10 | 25 | EGDD_04
EPS-GEN05 |  | Ronler Acres | D1D EGEN | 2002 | 2885 | No | 147.46 | 10 | 25 | EGDD_05
EPS-GEN06 |  | Ronler Acres | D1D EGEN | 2002 | 2885 | No | 147.46 | 10 | 25 | EGDD_06
D1D-GEN-7 |  | Ronler Acres | D1D EGEN | Future - TBD | 2885 | No | 147.5 | 10 | 25 | EGDD_07
RS4-ELEC-EG-4-1 |  | Ronler Acres | RS4 | 2005 | 449 | No | 22.9 | 10 | 25 | EGRS4_01
RS6-ELEC-EG-6-1 |  | Ronler Acres | RS6 | 2005 | 449 | No | 22.9 | 10 | 25 | EGRS6_01
RS6-GEN-2 |  | Ronler Acres | RS6 | Future - TBD | 2885 | No | 147.5 | 10 | 25 | EGRS6_02
D1X-GEN-1A |  | Ronler Acres | D1X EGEN1 | 2012 | 3680 | No | 176 | 10 | 25 | EGE1_01
D1X-GEN-1B |  | Ronler Acres | D1X EGEN1 | 2013 | 3705 | No | 172.1 | 10 | 25 | EGE1_02
D1X-GEN-1C |  | Ronler Acres | D1X EGEN1 | 2012 | 3680 | No | 176 | 10 | 25 | EGE1_03
D1X-GEN-2A |  | Ronler Acres | D1X EGEN1 | 2012 | 3680 | No | 176 | 10 | 25 | EGE1_04
D1X-GEN-2B |  | Ronler Acres | D1X EGEN1 | 2012 | 3680 | No | 176 | 10 | 25 | EGE1_05
D1X-GEN-2C |  | Ronler Acres | D1X EGEN1 | 2012 | 3680 | No | 176 | 10 | 25 | EGE1_06
D1X-GEN-3A |  | Ronler Acres | D1X EGEN1 | 2013 | 3705 | No | 172.1 | 10 | 25 | EGE1_07
D1X-GEN-3B |  | Ronler Acres | D1X EGEN1 | 2012 | 3680 | No | 176 | 10 | 25 | EGE1_08
D1X-GEN-3C |  | Ronler Acres | D1X EGEN1 | 2013 | 3705 | No | 172.1 | 10 | 25 | EGE1_09
D1X-GEN-4A |  | Ronler Acres | D1X EGEN1 | 2013 | 3705 | No | 172.1 | 10 | 25 | EGE1_10
D1X-GEN-4B |  | Ronler Acres | D1X EGEN1 | 2013 | 3705 | No | 172.1 | 10 | 25 | EGE1_11
D1X-GEN-4C |  | Ronler Acres | D1X EGEN1 | 2013 | 4265 | Yes | 206 | 10 | 25 | EGE1_13
D1X-GEN-5A |  | Ronler Acres | D1X EGEN1 | 2017 | 4265 | Yes | 206 | 10 | 25 | EGE1_14
D1X-GEN-5B |  | Ronler Acres | D1X EGEN1 | 2017 | 4265 | Yes | 206 | 10 | 25 | EGE1_15
D1X-GEN-5C |  | Ronler Acres | D1X EGEN1 | 2017 | 3632 | No | 172.1 | 10 | 25 | EGE1_12
D1X-GEN-6A |  | Ronler Acres | D1X EGEN1 | 2018 | 4265 | Yes | 206 | 10 | 25 | EGE1_16
D1X-GEN-6B |  | Ronler Acres | D1X EGEN1 | 2018 | 4265 | Yes | 206 | 10 | 25 | EGE1_17
D1X-GEN-6C |  | Ronler Acres | D1X EGEN1 | 2018 | 4265 | Yes | 206 | 10 | 25 | EGE1_18
D1X-GEN-7A |  | Ronler Acres | D1X EGEN1 | Future - TBD | 3632 | Yes | 172 | 10 | 25 | EGE1_19
D1X-GEN-7B |  | Ronler Acres | D1X EGEN1 | Future - TBD | 3632 | Yes | 172 | 10 | 25 | EGE1_20
D1X-GEN-7C |  | Ronler Acres | D1X EGEN1 | Future - TBD | 3632 | Yes | 172 | 10 | 25 | EGE1_21
D1X2-GEN-6A |  | Ronler Acres | CUB5 | Future - TBD | 5028 | Yes | 240 | 10 | 25 | EGC5_16
D1X2-GEN-6B |  | Ronler Acres | CUB5 | Future - TBD | 5028 | Yes | 240 | 10 | 25 | EGC5_17
D1X2-GEN-6C |  | Ronler Acres | CUB5 | Future - TBD | 5028 | Yes | 240 | 10 | 25 | EGC5_18
D1X2-GEN-7A |  | Ronler Acres | CUB5 | Future - TBD | 5028 | Yes | 240 | 10 | 25 | EGC5_19
D1X2-GEN-7B |  | Ronler Acres | CUB5 | Future - TBD | 5028 | Yes | 240 | 10 | 25 | EGC5_20
D1X2-GEN-7C |  | Ronler Acres | CUB5 | Future - TBD | 5028 | Yes | 240 | 10 | 25 | EGC5_21
D1X2-GEN-1A |  | Ronler Acres | CUB5 | 2021 | 5028 | Yes | 240 | 10 | 25 | EGC5_01
D1X2-GEN-1B |  | Ronler Acres | CUB5 | 2021 | 5028 | Yes | 240 | 10 | 25 | EGC5_02
D1X2-GEN-1C |  | Ronler Acres | CUB5 | 2021 | 5028 | Yes | 240 | 10 | 25 | EGC5_03
D1X2-GEN-2A |  | Ronler Acres | CUB5 | 2021 | 5028 | Yes | 240 | 10 | 25 | EGC5_04
D1X2-GEN-2B |  | Ronler Acres | CUB5 | 2021 | 5028 | Yes | 240 | 10 | 25 | EGC5_05
D1X2-GEN-2C |  | Ronler Acres | CUB5 | 2021 | 5028 | Yes | 240 | 10 | 25 | EGC5_06
D1X2-GEN-3A |  | Ronler Acres | CUB5 | 2021 | 5028 | Yes | 240 | 10 | 25 | EGC5_07
D1X2-GEN-3B |  | Ronler Acres | CUB5 | 2021 | 5028 | Yes | 240 | 10 | 25 | EGC5_08
D1X2-GEN-3C |  | Ronler Acres | CUB5 | 2021 | 5028 | Yes | 240 | 10 | 25 | EGC5_09
D1X2-GEN-4A |  | Ronler Acres | CUB5 | 2021 | 5028 | Yes | 240 | 10 | 25 | EGC5_10
D1X2-GEN-4B |  | Ronler Acres | CUB5 | 2021 | 5028 | Yes | 240 | 10 | 25 | EGC5_11
D1X2-GEN-4C |  | Ronler Acres | CUB5 | 2021 | 5028 | Yes | 240 | 10 | 25 | EGC5_12
D1X2-GEN-5A |  | Ronler Acres | CUB5 | Future - TBD | 5028 | Yes | 240 | 10 | 25 | EGC5_13
D1X2-GEN-5B |  | Ronler Acres | CUB5 | Future - TBD | 5028 | Yes | 240 | 10 | 25 | EGC5_14
D1X2-GEN-5C |  | Ronler Acres | CUB5 | Future - TBD | 5028 | Yes | 240 | 10 | 25 | EGC5_15
F20-EPS-1 |  | Ronler Acres | D1B | 2016 | 4265 | Yes | 206 | 10 | 25 | EGDB_01
F20-EPS-2 |  | Ronler Acres | D1B | 2016 | 4265 | Yes | 206 | 10 | 25 | EGDB_02
F20-CPS-1 |  | Ronler Acres | D1B | stored | 2011 | No | 46.4 | 10 | 25 | EGDB_03
F15-EG01 |  | Aloha | F15 | 1994 | 2012 | No | 107.8 | 10 | 25 | EGF15_01
F15-EG02 |  | Aloha | F15 | 1994 | 2012 | No | 107.8 | 10 | 25 | EGF15_02
F15-EG03 |  | Aloha | F15 | 1994 | 2012 | No | 107.8 | 10 | 25 | EGF15_03
F15.5-EG01 |  | Aloha | F5 | 2001 | 2153 | No | 107.86 | 10 | 25 | EGF5_01
F15.5-EG02 |  | Aloha | F5 | 2001 | 2157 | No | 107.28 | 10 | 25 | EGF5_02
PH #1 |  | Ronler Acres | Pump House #1 | 2009 | 208 | No | 10.4 | 10 | 50 | FIPH1_01
PH #2 |  | Ronler Acres | Pump House #2 | 2013 | 215 | No | 11.3 | 10 | 50 | FIPH2_01
PH #3 |  | Ronler Acres | Pump House #3 | 2009 | 130 | No | 6.6 | 10 | 50 | FIRS4_01
PH #4 |  | Ronler Acres | Pump House #4 | 2021 | 118 | No | 6.1 | 10 | 50 | FIC5_01
N2-GEN-1A |  | Ronler Acres | N2 Plant | 2017 | 603.5 | Yes | 30.1 | 10 | 25 | EGN2_01
IWW-GEN-1 |  | Ronler Acres | IWW | 2018 | 4265 | Yes | 206 | 10 | 25 | EGIW_02
IWW-GEN-2 |  | Ronler Acres | IWW | Future - TBD | 4265 | Yes | 206 | 10 | 25 | EGIW_01
IWW-PS-1 |  | Ronler Acres | IWW PS | 2018 | 755 | Yes | 34.4 | 10 | 25 | EGIW_03
MAX-EGEN |  | Ronler Acres | RS7 | 2005 | 398 | No | 19.4 | 10 | 25 | EGRS8_01
H2-GEN-1 |  | Ronler Acres | H2 Plant | Future - TBD | 463 | Yes | 21.4 | 10 | 25 | EGH2_01
D1A-GEN-1 |  | Ronler Acres | D1A | Future - TBD | 5028 | Yes | 240 | 10 | 25 | EGDA_01
D1A-GEN-2 |  | Ronler Acres | D1A | Future - TBD | 5028 | Yes | 240 | 10 | 25 | EGDA_02
D1A-GEN-3 |  | Ronler Acres | D1A | Future - TBD | 5028 | Yes | 240 | 10 | 25 | EGDA_03
D1A-GEN-4 |  | Ronler Acres | D1A | Future - TBD | 5028 | Yes | 240 | 10 | 25 | EGDA_04
D1A-GEN-5 |  | Ronler Acres | D1A | Future - TBD | 5028 | Yes | 240 | 10 | 25 | EGDA_05
D1A-GEN-6 |  | Ronler Acres | D1A | Future - TBD | 5028 | Yes | 240 | 10 | 25 | EGDA_06
D1A-GEN-7 |  | Ronler Acres | D1A | Future - TBD | 5028 | Yes | 240 | 10 | 25 | EGDA_07
D1A-GEN-8 |  | Ronler Acres | D1A | Future - TBD | 5028 | Yes | 240 | 10 | 25 | EGDA_08
References
(1) | Information provided by Intel.
(2) | Emergency generators are limited to 10 hours/day. Although only 10 generators are permitted to operate in one day, daily emissions have been provided for all
emergency generators for informational purposes only. Intel will operate a maximum on 10 emergency generators in one day.
(3) | Emergency generators are limited to 25 hours/year.

## EGEN_DPF_a_RONLER
Table 2
Emergency Generator with DPF, Pre-2006 and <750 hp TAC Emission Estimates—Ronler Campus
Intel Corporation
Sub TEU ID | [6 empty] | N2-GEN-1A |  |  |  | H2-GEN-1
Fuel Consumption (gal/hr) | [5 empty] | (1) | 30.1 |  |  |  | 21.4
Daily Hours of Operation (hrs/day) | [5 empty] | (1) | 10 |  |  |  | 10
Annual Hours of Operation (hrs/yr) | [5 empty] | (1) | 25 |  |  |  | 25
Pollutant |  | CAS | Emission Factor (2) (lb/Mgal) |  | Johnson Matthey DPF Control Efficiency (%) |  | Emissions Estimate
[7 empty] | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr)
METALS
| Antimony and Compounds | 7440-36-0 | 0.00031819 |  | 70 | (3) | 2.8732e-05 | (a) | 7.1831e-05 | (e) | 2.0428e-05 | (a) | 5.1069e-05 | (e)
| Arsenic and Compounds | 7440-38-2 | 0.0016 |  | 70 | (3) | 0.00014448 | (a) | 0.0003612 | (e) | 0.00010272 | (a) | 0.0002568 | (e)
| Barium and Compounds | 7440-39-3 | 0.00037389 |  | 94.5 | (7) | 6.1898e-06 | (a) | 1.5475e-05 | (e) | 4.4007e-06 | (a) | 1.1002e-05 | (e)
| Beryllium and compounds | 7440-41-7 | 4.7708e-06 |  | 70 | (3) | 4.3081e-07 | (a) | 1.077e-06 | (e) | 3.0629e-07 | (a) | 7.6572e-07 | (e)
| Cadmium and Compounds | 7440-43-9 | 0.0015 |  | 70 | (3) | 0.00013545 | (a) | 0.00033863 | (e) | 9.63e-05 | (a) | 0.00024075 | (e)
| Chromium VI | 18540-29-9 | 0.0001 |  | 94.5 | (7) | 1.6555e-06 | (a) | 4.1388e-06 | (e) | 1.177e-06 | (a) | 2.9425e-06 | (e)
| Copper and Compounds | 7440-50-8 | 0.0041 |  | 94.5 | (7) | 6.7876e-05 | (a) | 0.00016969 | (e) | 4.8257e-05 | (a) | 0.00012064 | (e)
| Cobalt and compounds | 7440-48-4 | 1.5751e-05 |  | 70 | (3) | 1.4223e-06 | (a) | 3.5558e-06 | (e) | 1.0112e-06 | (a) | 2.5281e-06 | (e)
| Lead and Compounds | 7439-92-1 | 0.0083 |  | 70 | (7) | 0.00074949 | (a) | 0.0018737 | (e) | 0.00053286 | (a) | 0.0013322 | (e)
| Manganese and Compounds | 7439-96-5 | 0.0031 |  | 94.5 | (7) | 5.1321e-05 | (a) | 0.0001283 | (e) | 3.6487e-05 | (a) | 9.1218e-05 | (e)
| Mercury and Compounds | 7439-97-6 | 0.002 |  | 40 | (7) | 0.0003612 | (a) | 0.000903 | (e) | 0.0002568 | (a) | 0.000642 | (e)
| Nickel and Compounds | 7440-02-0 | 0.0039 |  | 94.5 | (7) | 6.4565e-05 | (a) | 0.00016141 | (e) | 4.5903e-05 | (a) | 0.00011476 | (e)
| Phosphorus and compounds | 504 | 0.008404 |  | 95 | (7) | 0.00012648 | (a) | 0.0003162 | (e) | 8.9923e-05 | (a) | 0.00022481 | (e)
| Selenium and Compounds | 7782-49-2 | 0.0022 |  | 70 | (3) | 0.00019866 | (a) | 0.00049665 | (e) | 0.00014124 | (a) | 0.0003531 | (e)
| Silver and compounds | 7440-22-4 | 4.8013e-05 |  | 70 | (3) | 4.3356e-06 | (a) | 1.0839e-05 | (e) | 3.0824e-06 | (a) | 7.7061e-06 | (e)
| Thallium and compounds | 7440-28-0 | 0.00024009 |  | 70 | (3) | 2.168e-05 | (a) | 5.4201e-05 | (e) | 1.5414e-05 | (a) | 3.8535e-05 | (e)
| Zinc and compounds | 7440-66-6 | 0.0052262 |  | 70 | (3) | 0.00047192 | (a) | 0.0011798 | (e) | 0.00033552 | (a) | 0.0008388 | (e)
ORGANIC COMPOUNDS
| 1,3-Butadiene | 106-99-0 | 0.2174 |  | 70 | (8) | 0.019739 | (b) | 0.050374 | (f) | 0.014034 | (b) | 0.035814 | (f)
| Acetaldehyde | 75-07-0 | 0.7833 |  | 63 | (7) | 0.087716 | (b) | 0.22385 | (f) | 0.062363 | (b) | 0.15915 | (f)
| Acrolein | 107-02-8 | 0.0339 |  | 70 | (7) | 0.003078 | (b) | 0.007855 | (f) | 0.0021884 | (b) | 0.0055846 | (f)
| Benzene | 71-43-2 | 0.1863 |  | 65 | (7) | 0.019735 | (b) | 0.050362 | (f) | 0.014031 | (b) | 0.035806 | (f)
| Chlorobenzene | 108-90-7 | 0.0002 |  | 63 | (8) | 2.2397e-05 | (b) | 5.7155e-05 | (f) | 1.5923e-05 | (b) | 4.0635e-05 | (f)
| Ethylbenzene | 100-41-4 | 0.0109 |  | 67 | (7) | 0.0010887 | (b) | 0.0027782 | (f) | 0.00077399 | (b) | 0.0019752 | (f)
| Formaldehyde | 50-00-0 | 1.7261 |  | 65 | (7) | 0.183 | (b) | 0.46843 | (f) | 0.1301 | (b) | 0.33304 | (f)
| Hexane | 110-54-3 | 0.0269 |  | 60 | (7) | 0.0032566 | (b) | 0.0083107 | (f) | 0.0023153 | (b) | 0.0059086 | (f)
| Propylene | 115-07-1 | 0.47 |  | 63 | (8) | 0.052632 | (b) | 0.13431 | (f) | 0.037419 | (b) | 0.095493 | (f)
| Toluene | 108-88-3 | 0.1054 |  | 73 | (7) | 0.008613 | (b) | 0.02198 | (f) | 0.0061235 | (b) | 0.015627 | (f)
| Xylene (mixed isomers) | 1330-20-7 | 0.0424 |  | 66 | (7) | 0.0043631 | (b) | 0.011134 | (f) | 0.003102 | (b) | 0.0079162 | (f)
INORGANIC COMPOUNDS
| Ammonia | 7664-41-7 | 0.8 |  | 0 |  | 0.24212 | (b) | 0.61789 | (f) | 0.17214 | (b) | 0.4393 | (f)
| Hydrochloric Acid | 7647-01-0 | 0.1863 |  | 0 |  | 0.056385 | (b) | 0.14389 | (f) | 0.040087 | (b) | 0.1023 | (f)
POLYCYCLIC AROMATIC HYDROCARBONS (PAH)
| Benzo[a]pyrene | 50-32-8 | 3.52e-05 |  | 65 | (7) | 3.7287e-06 | (b) | 9.5155e-06 | (f) | 2.651e-06 | (b) | 6.7652e-06 | (f)
| Naphthalene | 91-20-3 | 0.0197 |  | 65 | (7) | 0.0020868 | (b) | 0.0053255 | (f) | 0.0014836 | (b) | 0.0037862 | (f)
| PAH | 401 | 0.0362 |  | 63 | (7) | 0.0040538 | (b) | 0.010345 | (f) | 0.0028821 | (b) | 0.007355 | (f)
DIESEL PARTICULATE MATTER (DPM)
| DPM | 200 | 33.5 |  | 93 | (9) | 0.70973 | (b) | 1.8112 | (f) | 0.50459 | (b) | 1.2877 | (f)
Notes
DPF = Diesel Particulate Filter; HAP = Hazardous Air Pollutant; Mgal = 1,000 gallons; TAC = Toxic Air Contaminant.
(a) | Daily emissions estimate (lb/day) = ([emission factor {lb/Mgal}] x [fuel consumption {gal/hr}] x [daily hours of operation {hrs/day}] x [Mgal/1,000 gal]
x (1 - [DPF control efficiency {%}] / 100))
(b) | Daily emissions estimate (lb/day) = ([emission factor {lb/Mgal}] x [fuel consumption {gal/hr}] x [daily hours of operation {hrs/day}] x [Mgal/1,000 gal]
| + [cold start emissions {lb/minute}] x [number of cold starts per day] - [emissions per minute, normal operation {lb/minute}] x [number of cold starts per day]) | [11 empty] | (c), (d)
| x (1 - [DPF control efficiency {%}] / 100) | [11 empty] | (4)
|  | Cold start adjustment factor = | 4.3 | (5)
|  | Cold start adjustment factor (formaldehyde) = | 4.8 | (5)
|  | Number of cold starts per day = | 1 | (6)
(c) | Cold start emissions (lb/minute) = (emission factor [lb/Mgal]) x [Mgal/1,000 gal] x (cold start adjustment factor) x (hourly fuel consumption [gal/hr]) / 60
(d) | Emissions per minute, normal operation (lb/minute) = (emission factor [lb/Mgal]) x (hourly fuel consumption [gal/hr]) / 60 / 1,000
(e) | Annual emissions estimate (lb/yr) = ([emission factor {lb/Mgal}] x [fuel consumption {gal/hr}] x [annual hours of operation {hrs/yr}] x [Mgal/1,000 gal]
x (1 - [DPF control efficiency {%}] / 100))
(f) | Annual emissions estimate (lb/yr) = ([emission factor {lb/Mgal}] x [fuel consumption {gal/hr}] x [annual hours of operation {hrs/yr}] x [Mgal/1,000 gal] | [11 empty] | (c), (d)
+ [cold start emissions {lb/minute}] x [number of cold starts per year] - [emissions per minute, normal operation {lb/minute}] x [number of cold starts per year])
| x (1 - [DPF control efficiency {%}] / 100)) | [11 empty] | (4)
|  | Cold start adjustment factor = | 4.3 | (5)
|  | Cold start adjustment factor (formaldehyde) = | 4.8 | (5)
|  | Number of cold starts per year = | 12 | (6)
References
(1) | See Table 1, Input Emergency Generator Rates and Parameters
(2) | Emission factors from the Oregon Department of Environmental Quality, AQ104B, diesel internal combustion, less than
750 hp. Ammonia emission factor assumes value for no SNCR or SCR control. DEQ reference CAO Diesel RICE (a).
(3) | Assumed 70 percent per DEQ guidance.
(4) | Time allotted for cold starts was omitted from the daily/annual operating capacity in emission calculations. Cold start adjustments are not required for metals.
(5) | Cold start adjustment factors provided by the Oregon Department of Environmental Quality. All applicable pollutants, except formaldehyde,
share the same adjustment factor. Cold start adjustments are not required for metals.
(6) | Information provided by Intel based on one cold start per month per engine and one minute per cold start.
(7) | Information provided by Johnson Matthey. If a range was provided, the value assumes the midpoint of the range.
(8) | Value based on similar TAC.
(9) | Value based on filterable PM efficiency provided by Johnson Matthey.

## EGEN_DPF_b_RONLER
Table 3
Emergency Generator—DPF, Post 2006, > 750 hp TAC Emission Estimates—Ronler Acres
Intel Corporation
[137 empty] | Rypos |  |  |  | Rypos |  |  |  | Rypos
Sub TEU ID | [8 empty] | D1X-GEN-5A |  |  |  | D1X-GEN-5B |  |  |  | D1X-GEN-4C |  |  |  | D1X-GEN-6A |  |  |  | D1X-GEN-6B |  |  |  | D1X-GEN-6C |  |  |  | D1X-GEN-7A |  |  |  | D1X-GEN-7B |  |  |  | D1X-GEN-7C |  |  |  | D1X2-GEN-6A |  |  |  | D1X2-GEN-6B |  |  |  | D1X2-GEN-6C |  |  |  | D1X2-GEN-7A |  |  |  | D1X2-GEN-7B |  |  |  | D1X2-GEN-7C |  |  |  | D1X2-GEN-1A |  |  |  | D1X2-GEN-1B |  |  |  | D1X2-GEN-1C |  |  |  | D1X2-GEN-2A |  |  |  | D1X2-GEN-2B |  |  |  | D1X2-GEN-2C |  |  |  | D1X2-GEN-3A |  |  |  | D1X2-GEN-3B |  |  |  | D1X2-GEN-3C |  |  |  | D1X2-GEN-4A |  |  |  | D1X2-GEN-4B |  |  |  | D1X2-GEN-4C |  |  |  | D1X2-GEN-5A |  |  |  | D1X2-GEN-5B |  |  |  | D1X2-GEN-5C |  |  |  | F20-EPS-1 |  |  |  | F20-EPS-2 |  |  |  | IWW-GEN-1 |  |  |  | IWW-GEN-2 |  |  |  | IWW-PS-1 |  |  |  | D1A-GEN-1 |  |  |  | D1A-GEN-2 |  |  |  | D1A-GEN-3 |  |  |  | D1A-GEN-4 |  |  |  | D1A-GEN-5 |  |  |  | D1A-GEN-6 |  |  |  | D1A-GEN-7 |  |  |  | D1A-GEN-8
Fuel Consumption (gal/hr) | [7 empty] | (1) | 206 |  |  |  | 206 |  |  |  | 206 |  |  |  | 206 |  |  |  | 206 |  |  |  | 206 |  |  |  | 172 |  |  |  | 172 |  |  |  | 172 |  |  |  | 240 |  |  |  | 240 |  |  |  | 240 |  |  |  | 240 |  |  |  | 240 |  |  |  | 240 |  |  |  | 240 |  |  |  | 240 |  |  |  | 240 |  |  |  | 240 |  |  |  | 240 |  |  |  | 240 |  |  |  | 240 |  |  |  | 240 |  |  |  | 240 |  |  |  | 240 |  |  |  | 240 |  |  |  | 240 |  |  |  | 240 |  |  |  | 240 |  |  |  | 240 |  |  |  | 206 |  |  |  | 206 |  |  |  | 206 |  |  |  | 206 |  |  |  | 34.4 |  |  |  | 240 |  |  |  | 240 |  |  |  | 240 |  |  |  | 240 |  |  |  | 240 |  |  |  | 240 |  |  |  | 240 |  |  |  | 240
Daily Hours of Operation (hrs/day) | [7 empty] | (1) | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10
Annual Hours of Operation (hrs/yr) | [7 empty] | (1) | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25
Pollutant |  | CAS | Emission Factor (2) (lb/Mgal) |  | DPF Control Efficiency (%) |  |  |  | Emissions Estimate
[9 empty] | D1X-GEN-5A |  |  |  | D1X-GEN-5B |  |  |  | D1X-GEN-4C |  |  |  | D1X-GEN-6A |  |  |  | D1X-GEN-6B |  |  |  | D1X-GEN-6C |  |  |  | D1X-GEN-7A |  |  |  | D1X-GEN-7B |  |  |  | D1X-GEN-7C |  |  |  | D1X2-GEN-6A |  |  |  | D1X2-GEN-6B |  |  |  | D1X2-GEN-6C |  |  |  | D1X2-GEN-7A |  |  |  | D1X2-GEN-7B |  |  |  | D1X2-GEN-7C |  |  |  | D1X2-GEN-1A |  |  |  | D1X2-GEN-1B |  |  |  | D1X2-GEN-1C |  |  |  | D1X2-GEN-2A |  |  |  | D1X2-GEN-2B |  |  |  | D1X2-GEN-2C |  |  |  | D1X2-GEN-3A |  |  |  | D1X2-GEN-3B |  |  |  | D1X2-GEN-3C |  |  |  | D1X2-GEN-4A |  |  |  | D1X2-GEN-4B |  |  |  | D1X2-GEN-4C |  |  |  | D1X2-GEN-5A |  |  |  | D1X2-GEN-5B |  |  |  | D1X2-GEN-5C |  |  |  | F20-EPS-1 |  |  |  | F20-EPS-2 |  |  |  | IWW-GEN-1 |  |  |  | IWW-GEN-2 |  |  |  | IWW-PS-1 |  |  |  | D1A-GEN-1 |  |  |  | D1A-GEN-2 |  |  |  | D1A-GEN-3 |  |  |  | D1A-GEN-4 |  |  |  | D1A-GEN-5 |  |  |  | D1A-GEN-6 |  |  |  | D1A-GEN-7 |  |  |  | D1A-GEN-8
[5 empty] | Rypos |  | Johnson Matthey |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr)
METALS
| Antimony and Compounds | 7440-36-0 | 0.00031819 |  | 70 | (3) | 70 | (4) | 0.00019664 | (a) | 0.0004916 | (e) | 0.00019664 | (a) | 0.0004916 | (e) | 0.00019664 | (a) | 0.0004916 | (e) | 0.00019664 | (a) | 0.0004916 | (e) | 0.00019664 | (a) | 0.0004916 | (e) | 0.00019664 | (a) | 0.0004916 | (e) | 0.00016418 | (a) | 0.00041046 | (e) | 0.00016418 | (a) | 0.00041046 | (e) | 0.00016418 | (a) | 0.00041046 | (e) | 0.00022909 | (a) | 0.00057274 | (e) | 0.00022909 | (a) | 0.00057274 | (e) | 0.00022909 | (a) | 0.00057274 | (e) | 0.00022909 | (a) | 0.00057274 | (e) | 0.00022909 | (a) | 0.00057274 | (e) | 0.00022909 | (a) | 0.00057274 | (e) | 0.00022909 | (a) | 0.00057274 | (e) | 0.00022909 | (a) | 0.00057274 | (e) | 0.00022909 | (a) | 0.00057274 | (e) | 0.00022909 | (a) | 0.00057274 | (e) | 0.00022909 | (a) | 0.00057274 | (e) | 0.00022909 | (a) | 0.00057274 | (e) | 0.00022909 | (a) | 0.00057274 | (e) | 0.00022909 | (a) | 0.00057274 | (e) | 0.00022909 | (a) | 0.00057274 | (e) | 0.00022909 | (a) | 0.00057274 | (e) | 0.00022909 | (a) | 0.00057274 | (e) | 0.00022909 | (a) | 0.00057274 | (e) | 0.00022909 | (a) | 0.00057274 | (e) | 0.00022909 | (a) | 0.00057274 | (e) | 0.00022909 | (a) | 0.00057274 | (e) | 0.00019664 | (a) | 0.0004916 | (e) | 0.00019664 | (a) | 0.0004916 | (e) | 0.00019664 | (a) | 0.0004916 | (e) | 0.00019664 | (a) | 0.0004916 | (e) | 3.2837e-05 | (a) | 8.2092e-05 | (e) | 0.00022909 | (a) | 0.00057274 | (e) | 0.00022909 | (a) | 0.00057274 | (e) | 0.00022909 | (a) | 0.00057274 | (e) | 0.00022909 | (a) | 0.00057274 | (e) | 0.00022909 | (a) | 0.00057274 | (e) | 0.00022909 | (a) | 0.00057274 | (e) | 0.00022909 | (a) | 0.00057274 | (e) | 0.00022909 | (a) | 0.00057274 | (e)
| Arsenic and Compounds | 7440-38-2 | 0.00027685 |  | 70 | (3) | 70 | (4) | 0.00017109 | (a) | 0.00042774 | (e) | 0.00017109 | (a) | 0.00042774 | (e) | 0.00017109 | (a) | 0.00042774 | (e) | 0.00017109 | (a) | 0.00042774 | (e) | 0.00017109 | (a) | 0.00042774 | (e) | 0.00017109 | (a) | 0.00042774 | (e) | 0.00014286 | (a) | 0.00035714 | (e) | 0.00014286 | (a) | 0.00035714 | (e) | 0.00014286 | (a) | 0.00035714 | (e) | 0.00019933 | (a) | 0.00049833 | (e) | 0.00019933 | (a) | 0.00049833 | (e) | 0.00019933 | (a) | 0.00049833 | (e) | 0.00019933 | (a) | 0.00049833 | (e) | 0.00019933 | (a) | 0.00049833 | (e) | 0.00019933 | (a) | 0.00049833 | (e) | 0.00019933 | (a) | 0.00049833 | (e) | 0.00019933 | (a) | 0.00049833 | (e) | 0.00019933 | (a) | 0.00049833 | (e) | 0.00019933 | (a) | 0.00049833 | (e) | 0.00019933 | (a) | 0.00049833 | (e) | 0.00019933 | (a) | 0.00049833 | (e) | 0.00019933 | (a) | 0.00049833 | (e) | 0.00019933 | (a) | 0.00049833 | (e) | 0.00019933 | (a) | 0.00049833 | (e) | 0.00019933 | (a) | 0.00049833 | (e) | 0.00019933 | (a) | 0.00049833 | (e) | 0.00019933 | (a) | 0.00049833 | (e) | 0.00019933 | (a) | 0.00049833 | (e) | 0.00019933 | (a) | 0.00049833 | (e) | 0.00019933 | (a) | 0.00049833 | (e) | 0.00017109 | (a) | 0.00042774 | (e) | 0.00017109 | (a) | 0.00042774 | (e) | 0.00017109 | (a) | 0.00042774 | (e) | 0.00017109 | (a) | 0.00042774 | (e) | 2.8571e-05 | (a) | 7.1428e-05 | (e) | 0.00019933 | (a) | 0.00049833 | (e) | 0.00019933 | (a) | 0.00049833 | (e) | 0.00019933 | (a) | 0.00049833 | (e) | 0.00019933 | (a) | 0.00049833 | (e) | 0.00019933 | (a) | 0.00049833 | (e) | 0.00019933 | (a) | 0.00049833 | (e) | 0.00019933 | (a) | 0.00049833 | (e) | 0.00019933 | (a) | 0.00049833 | (e)
| Barium and Compounds | 7440-39-3 | 0.00037389 |  | 70 | (4) | 94.5 | (8) | 4.2362e-05 | (a) | 0.00010591 | (e) | 4.2362e-05 | (a) | 0.00010591 | (e) | 4.2362e-05 | (a) | 0.00010591 | (e) | 4.2362e-05 | (a) | 0.00010591 | (e) | 4.2362e-05 | (a) | 0.00010591 | (e) | 4.2362e-05 | (a) | 0.00010591 | (e) | 3.537e-05 | (a) | 8.8426e-05 | (e) | 3.537e-05 | (a) | 8.8426e-05 | (e) | 3.537e-05 | (a) | 8.8426e-05 | (e) | 4.9354e-05 | (a) | 0.00012338 | (e) | 4.9354e-05 | (a) | 0.00012338 | (e) | 4.9354e-05 | (a) | 0.00012338 | (e) | 4.9354e-05 | (a) | 0.00012338 | (e) | 4.9354e-05 | (a) | 0.00012338 | (e) | 4.9354e-05 | (a) | 0.00012338 | (e) | 4.9354e-05 | (a) | 0.00012338 | (e) | 4.9354e-05 | (a) | 0.00012338 | (e) | 4.9354e-05 | (a) | 0.00012338 | (e) | 4.9354e-05 | (a) | 0.00012338 | (e) | 4.9354e-05 | (a) | 0.00012338 | (e) | 4.9354e-05 | (a) | 0.00012338 | (e) | 4.9354e-05 | (a) | 0.00012338 | (e) | 4.9354e-05 | (a) | 0.00012338 | (e) | 4.9354e-05 | (a) | 0.00012338 | (e) | 4.9354e-05 | (a) | 0.00012338 | (e) | 4.9354e-05 | (a) | 0.00012338 | (e) | 4.9354e-05 | (a) | 0.00012338 | (e) | 4.9354e-05 | (a) | 0.00012338 | (e) | 4.9354e-05 | (a) | 0.00012338 | (e) | 4.9354e-05 | (a) | 0.00012338 | (e) | 4.2362e-05 | (a) | 0.00010591 | (e) | 4.2362e-05 | (a) | 0.00010591 | (e) | 0.00023107 | (a) | 0.00057767 | (e) | 0.00023107 | (a) | 0.00057767 | (e) | 3.8586e-05 | (a) | 9.6464e-05 | (e) | 4.9354e-05 | (a) | 0.00012338 | (e) | 4.9354e-05 | (a) | 0.00012338 | (e) | 4.9354e-05 | (a) | 0.00012338 | (e) | 4.9354e-05 | (a) | 0.00012338 | (e) | 4.9354e-05 | (a) | 0.00012338 | (e) | 4.9354e-05 | (a) | 0.00012338 | (e) | 4.9354e-05 | (a) | 0.00012338 | (e) | 4.9354e-05 | (a) | 0.00012338 | (e)
| Beryllium and compounds | 7440-41-7 | 4.7708e-06 |  | 70 | (3) | 70 | (4) | 2.9484e-06 | (a) | 7.371e-06 | (e) | 2.9484e-06 | (a) | 7.371e-06 | (e) | 2.9484e-06 | (a) | 7.371e-06 | (e) | 2.9484e-06 | (a) | 7.371e-06 | (e) | 2.9484e-06 | (a) | 7.371e-06 | (e) | 2.9484e-06 | (a) | 7.371e-06 | (e) | 2.4618e-06 | (a) | 6.1544e-06 | (e) | 2.4618e-06 | (a) | 6.1544e-06 | (e) | 2.4618e-06 | (a) | 6.1544e-06 | (e) | 3.435e-06 | (a) | 8.5875e-06 | (e) | 3.435e-06 | (a) | 8.5875e-06 | (e) | 3.435e-06 | (a) | 8.5875e-06 | (e) | 3.435e-06 | (a) | 8.5875e-06 | (e) | 3.435e-06 | (a) | 8.5875e-06 | (e) | 3.435e-06 | (a) | 8.5875e-06 | (e) | 3.435e-06 | (a) | 8.5875e-06 | (e) | 3.435e-06 | (a) | 8.5875e-06 | (e) | 3.435e-06 | (a) | 8.5875e-06 | (e) | 3.435e-06 | (a) | 8.5875e-06 | (e) | 3.435e-06 | (a) | 8.5875e-06 | (e) | 3.435e-06 | (a) | 8.5875e-06 | (e) | 3.435e-06 | (a) | 8.5875e-06 | (e) | 3.435e-06 | (a) | 8.5875e-06 | (e) | 3.435e-06 | (a) | 8.5875e-06 | (e) | 3.435e-06 | (a) | 8.5875e-06 | (e) | 3.435e-06 | (a) | 8.5875e-06 | (e) | 3.435e-06 | (a) | 8.5875e-06 | (e) | 3.435e-06 | (a) | 8.5875e-06 | (e) | 3.435e-06 | (a) | 8.5875e-06 | (e) | 3.435e-06 | (a) | 8.5875e-06 | (e) | 2.9484e-06 | (a) | 7.371e-06 | (e) | 2.9484e-06 | (a) | 7.371e-06 | (e) | 2.9484e-06 | (a) | 7.371e-06 | (e) | 2.9484e-06 | (a) | 7.371e-06 | (e) | 4.9235e-07 | (a) | 1.2309e-06 | (e) | 3.435e-06 | (a) | 8.5875e-06 | (e) | 3.435e-06 | (a) | 8.5875e-06 | (e) | 3.435e-06 | (a) | 8.5875e-06 | (e) | 3.435e-06 | (a) | 8.5875e-06 | (e) | 3.435e-06 | (a) | 8.5875e-06 | (e) | 3.435e-06 | (a) | 8.5875e-06 | (e) | 3.435e-06 | (a) | 8.5875e-06 | (e) | 3.435e-06 | (a) | 8.5875e-06 | (e)
| Cadmium and Compounds | 7440-43-9 | 8.0778e-05 |  | 70 | (3) | 70 | (4) | 4.9921e-05 | (a) | 0.0001248 | (e) | 4.9921e-05 | (a) | 0.0001248 | (e) | 4.9921e-05 | (a) | 0.0001248 | (e) | 4.9921e-05 | (a) | 0.0001248 | (e) | 4.9921e-05 | (a) | 0.0001248 | (e) | 4.9921e-05 | (a) | 0.0001248 | (e) | 4.1682e-05 | (a) | 0.0001042 | (e) | 4.1682e-05 | (a) | 0.0001042 | (e) | 4.1682e-05 | (a) | 0.0001042 | (e) | 5.816e-05 | (a) | 0.0001454 | (e) | 5.816e-05 | (a) | 0.0001454 | (e) | 5.816e-05 | (a) | 0.0001454 | (e) | 5.816e-05 | (a) | 0.0001454 | (e) | 5.816e-05 | (a) | 0.0001454 | (e) | 5.816e-05 | (a) | 0.0001454 | (e) | 5.816e-05 | (a) | 0.0001454 | (e) | 5.816e-05 | (a) | 0.0001454 | (e) | 5.816e-05 | (a) | 0.0001454 | (e) | 5.816e-05 | (a) | 0.0001454 | (e) | 5.816e-05 | (a) | 0.0001454 | (e) | 5.816e-05 | (a) | 0.0001454 | (e) | 5.816e-05 | (a) | 0.0001454 | (e) | 5.816e-05 | (a) | 0.0001454 | (e) | 5.816e-05 | (a) | 0.0001454 | (e) | 5.816e-05 | (a) | 0.0001454 | (e) | 5.816e-05 | (a) | 0.0001454 | (e) | 5.816e-05 | (a) | 0.0001454 | (e) | 5.816e-05 | (a) | 0.0001454 | (e) | 5.816e-05 | (a) | 0.0001454 | (e) | 5.816e-05 | (a) | 0.0001454 | (e) | 4.9921e-05 | (a) | 0.0001248 | (e) | 4.9921e-05 | (a) | 0.0001248 | (e) | 4.9921e-05 | (a) | 0.0001248 | (e) | 4.9921e-05 | (a) | 0.0001248 | (e) | 8.3363e-06 | (a) | 2.0841e-05 | (e) | 5.816e-05 | (a) | 0.0001454 | (e) | 5.816e-05 | (a) | 0.0001454 | (e) | 5.816e-05 | (a) | 0.0001454 | (e) | 5.816e-05 | (a) | 0.0001454 | (e) | 5.816e-05 | (a) | 0.0001454 | (e) | 5.816e-05 | (a) | 0.0001454 | (e) | 5.816e-05 | (a) | 0.0001454 | (e) | 5.816e-05 | (a) | 0.0001454 | (e)
| Chromium VI | 18540-29-9 | 6.3144e-05 |  | 70 | (3) | 94.5 | (8) | 7.1543e-06 | (a) | 1.7886e-05 | (e) | 7.1543e-06 | (a) | 1.7886e-05 | (e) | 7.1543e-06 | (a) | 1.7886e-05 | (e) | 7.1543e-06 | (a) | 1.7886e-05 | (e) | 7.1543e-06 | (a) | 1.7886e-05 | (e) | 7.1543e-06 | (a) | 1.7886e-05 | (e) | 5.9735e-06 | (a) | 1.4934e-05 | (e) | 5.9735e-06 | (a) | 1.4934e-05 | (e) | 5.9735e-06 | (a) | 1.4934e-05 | (e) | 8.3351e-06 | (a) | 2.0838e-05 | (e) | 8.3351e-06 | (a) | 2.0838e-05 | (e) | 8.3351e-06 | (a) | 2.0838e-05 | (e) | 8.3351e-06 | (a) | 2.0838e-05 | (e) | 8.3351e-06 | (a) | 2.0838e-05 | (e) | 8.3351e-06 | (a) | 2.0838e-05 | (e) | 8.3351e-06 | (a) | 2.0838e-05 | (e) | 8.3351e-06 | (a) | 2.0838e-05 | (e) | 8.3351e-06 | (a) | 2.0838e-05 | (e) | 8.3351e-06 | (a) | 2.0838e-05 | (e) | 8.3351e-06 | (a) | 2.0838e-05 | (e) | 8.3351e-06 | (a) | 2.0838e-05 | (e) | 8.3351e-06 | (a) | 2.0838e-05 | (e) | 8.3351e-06 | (a) | 2.0838e-05 | (e) | 8.3351e-06 | (a) | 2.0838e-05 | (e) | 8.3351e-06 | (a) | 2.0838e-05 | (e) | 8.3351e-06 | (a) | 2.0838e-05 | (e) | 8.3351e-06 | (a) | 2.0838e-05 | (e) | 8.3351e-06 | (a) | 2.0838e-05 | (e) | 8.3351e-06 | (a) | 2.0838e-05 | (e) | 8.3351e-06 | (a) | 2.0838e-05 | (e) | 7.1543e-06 | (a) | 1.7886e-05 | (e) | 7.1543e-06 | (a) | 1.7886e-05 | (e) | 3.9023e-05 | (a) | 9.7558e-05 | (e) | 3.9023e-05 | (a) | 9.7558e-05 | (e) | 6.5165e-06 | (a) | 1.6291e-05 | (e) | 8.3351e-06 | (a) | 2.0838e-05 | (e) | 8.3351e-06 | (a) | 2.0838e-05 | (e) | 8.3351e-06 | (a) | 2.0838e-05 | (e) | 8.3351e-06 | (a) | 2.0838e-05 | (e) | 8.3351e-06 | (a) | 2.0838e-05 | (e) | 8.3351e-06 | (a) | 2.0838e-05 | (e) | 8.3351e-06 | (a) | 2.0838e-05 | (e) | 8.3351e-06 | (a) | 2.0838e-05 | (e)
| Copper and Compounds | 7440-50-8 | 0.00050214 |  | 70 | (4) | 94.5 | (8) | 5.6892e-05 | (a) | 0.00014223 | (e) | 5.6892e-05 | (a) | 0.00014223 | (e) | 5.6892e-05 | (a) | 0.00014223 | (e) | 5.6892e-05 | (a) | 0.00014223 | (e) | 5.6892e-05 | (a) | 0.00014223 | (e) | 5.6892e-05 | (a) | 0.00014223 | (e) | 4.7502e-05 | (a) | 0.00011875 | (e) | 4.7502e-05 | (a) | 0.00011875 | (e) | 4.7502e-05 | (a) | 0.00011875 | (e) | 6.6282e-05 | (a) | 0.0001657 | (e) | 6.6282e-05 | (a) | 0.0001657 | (e) | 6.6282e-05 | (a) | 0.0001657 | (e) | 6.6282e-05 | (a) | 0.0001657 | (e) | 6.6282e-05 | (a) | 0.0001657 | (e) | 6.6282e-05 | (a) | 0.0001657 | (e) | 6.6282e-05 | (a) | 0.0001657 | (e) | 6.6282e-05 | (a) | 0.0001657 | (e) | 6.6282e-05 | (a) | 0.0001657 | (e) | 6.6282e-05 | (a) | 0.0001657 | (e) | 6.6282e-05 | (a) | 0.0001657 | (e) | 6.6282e-05 | (a) | 0.0001657 | (e) | 6.6282e-05 | (a) | 0.0001657 | (e) | 6.6282e-05 | (a) | 0.0001657 | (e) | 6.6282e-05 | (a) | 0.0001657 | (e) | 6.6282e-05 | (a) | 0.0001657 | (e) | 6.6282e-05 | (a) | 0.0001657 | (e) | 6.6282e-05 | (a) | 0.0001657 | (e) | 6.6282e-05 | (a) | 0.0001657 | (e) | 6.6282e-05 | (a) | 0.0001657 | (e) | 6.6282e-05 | (a) | 0.0001657 | (e) | 5.6892e-05 | (a) | 0.00014223 | (e) | 5.6892e-05 | (a) | 0.00014223 | (e) | 0.00031032 | (a) | 0.0007758 | (e) | 0.00031032 | (a) | 0.0007758 | (e) | 5.182e-05 | (a) | 0.00012955 | (e) | 6.6282e-05 | (a) | 0.0001657 | (e) | 6.6282e-05 | (a) | 0.0001657 | (e) | 6.6282e-05 | (a) | 0.0001657 | (e) | 6.6282e-05 | (a) | 0.0001657 | (e) | 6.6282e-05 | (a) | 0.0001657 | (e) | 6.6282e-05 | (a) | 0.0001657 | (e) | 6.6282e-05 | (a) | 0.0001657 | (e) | 6.6282e-05 | (a) | 0.0001657 | (e)
| Cobalt and compounds | 7440-48-4 | 1.5751e-05 |  | 70 | (3) | 70 | (4) | 9.7342e-06 | (a) | 2.4336e-05 | (e) | 9.7342e-06 | (a) | 2.4336e-05 | (e) | 9.7342e-06 | (a) | 2.4336e-05 | (e) | 9.7342e-06 | (a) | 2.4336e-05 | (e) | 9.7342e-06 | (a) | 2.4336e-05 | (e) | 9.7342e-06 | (a) | 2.4336e-05 | (e) | 8.1276e-06 | (a) | 2.0319e-05 | (e) | 8.1276e-06 | (a) | 2.0319e-05 | (e) | 8.1276e-06 | (a) | 2.0319e-05 | (e) | 1.1341e-05 | (a) | 2.8352e-05 | (e) | 1.1341e-05 | (a) | 2.8352e-05 | (e) | 1.1341e-05 | (a) | 2.8352e-05 | (e) | 1.1341e-05 | (a) | 2.8352e-05 | (e) | 1.1341e-05 | (a) | 2.8352e-05 | (e) | 1.1341e-05 | (a) | 2.8352e-05 | (e) | 1.1341e-05 | (a) | 2.8352e-05 | (e) | 1.1341e-05 | (a) | 2.8352e-05 | (e) | 1.1341e-05 | (a) | 2.8352e-05 | (e) | 1.1341e-05 | (a) | 2.8352e-05 | (e) | 1.1341e-05 | (a) | 2.8352e-05 | (e) | 1.1341e-05 | (a) | 2.8352e-05 | (e) | 1.1341e-05 | (a) | 2.8352e-05 | (e) | 1.1341e-05 | (a) | 2.8352e-05 | (e) | 1.1341e-05 | (a) | 2.8352e-05 | (e) | 1.1341e-05 | (a) | 2.8352e-05 | (e) | 1.1341e-05 | (a) | 2.8352e-05 | (e) | 1.1341e-05 | (a) | 2.8352e-05 | (e) | 1.1341e-05 | (a) | 2.8352e-05 | (e) | 1.1341e-05 | (a) | 2.8352e-05 | (e) | 1.1341e-05 | (a) | 2.8352e-05 | (e) | 9.7342e-06 | (a) | 2.4336e-05 | (e) | 9.7342e-06 | (a) | 2.4336e-05 | (e) | 9.7342e-06 | (a) | 2.4336e-05 | (e) | 9.7342e-06 | (a) | 2.4336e-05 | (e) | 1.6255e-06 | (a) | 4.0638e-06 | (e) | 1.1341e-05 | (a) | 2.8352e-05 | (e) | 1.1341e-05 | (a) | 2.8352e-05 | (e) | 1.1341e-05 | (a) | 2.8352e-05 | (e) | 1.1341e-05 | (a) | 2.8352e-05 | (e) | 1.1341e-05 | (a) | 2.8352e-05 | (e) | 1.1341e-05 | (a) | 2.8352e-05 | (e) | 1.1341e-05 | (a) | 2.8352e-05 | (e) | 1.1341e-05 | (a) | 2.8352e-05 | (e)
| Lead and Compounds | 7439-92-1 | 0.00036367 |  | 70 | (3) | 70 | (8) | 0.00022475 | (a) | 0.00056187 | (e) | 0.00022475 | (a) | 0.00056187 | (e) | 0.00022475 | (a) | 0.00056187 | (e) | 0.00022475 | (a) | 0.00056187 | (e) | 0.00022475 | (a) | 0.00056187 | (e) | 0.00022475 | (a) | 0.00056187 | (e) | 0.00018765 | (a) | 0.00046914 | (e) | 0.00018765 | (a) | 0.00046914 | (e) | 0.00018765 | (a) | 0.00046914 | (e) | 0.00026184 | (a) | 0.00065461 | (e) | 0.00026184 | (a) | 0.00065461 | (e) | 0.00026184 | (a) | 0.00065461 | (e) | 0.00026184 | (a) | 0.00065461 | (e) | 0.00026184 | (a) | 0.00065461 | (e) | 0.00026184 | (a) | 0.00065461 | (e) | 0.00026184 | (a) | 0.00065461 | (e) | 0.00026184 | (a) | 0.00065461 | (e) | 0.00026184 | (a) | 0.00065461 | (e) | 0.00026184 | (a) | 0.00065461 | (e) | 0.00026184 | (a) | 0.00065461 | (e) | 0.00026184 | (a) | 0.00065461 | (e) | 0.00026184 | (a) | 0.00065461 | (e) | 0.00026184 | (a) | 0.00065461 | (e) | 0.00026184 | (a) | 0.00065461 | (e) | 0.00026184 | (a) | 0.00065461 | (e) | 0.00026184 | (a) | 0.00065461 | (e) | 0.00026184 | (a) | 0.00065461 | (e) | 0.00026184 | (a) | 0.00065461 | (e) | 0.00026184 | (a) | 0.00065461 | (e) | 0.00026184 | (a) | 0.00065461 | (e) | 0.00022475 | (a) | 0.00056187 | (e) | 0.00022475 | (a) | 0.00056187 | (e) | 0.00022475 | (a) | 0.00056187 | (e) | 0.00022475 | (a) | 0.00056187 | (e) | 3.7531e-05 | (a) | 9.3827e-05 | (e) | 0.00026184 | (a) | 0.00065461 | (e) | 0.00026184 | (a) | 0.00065461 | (e) | 0.00026184 | (a) | 0.00065461 | (e) | 0.00026184 | (a) | 0.00065461 | (e) | 0.00026184 | (a) | 0.00065461 | (e) | 0.00026184 | (a) | 0.00065461 | (e) | 0.00026184 | (a) | 0.00065461 | (e) | 0.00026184 | (a) | 0.00065461 | (e)
| Manganese and Compounds | 7439-96-5 | 0.00041991 |  | 70 | (3) | 94.5 | (8) | 4.7576e-05 | (a) | 0.00011894 | (e) | 4.7576e-05 | (a) | 0.00011894 | (e) | 4.7576e-05 | (a) | 0.00011894 | (e) | 4.7576e-05 | (a) | 0.00011894 | (e) | 4.7576e-05 | (a) | 0.00011894 | (e) | 4.7576e-05 | (a) | 0.00011894 | (e) | 3.9724e-05 | (a) | 9.9309e-05 | (e) | 3.9724e-05 | (a) | 9.9309e-05 | (e) | 3.9724e-05 | (a) | 9.9309e-05 | (e) | 5.5428e-05 | (a) | 0.00013857 | (e) | 5.5428e-05 | (a) | 0.00013857 | (e) | 5.5428e-05 | (a) | 0.00013857 | (e) | 5.5428e-05 | (a) | 0.00013857 | (e) | 5.5428e-05 | (a) | 0.00013857 | (e) | 5.5428e-05 | (a) | 0.00013857 | (e) | 5.5428e-05 | (a) | 0.00013857 | (e) | 5.5428e-05 | (a) | 0.00013857 | (e) | 5.5428e-05 | (a) | 0.00013857 | (e) | 5.5428e-05 | (a) | 0.00013857 | (e) | 5.5428e-05 | (a) | 0.00013857 | (e) | 5.5428e-05 | (a) | 0.00013857 | (e) | 5.5428e-05 | (a) | 0.00013857 | (e) | 5.5428e-05 | (a) | 0.00013857 | (e) | 5.5428e-05 | (a) | 0.00013857 | (e) | 5.5428e-05 | (a) | 0.00013857 | (e) | 5.5428e-05 | (a) | 0.00013857 | (e) | 5.5428e-05 | (a) | 0.00013857 | (e) | 5.5428e-05 | (a) | 0.00013857 | (e) | 5.5428e-05 | (a) | 0.00013857 | (e) | 5.5428e-05 | (a) | 0.00013857 | (e) | 4.7576e-05 | (a) | 0.00011894 | (e) | 4.7576e-05 | (a) | 0.00011894 | (e) | 0.00025951 | (a) | 0.00064877 | (e) | 0.00025951 | (a) | 0.00064877 | (e) | 4.3335e-05 | (a) | 0.00010834 | (e) | 5.5428e-05 | (a) | 0.00013857 | (e) | 5.5428e-05 | (a) | 0.00013857 | (e) | 5.5428e-05 | (a) | 0.00013857 | (e) | 5.5428e-05 | (a) | 0.00013857 | (e) | 5.5428e-05 | (a) | 0.00013857 | (e) | 5.5428e-05 | (a) | 0.00013857 | (e) | 5.5428e-05 | (a) | 0.00013857 | (e) | 5.5428e-05 | (a) | 0.00013857 | (e)
| Mercury and Compounds | 7439-97-6 | 1.5107e-05 |  | 70 | (3) | 40 | (8) | 1.8673e-05 | (a) | 4.6682e-05 | (e) | 1.8673e-05 | (a) | 4.6682e-05 | (e) | 1.8673e-05 | (a) | 4.6682e-05 | (e) | 1.8673e-05 | (a) | 4.6682e-05 | (e) | 1.8673e-05 | (a) | 4.6682e-05 | (e) | 1.8673e-05 | (a) | 4.6682e-05 | (e) | 1.5591e-05 | (a) | 3.8977e-05 | (e) | 1.5591e-05 | (a) | 3.8977e-05 | (e) | 1.5591e-05 | (a) | 3.8977e-05 | (e) | 2.1755e-05 | (a) | 5.4386e-05 | (e) | 2.1755e-05 | (a) | 5.4386e-05 | (e) | 2.1755e-05 | (a) | 5.4386e-05 | (e) | 2.1755e-05 | (a) | 5.4386e-05 | (e) | 2.1755e-05 | (a) | 5.4386e-05 | (e) | 2.1755e-05 | (a) | 5.4386e-05 | (e) | 2.1755e-05 | (a) | 5.4386e-05 | (e) | 2.1755e-05 | (a) | 5.4386e-05 | (e) | 2.1755e-05 | (a) | 5.4386e-05 | (e) | 2.1755e-05 | (a) | 5.4386e-05 | (e) | 2.1755e-05 | (a) | 5.4386e-05 | (e) | 2.1755e-05 | (a) | 5.4386e-05 | (e) | 2.1755e-05 | (a) | 5.4386e-05 | (e) | 2.1755e-05 | (a) | 5.4386e-05 | (e) | 2.1755e-05 | (a) | 5.4386e-05 | (e) | 2.1755e-05 | (a) | 5.4386e-05 | (e) | 2.1755e-05 | (a) | 5.4386e-05 | (e) | 2.1755e-05 | (a) | 5.4386e-05 | (e) | 2.1755e-05 | (a) | 5.4386e-05 | (e) | 2.1755e-05 | (a) | 5.4386e-05 | (e) | 2.1755e-05 | (a) | 5.4386e-05 | (e) | 1.8673e-05 | (a) | 4.6682e-05 | (e) | 1.8673e-05 | (a) | 4.6682e-05 | (e) | 9.3363e-06 | (a) | 2.3341e-05 | (e) | 9.3363e-06 | (a) | 2.3341e-05 | (e) | 1.5591e-06 | (a) | 3.8977e-06 | (e) | 2.1755e-05 | (a) | 5.4386e-05 | (e) | 2.1755e-05 | (a) | 5.4386e-05 | (e) | 2.1755e-05 | (a) | 5.4386e-05 | (e) | 2.1755e-05 | (a) | 5.4386e-05 | (e) | 2.1755e-05 | (a) | 5.4386e-05 | (e) | 2.1755e-05 | (a) | 5.4386e-05 | (e) | 2.1755e-05 | (a) | 5.4386e-05 | (e) | 2.1755e-05 | (a) | 5.4386e-05 | (e)
| Nickel and Compounds | 7440-02-0 | 0.00018223 |  | 70 | (3) | 94.5 | (8) | 2.0647e-05 | (a) | 5.1616e-05 | (e) | 2.0647e-05 | (a) | 5.1616e-05 | (e) | 2.0647e-05 | (a) | 5.1616e-05 | (e) | 2.0647e-05 | (a) | 5.1616e-05 | (e) | 2.0647e-05 | (a) | 5.1616e-05 | (e) | 2.0647e-05 | (a) | 5.1616e-05 | (e) | 1.7239e-05 | (a) | 4.3097e-05 | (e) | 1.7239e-05 | (a) | 4.3097e-05 | (e) | 1.7239e-05 | (a) | 4.3097e-05 | (e) | 2.4054e-05 | (a) | 6.0136e-05 | (e) | 2.4054e-05 | (a) | 6.0136e-05 | (e) | 2.4054e-05 | (a) | 6.0136e-05 | (e) | 2.4054e-05 | (a) | 6.0136e-05 | (e) | 2.4054e-05 | (a) | 6.0136e-05 | (e) | 2.4054e-05 | (a) | 6.0136e-05 | (e) | 2.4054e-05 | (a) | 6.0136e-05 | (e) | 2.4054e-05 | (a) | 6.0136e-05 | (e) | 2.4054e-05 | (a) | 6.0136e-05 | (e) | 2.4054e-05 | (a) | 6.0136e-05 | (e) | 2.4054e-05 | (a) | 6.0136e-05 | (e) | 2.4054e-05 | (a) | 6.0136e-05 | (e) | 2.4054e-05 | (a) | 6.0136e-05 | (e) | 2.4054e-05 | (a) | 6.0136e-05 | (e) | 2.4054e-05 | (a) | 6.0136e-05 | (e) | 2.4054e-05 | (a) | 6.0136e-05 | (e) | 2.4054e-05 | (a) | 6.0136e-05 | (e) | 2.4054e-05 | (a) | 6.0136e-05 | (e) | 2.4054e-05 | (a) | 6.0136e-05 | (e) | 2.4054e-05 | (a) | 6.0136e-05 | (e) | 2.4054e-05 | (a) | 6.0136e-05 | (e) | 2.0647e-05 | (a) | 5.1616e-05 | (e) | 2.0647e-05 | (a) | 5.1616e-05 | (e) | 0.00011262 | (a) | 0.00028154 | (e) | 0.00011262 | (a) | 0.00028154 | (e) | 1.8806e-05 | (a) | 4.7015e-05 | (e) | 2.4054e-05 | (a) | 6.0136e-05 | (e) | 2.4054e-05 | (a) | 6.0136e-05 | (e) | 2.4054e-05 | (a) | 6.0136e-05 | (e) | 2.4054e-05 | (a) | 6.0136e-05 | (e) | 2.4054e-05 | (a) | 6.0136e-05 | (e) | 2.4054e-05 | (a) | 6.0136e-05 | (e) | 2.4054e-05 | (a) | 6.0136e-05 | (e) | 2.4054e-05 | (a) | 6.0136e-05 | (e)
| Phosphorus and compounds | 504 | 0.008404 |  | 70 | (3) | 95 | (8) | 0.00086561 | (a) | 0.002164 | (e) | 0.00086561 | (a) | 0.002164 | (e) | 0.00086561 | (a) | 0.002164 | (e) | 0.00086561 | (a) | 0.002164 | (e) | 0.00086561 | (a) | 0.002164 | (e) | 0.00086561 | (a) | 0.002164 | (e) | 0.00072274 | (a) | 0.0018069 | (e) | 0.00072274 | (a) | 0.0018069 | (e) | 0.00072274 | (a) | 0.0018069 | (e) | 0.0010085 | (a) | 0.0025212 | (e) | 0.0010085 | (a) | 0.0025212 | (e) | 0.0010085 | (a) | 0.0025212 | (e) | 0.0010085 | (a) | 0.0025212 | (e) | 0.0010085 | (a) | 0.0025212 | (e) | 0.0010085 | (a) | 0.0025212 | (e) | 0.0010085 | (a) | 0.0025212 | (e) | 0.0010085 | (a) | 0.0025212 | (e) | 0.0010085 | (a) | 0.0025212 | (e) | 0.0010085 | (a) | 0.0025212 | (e) | 0.0010085 | (a) | 0.0025212 | (e) | 0.0010085 | (a) | 0.0025212 | (e) | 0.0010085 | (a) | 0.0025212 | (e) | 0.0010085 | (a) | 0.0025212 | (e) | 0.0010085 | (a) | 0.0025212 | (e) | 0.0010085 | (a) | 0.0025212 | (e) | 0.0010085 | (a) | 0.0025212 | (e) | 0.0010085 | (a) | 0.0025212 | (e) | 0.0010085 | (a) | 0.0025212 | (e) | 0.0010085 | (a) | 0.0025212 | (e) | 0.0010085 | (a) | 0.0025212 | (e) | 0.00086561 | (a) | 0.002164 | (e) | 0.00086561 | (a) | 0.002164 | (e) | 0.0051937 | (a) | 0.012984 | (e) | 0.0051937 | (a) | 0.012984 | (e) | 0.00086729 | (a) | 0.0021682 | (e) | 0.0010085 | (a) | 0.0025212 | (e) | 0.0010085 | (a) | 0.0025212 | (e) | 0.0010085 | (a) | 0.0025212 | (e) | 0.0010085 | (a) | 0.0025212 | (e) | 0.0010085 | (a) | 0.0025212 | (e) | 0.0010085 | (a) | 0.0025212 | (e) | 0.0010085 | (a) | 0.0025212 | (e) | 0.0010085 | (a) | 0.0025212 | (e)
| Selenium and Compounds | 7782-49-2 | 0.00037638 |  | 70 | (3) | 70 | (4) | 0.0002326 | (a) | 0.00058151 | (e) | 0.0002326 | (a) | 0.00058151 | (e) | 0.0002326 | (a) | 0.00058151 | (e) | 0.0002326 | (a) | 0.00058151 | (e) | 0.0002326 | (a) | 0.00058151 | (e) | 0.0002326 | (a) | 0.00058151 | (e) | 0.00019421 | (a) | 0.00048553 | (e) | 0.00019421 | (a) | 0.00048553 | (e) | 0.00019421 | (a) | 0.00048553 | (e) | 0.000271 | (a) | 0.00067749 | (e) | 0.000271 | (a) | 0.00067749 | (e) | 0.000271 | (a) | 0.00067749 | (e) | 0.000271 | (a) | 0.00067749 | (e) | 0.000271 | (a) | 0.00067749 | (e) | 0.000271 | (a) | 0.00067749 | (e) | 0.000271 | (a) | 0.00067749 | (e) | 0.000271 | (a) | 0.00067749 | (e) | 0.000271 | (a) | 0.00067749 | (e) | 0.000271 | (a) | 0.00067749 | (e) | 0.000271 | (a) | 0.00067749 | (e) | 0.000271 | (a) | 0.00067749 | (e) | 0.000271 | (a) | 0.00067749 | (e) | 0.000271 | (a) | 0.00067749 | (e) | 0.000271 | (a) | 0.00067749 | (e) | 0.000271 | (a) | 0.00067749 | (e) | 0.000271 | (a) | 0.00067749 | (e) | 0.000271 | (a) | 0.00067749 | (e) | 0.000271 | (a) | 0.00067749 | (e) | 0.000271 | (a) | 0.00067749 | (e) | 0.000271 | (a) | 0.00067749 | (e) | 0.0002326 | (a) | 0.00058151 | (e) | 0.0002326 | (a) | 0.00058151 | (e) | 0.0002326 | (a) | 0.00058151 | (e) | 0.0002326 | (a) | 0.00058151 | (e) | 3.8843e-05 | (a) | 9.7107e-05 | (e) | 0.000271 | (a) | 0.00067749 | (e) | 0.000271 | (a) | 0.00067749 | (e) | 0.000271 | (a) | 0.00067749 | (e) | 0.000271 | (a) | 0.00067749 | (e) | 0.000271 | (a) | 0.00067749 | (e) | 0.000271 | (a) | 0.00067749 | (e) | 0.000271 | (a) | 0.00067749 | (e) | 0.000271 | (a) | 0.00067749 | (e)
| Silver and compounds | 7440-22-4 | 4.8013e-05 |  | 70 | (4) | 70 | (4) | 2.9672e-05 | (a) | 7.418e-05 | (e) | 2.9672e-05 | (a) | 7.418e-05 | (e) | 2.9672e-05 | (a) | 7.418e-05 | (e) | 2.9672e-05 | (a) | 7.418e-05 | (e) | 2.9672e-05 | (a) | 7.418e-05 | (e) | 2.9672e-05 | (a) | 7.418e-05 | (e) | 2.4775e-05 | (a) | 6.1937e-05 | (e) | 2.4775e-05 | (a) | 6.1937e-05 | (e) | 2.4775e-05 | (a) | 6.1937e-05 | (e) | 3.4569e-05 | (a) | 8.6423e-05 | (e) | 3.4569e-05 | (a) | 8.6423e-05 | (e) | 3.4569e-05 | (a) | 8.6423e-05 | (e) | 3.4569e-05 | (a) | 8.6423e-05 | (e) | 3.4569e-05 | (a) | 8.6423e-05 | (e) | 3.4569e-05 | (a) | 8.6423e-05 | (e) | 3.4569e-05 | (a) | 8.6423e-05 | (e) | 3.4569e-05 | (a) | 8.6423e-05 | (e) | 3.4569e-05 | (a) | 8.6423e-05 | (e) | 3.4569e-05 | (a) | 8.6423e-05 | (e) | 3.4569e-05 | (a) | 8.6423e-05 | (e) | 3.4569e-05 | (a) | 8.6423e-05 | (e) | 3.4569e-05 | (a) | 8.6423e-05 | (e) | 3.4569e-05 | (a) | 8.6423e-05 | (e) | 3.4569e-05 | (a) | 8.6423e-05 | (e) | 3.4569e-05 | (a) | 8.6423e-05 | (e) | 3.4569e-05 | (a) | 8.6423e-05 | (e) | 3.4569e-05 | (a) | 8.6423e-05 | (e) | 3.4569e-05 | (a) | 8.6423e-05 | (e) | 3.4569e-05 | (a) | 8.6423e-05 | (e) | 3.4569e-05 | (a) | 8.6423e-05 | (e) | 2.9672e-05 | (a) | 7.418e-05 | (e) | 2.9672e-05 | (a) | 7.418e-05 | (e) | 2.9672e-05 | (a) | 7.418e-05 | (e) | 2.9672e-05 | (a) | 7.418e-05 | (e) | 4.9549e-06 | (a) | 1.2387e-05 | (e) | 3.4569e-05 | (a) | 8.6423e-05 | (e) | 3.4569e-05 | (a) | 8.6423e-05 | (e) | 3.4569e-05 | (a) | 8.6423e-05 | (e) | 3.4569e-05 | (a) | 8.6423e-05 | (e) | 3.4569e-05 | (a) | 8.6423e-05 | (e) | 3.4569e-05 | (a) | 8.6423e-05 | (e) | 3.4569e-05 | (a) | 8.6423e-05 | (e) | 3.4569e-05 | (a) | 8.6423e-05 | (e)
| Thallium and compounds | 7440-28-0 | 0.00024009 |  | 70 | (4) | 70 | (4) | 0.00014838 | (a) | 0.00037094 | (e) | 0.00014838 | (a) | 0.00037094 | (e) | 0.00014838 | (a) | 0.00037094 | (e) | 0.00014838 | (a) | 0.00037094 | (e) | 0.00014838 | (a) | 0.00037094 | (e) | 0.00014838 | (a) | 0.00037094 | (e) | 0.00012389 | (a) | 0.00030972 | (e) | 0.00012389 | (a) | 0.00030972 | (e) | 0.00012389 | (a) | 0.00030972 | (e) | 0.00017287 | (a) | 0.00043217 | (e) | 0.00017287 | (a) | 0.00043217 | (e) | 0.00017287 | (a) | 0.00043217 | (e) | 0.00017287 | (a) | 0.00043217 | (e) | 0.00017287 | (a) | 0.00043217 | (e) | 0.00017287 | (a) | 0.00043217 | (e) | 0.00017287 | (a) | 0.00043217 | (e) | 0.00017287 | (a) | 0.00043217 | (e) | 0.00017287 | (a) | 0.00043217 | (e) | 0.00017287 | (a) | 0.00043217 | (e) | 0.00017287 | (a) | 0.00043217 | (e) | 0.00017287 | (a) | 0.00043217 | (e) | 0.00017287 | (a) | 0.00043217 | (e) | 0.00017287 | (a) | 0.00043217 | (e) | 0.00017287 | (a) | 0.00043217 | (e) | 0.00017287 | (a) | 0.00043217 | (e) | 0.00017287 | (a) | 0.00043217 | (e) | 0.00017287 | (a) | 0.00043217 | (e) | 0.00017287 | (a) | 0.00043217 | (e) | 0.00017287 | (a) | 0.00043217 | (e) | 0.00017287 | (a) | 0.00043217 | (e) | 0.00014838 | (a) | 0.00037094 | (e) | 0.00014838 | (a) | 0.00037094 | (e) | 0.00014838 | (a) | 0.00037094 | (e) | 0.00014838 | (a) | 0.00037094 | (e) | 2.4778e-05 | (a) | 6.1944e-05 | (e) | 0.00017287 | (a) | 0.00043217 | (e) | 0.00017287 | (a) | 0.00043217 | (e) | 0.00017287 | (a) | 0.00043217 | (e) | 0.00017287 | (a) | 0.00043217 | (e) | 0.00017287 | (a) | 0.00043217 | (e) | 0.00017287 | (a) | 0.00043217 | (e) | 0.00017287 | (a) | 0.00043217 | (e) | 0.00017287 | (a) | 0.00043217 | (e)
| Zinc and compounds | 7440-66-6 | 0.0052262 |  | 70 | (4) | 70 | (4) | 0.0032298 | (a) | 0.0080744 | (e) | 0.0032298 | (a) | 0.0080744 | (e) | 0.0032298 | (a) | 0.0080744 | (e) | 0.0032298 | (a) | 0.0080744 | (e) | 0.0032298 | (a) | 0.0080744 | (e) | 0.0032298 | (a) | 0.0080744 | (e) | 0.0026967 | (a) | 0.0067418 | (e) | 0.0026967 | (a) | 0.0067418 | (e) | 0.0026967 | (a) | 0.0067418 | (e) | 0.0037628 | (a) | 0.0094071 | (e) | 0.0037628 | (a) | 0.0094071 | (e) | 0.0037628 | (a) | 0.0094071 | (e) | 0.0037628 | (a) | 0.0094071 | (e) | 0.0037628 | (a) | 0.0094071 | (e) | 0.0037628 | (a) | 0.0094071 | (e) | 0.0037628 | (a) | 0.0094071 | (e) | 0.0037628 | (a) | 0.0094071 | (e) | 0.0037628 | (a) | 0.0094071 | (e) | 0.0037628 | (a) | 0.0094071 | (e) | 0.0037628 | (a) | 0.0094071 | (e) | 0.0037628 | (a) | 0.0094071 | (e) | 0.0037628 | (a) | 0.0094071 | (e) | 0.0037628 | (a) | 0.0094071 | (e) | 0.0037628 | (a) | 0.0094071 | (e) | 0.0037628 | (a) | 0.0094071 | (e) | 0.0037628 | (a) | 0.0094071 | (e) | 0.0037628 | (a) | 0.0094071 | (e) | 0.0037628 | (a) | 0.0094071 | (e) | 0.0037628 | (a) | 0.0094071 | (e) | 0.0037628 | (a) | 0.0094071 | (e) | 0.0032298 | (a) | 0.0080744 | (e) | 0.0032298 | (a) | 0.0080744 | (e) | 0.0032298 | (a) | 0.0080744 | (e) | 0.0032298 | (a) | 0.0080744 | (e) | 0.00053934 | (a) | 0.0013484 | (e) | 0.0037628 | (a) | 0.0094071 | (e) | 0.0037628 | (a) | 0.0094071 | (e) | 0.0037628 | (a) | 0.0094071 | (e) | 0.0037628 | (a) | 0.0094071 | (e) | 0.0037628 | (a) | 0.0094071 | (e) | 0.0037628 | (a) | 0.0094071 | (e) | 0.0037628 | (a) | 0.0094071 | (e) | 0.0037628 | (a) | 0.0094071 | (e)
ORGANIC COMPOUNDS
| 1,3-Butadiene | 106-99-0 | 0.2174 |  | 68 | (3) | 70 | (9) | 0.13509 | (b) | 0.34475 | (f) | 0.13509 | (b) | 0.34475 | (f) | 0.13509 | (b) | 0.34475 | (f) | 0.13509 | (b) | 0.34475 | (f) | 0.13509 | (b) | 0.34475 | (f) | 0.13509 | (b) | 0.34475 | (f) | 0.1128 | (b) | 0.28785 | (f) | 0.1128 | (b) | 0.28785 | (f) | 0.1128 | (b) | 0.28785 | (f) | 0.15739 | (b) | 0.40165 | (f) | 0.15739 | (b) | 0.40165 | (f) | 0.15739 | (b) | 0.40165 | (f) | 0.15739 | (b) | 0.40165 | (f) | 0.15739 | (b) | 0.40165 | (f) | 0.15739 | (b) | 0.40165 | (f) | 0.15739 | (b) | 0.40165 | (f) | 0.15739 | (b) | 0.40165 | (f) | 0.15739 | (b) | 0.40165 | (f) | 0.15739 | (b) | 0.40165 | (f) | 0.15739 | (b) | 0.40165 | (f) | 0.15739 | (b) | 0.40165 | (f) | 0.15739 | (b) | 0.40165 | (f) | 0.15739 | (b) | 0.40165 | (f) | 0.15739 | (b) | 0.40165 | (f) | 0.15739 | (b) | 0.40165 | (f) | 0.15739 | (b) | 0.40165 | (f) | 0.15739 | (b) | 0.40165 | (f) | 0.15739 | (b) | 0.40165 | (f) | 0.15739 | (b) | 0.40165 | (f) | 0.15739 | (b) | 0.40165 | (f) | 0.13509 | (b) | 0.34475 | (f) | 0.13509 | (b) | 0.34475 | (f) | 0.1441 | (b) | 0.36773 | (f) | 0.1441 | (b) | 0.36773 | (f) | 0.024063 | (b) | 0.061408 | (f) | 0.15739 | (b) | 0.40165 | (f) | 0.15739 | (b) | 0.40165 | (f) | 0.15739 | (b) | 0.40165 | (f) | 0.15739 | (b) | 0.40165 | (f) | 0.15739 | (b) | 0.40165 | (f) | 0.15739 | (b) | 0.40165 | (f) | 0.15739 | (b) | 0.40165 | (f) | 0.15739 | (b) | 0.40165 | (f)
| 2-Methyl naphthalene | 91-57-6 | 0.012298 |  | 63 | (3) | 65 | (8) | 0.0089156 | (b) | 0.022752 | (f) | 0.0089156 | (b) | 0.022752 | (f) | 0.0089156 | (b) | 0.022752 | (f) | 0.0089156 | (b) | 0.022752 | (f) | 0.0089156 | (b) | 0.022752 | (f) | 0.0089156 | (b) | 0.022752 | (f) | 0.0074441 | (b) | 0.018997 | (f) | 0.0074441 | (b) | 0.018997 | (f) | 0.0074441 | (b) | 0.018997 | (f) | 0.010387 | (b) | 0.026507 | (f) | 0.010387 | (b) | 0.026507 | (f) | 0.010387 | (b) | 0.026507 | (f) | 0.010387 | (b) | 0.026507 | (f) | 0.010387 | (b) | 0.026507 | (f) | 0.010387 | (b) | 0.026507 | (f) | 0.010387 | (b) | 0.026507 | (f) | 0.010387 | (b) | 0.026507 | (f) | 0.010387 | (b) | 0.026507 | (f) | 0.010387 | (b) | 0.026507 | (f) | 0.010387 | (b) | 0.026507 | (f) | 0.010387 | (b) | 0.026507 | (f) | 0.010387 | (b) | 0.026507 | (f) | 0.010387 | (b) | 0.026507 | (f) | 0.010387 | (b) | 0.026507 | (f) | 0.010387 | (b) | 0.026507 | (f) | 0.010387 | (b) | 0.026507 | (f) | 0.010387 | (b) | 0.026507 | (f) | 0.010387 | (b) | 0.026507 | (f) | 0.010387 | (b) | 0.026507 | (f) | 0.010387 | (b) | 0.026507 | (f) | 0.0089156 | (b) | 0.022752 | (f) | 0.0089156 | (b) | 0.022752 | (f) | 0.009425 | (b) | 0.024052 | (f) | 0.009425 | (b) | 0.024052 | (f) | 0.0015739 | (b) | 0.0040165 | (f) | 0.010387 | (b) | 0.026507 | (f) | 0.010387 | (b) | 0.026507 | (f) | 0.010387 | (b) | 0.026507 | (f) | 0.010387 | (b) | 0.026507 | (f) | 0.010387 | (b) | 0.026507 | (f) | 0.010387 | (b) | 0.026507 | (f) | 0.010387 | (b) | 0.026507 | (f) | 0.010387 | (b) | 0.026507 | (f)
| Acenaphthene | 83-32-9 | 0.00073461 |  | 63 | (3) | 66 | (8) | 0.00051735 | (b) | 0.0013203 | (f) | 0.00051735 | (b) | 0.0013203 | (f) | 0.00051735 | (b) | 0.0013203 | (f) | 0.00051735 | (b) | 0.0013203 | (f) | 0.00051735 | (b) | 0.0013203 | (f) | 0.00051735 | (b) | 0.0013203 | (f) | 0.00043197 | (b) | 0.0011024 | (f) | 0.00043197 | (b) | 0.0011024 | (f) | 0.00043197 | (b) | 0.0011024 | (f) | 0.00060274 | (b) | 0.0015382 | (f) | 0.00060274 | (b) | 0.0015382 | (f) | 0.00060274 | (b) | 0.0015382 | (f) | 0.00060274 | (b) | 0.0015382 | (f) | 0.00060274 | (b) | 0.0015382 | (f) | 0.00060274 | (b) | 0.0015382 | (f) | 0.00060274 | (b) | 0.0015382 | (f) | 0.00060274 | (b) | 0.0015382 | (f) | 0.00060274 | (b) | 0.0015382 | (f) | 0.00060274 | (b) | 0.0015382 | (f) | 0.00060274 | (b) | 0.0015382 | (f) | 0.00060274 | (b) | 0.0015382 | (f) | 0.00060274 | (b) | 0.0015382 | (f) | 0.00060274 | (b) | 0.0015382 | (f) | 0.00060274 | (b) | 0.0015382 | (f) | 0.00060274 | (b) | 0.0015382 | (f) | 0.00060274 | (b) | 0.0015382 | (f) | 0.00060274 | (b) | 0.0015382 | (f) | 0.00060274 | (b) | 0.0015382 | (f) | 0.00060274 | (b) | 0.0015382 | (f) | 0.00060274 | (b) | 0.0015382 | (f) | 0.00051735 | (b) | 0.0013203 | (f) | 0.00051735 | (b) | 0.0013203 | (f) | 0.000563 | (b) | 0.0014368 | (f) | 0.000563 | (b) | 0.0014368 | (f) | 9.4016e-05 | (b) | 0.00023993 | (f) | 0.00060274 | (b) | 0.0015382 | (f) | 0.00060274 | (b) | 0.0015382 | (f) | 0.00060274 | (b) | 0.0015382 | (f) | 0.00060274 | (b) | 0.0015382 | (f) | 0.00060274 | (b) | 0.0015382 | (f) | 0.00060274 | (b) | 0.0015382 | (f) | 0.00060274 | (b) | 0.0015382 | (f) | 0.00060274 | (b) | 0.0015382 | (f)
| Acenaphthylene | 208-96-8 | 0.00080982 |  | 63 | (3) | 63 | (8) | 0.00062064 | (b) | 0.0015838 | (f) | 0.00062064 | (b) | 0.0015838 | (f) | 0.00062064 | (b) | 0.0015838 | (f) | 0.00062064 | (b) | 0.0015838 | (f) | 0.00062064 | (b) | 0.0015838 | (f) | 0.00062064 | (b) | 0.0015838 | (f) | 0.0005182 | (b) | 0.0013224 | (f) | 0.0005182 | (b) | 0.0013224 | (f) | 0.0005182 | (b) | 0.0013224 | (f) | 0.00072307 | (b) | 0.0018453 | (f) | 0.00072307 | (b) | 0.0018453 | (f) | 0.00072307 | (b) | 0.0018453 | (f) | 0.00072307 | (b) | 0.0018453 | (f) | 0.00072307 | (b) | 0.0018453 | (f) | 0.00072307 | (b) | 0.0018453 | (f) | 0.00072307 | (b) | 0.0018453 | (f) | 0.00072307 | (b) | 0.0018453 | (f) | 0.00072307 | (b) | 0.0018453 | (f) | 0.00072307 | (b) | 0.0018453 | (f) | 0.00072307 | (b) | 0.0018453 | (f) | 0.00072307 | (b) | 0.0018453 | (f) | 0.00072307 | (b) | 0.0018453 | (f) | 0.00072307 | (b) | 0.0018453 | (f) | 0.00072307 | (b) | 0.0018453 | (f) | 0.00072307 | (b) | 0.0018453 | (f) | 0.00072307 | (b) | 0.0018453 | (f) | 0.00072307 | (b) | 0.0018453 | (f) | 0.00072307 | (b) | 0.0018453 | (f) | 0.00072307 | (b) | 0.0018453 | (f) | 0.00072307 | (b) | 0.0018453 | (f) | 0.00062064 | (b) | 0.0015838 | (f) | 0.00062064 | (b) | 0.0015838 | (f) | 0.00062064 | (b) | 0.0015838 | (f) | 0.00062064 | (b) | 0.0015838 | (f) | 0.00010364 | (b) | 0.00026449 | (f) | 0.00072307 | (b) | 0.0018453 | (f) | 0.00072307 | (b) | 0.0018453 | (f) | 0.00072307 | (b) | 0.0018453 | (f) | 0.00072307 | (b) | 0.0018453 | (f) | 0.00072307 | (b) | 0.0018453 | (f) | 0.00072307 | (b) | 0.0018453 | (f) | 0.00072307 | (b) | 0.0018453 | (f) | 0.00072307 | (b) | 0.0018453 | (f)
| Acetaldehyde | 75-07-0 | 0.7833 |  | 59 | (3) | 63 | (8) | 0.60031 | (b) | 1.532 | (f) | 0.60031 | (b) | 1.532 | (f) | 0.60031 | (b) | 1.532 | (f) | 0.60031 | (b) | 1.532 | (f) | 0.60031 | (b) | 1.532 | (f) | 0.60031 | (b) | 1.532 | (f) | 0.50123 | (b) | 1.2791 | (f) | 0.50123 | (b) | 1.2791 | (f) | 0.50123 | (b) | 1.2791 | (f) | 0.6994 | (b) | 1.7848 | (f) | 0.6994 | (b) | 1.7848 | (f) | 0.6994 | (b) | 1.7848 | (f) | 0.6994 | (b) | 1.7848 | (f) | 0.6994 | (b) | 1.7848 | (f) | 0.6994 | (b) | 1.7848 | (f) | 0.6994 | (b) | 1.7848 | (f) | 0.6994 | (b) | 1.7848 | (f) | 0.6994 | (b) | 1.7848 | (f) | 0.6994 | (b) | 1.7848 | (f) | 0.6994 | (b) | 1.7848 | (f) | 0.6994 | (b) | 1.7848 | (f) | 0.6994 | (b) | 1.7848 | (f) | 0.6994 | (b) | 1.7848 | (f) | 0.6994 | (b) | 1.7848 | (f) | 0.6994 | (b) | 1.7848 | (f) | 0.6994 | (b) | 1.7848 | (f) | 0.6994 | (b) | 1.7848 | (f) | 0.6994 | (b) | 1.7848 | (f) | 0.6994 | (b) | 1.7848 | (f) | 0.6994 | (b) | 1.7848 | (f) | 0.60031 | (b) | 1.532 | (f) | 0.60031 | (b) | 1.532 | (f) | 0.66521 | (b) | 1.6976 | (f) | 0.66521 | (b) | 1.6976 | (f) | 0.11108 | (b) | 0.28348 | (f) | 0.6994 | (b) | 1.7848 | (f) | 0.6994 | (b) | 1.7848 | (f) | 0.6994 | (b) | 1.7848 | (f) | 0.6994 | (b) | 1.7848 | (f) | 0.6994 | (b) | 1.7848 | (f) | 0.6994 | (b) | 1.7848 | (f) | 0.6994 | (b) | 1.7848 | (f) | 0.6994 | (b) | 1.7848 | (f)
| Acrolein | 107-02-8 | 0.0339 |  | 66 | (3) | 70 | (8) | 0.021065 | (b) | 0.053758 | (f) | 0.021065 | (b) | 0.053758 | (f) | 0.021065 | (b) | 0.053758 | (f) | 0.021065 | (b) | 0.053758 | (f) | 0.021065 | (b) | 0.053758 | (f) | 0.021065 | (b) | 0.053758 | (f) | 0.017589 | (b) | 0.044885 | (f) | 0.017589 | (b) | 0.044885 | (f) | 0.017589 | (b) | 0.044885 | (f) | 0.024542 | (b) | 0.062631 | (f) | 0.024542 | (b) | 0.062631 | (f) | 0.024542 | (b) | 0.062631 | (f) | 0.024542 | (b) | 0.062631 | (f) | 0.024542 | (b) | 0.062631 | (f) | 0.024542 | (b) | 0.062631 | (f) | 0.024542 | (b) | 0.062631 | (f) | 0.024542 | (b) | 0.062631 | (f) | 0.024542 | (b) | 0.062631 | (f) | 0.024542 | (b) | 0.062631 | (f) | 0.024542 | (b) | 0.062631 | (f) | 0.024542 | (b) | 0.062631 | (f) | 0.024542 | (b) | 0.062631 | (f) | 0.024542 | (b) | 0.062631 | (f) | 0.024542 | (b) | 0.062631 | (f) | 0.024542 | (b) | 0.062631 | (f) | 0.024542 | (b) | 0.062631 | (f) | 0.024542 | (b) | 0.062631 | (f) | 0.024542 | (b) | 0.062631 | (f) | 0.024542 | (b) | 0.062631 | (f) | 0.024542 | (b) | 0.062631 | (f) | 0.021065 | (b) | 0.053758 | (f) | 0.021065 | (b) | 0.053758 | (f) | 0.023874 | (b) | 0.060926 | (f) | 0.023874 | (b) | 0.060926 | (f) | 0.0039868 | (b) | 0.010174 | (f) | 0.024542 | (b) | 0.062631 | (f) | 0.024542 | (b) | 0.062631 | (f) | 0.024542 | (b) | 0.062631 | (f) | 0.024542 | (b) | 0.062631 | (f) | 0.024542 | (b) | 0.062631 | (f) | 0.024542 | (b) | 0.062631 | (f) | 0.024542 | (b) | 0.062631 | (f) | 0.024542 | (b) | 0.062631 | (f)
| Anthracene | 120-12-7 | 0.00045209 |  | 63 | (3) | 55 | (8) | 0.00042139 | (b) | 0.0010754 | (f) | 0.00042139 | (b) | 0.0010754 | (f) | 0.00042139 | (b) | 0.0010754 | (f) | 0.00042139 | (b) | 0.0010754 | (f) | 0.00042139 | (b) | 0.0010754 | (f) | 0.00042139 | (b) | 0.0010754 | (f) | 0.00035184 | (b) | 0.00089789 | (f) | 0.00035184 | (b) | 0.00089789 | (f) | 0.00035184 | (b) | 0.00089789 | (f) | 0.00049094 | (b) | 0.0012529 | (f) | 0.00049094 | (b) | 0.0012529 | (f) | 0.00049094 | (b) | 0.0012529 | (f) | 0.00049094 | (b) | 0.0012529 | (f) | 0.00049094 | (b) | 0.0012529 | (f) | 0.00049094 | (b) | 0.0012529 | (f) | 0.00049094 | (b) | 0.0012529 | (f) | 0.00049094 | (b) | 0.0012529 | (f) | 0.00049094 | (b) | 0.0012529 | (f) | 0.00049094 | (b) | 0.0012529 | (f) | 0.00049094 | (b) | 0.0012529 | (f) | 0.00049094 | (b) | 0.0012529 | (f) | 0.00049094 | (b) | 0.0012529 | (f) | 0.00049094 | (b) | 0.0012529 | (f) | 0.00049094 | (b) | 0.0012529 | (f) | 0.00049094 | (b) | 0.0012529 | (f) | 0.00049094 | (b) | 0.0012529 | (f) | 0.00049094 | (b) | 0.0012529 | (f) | 0.00049094 | (b) | 0.0012529 | (f) | 0.00049094 | (b) | 0.0012529 | (f) | 0.00049094 | (b) | 0.0012529 | (f) | 0.00042139 | (b) | 0.0010754 | (f) | 0.00042139 | (b) | 0.0010754 | (f) | 0.00034648 | (b) | 0.0008842 | (f) | 0.00034648 | (b) | 0.0008842 | (f) | 5.7858e-05 | (b) | 0.00014765 | (f) | 0.00049094 | (b) | 0.0012529 | (f) | 0.00049094 | (b) | 0.0012529 | (f) | 0.00049094 | (b) | 0.0012529 | (f) | 0.00049094 | (b) | 0.0012529 | (f) | 0.00049094 | (b) | 0.0012529 | (f) | 0.00049094 | (b) | 0.0012529 | (f) | 0.00049094 | (b) | 0.0012529 | (f) | 0.00049094 | (b) | 0.0012529 | (f)
| Benzene | 71-43-2 | 0.1863 |  | 63 | (3) | 65 | (8) | 0.13506 | (b) | 0.34467 | (f) | 0.13506 | (b) | 0.34467 | (f) | 0.13506 | (b) | 0.34467 | (f) | 0.13506 | (b) | 0.34467 | (f) | 0.13506 | (b) | 0.34467 | (f) | 0.13506 | (b) | 0.34467 | (f) | 0.11277 | (b) | 0.28778 | (f) | 0.11277 | (b) | 0.28778 | (f) | 0.11277 | (b) | 0.28778 | (f) | 0.15735 | (b) | 0.40156 | (f) | 0.15735 | (b) | 0.40156 | (f) | 0.15735 | (b) | 0.40156 | (f) | 0.15735 | (b) | 0.40156 | (f) | 0.15735 | (b) | 0.40156 | (f) | 0.15735 | (b) | 0.40156 | (f) | 0.15735 | (b) | 0.40156 | (f) | 0.15735 | (b) | 0.40156 | (f) | 0.15735 | (b) | 0.40156 | (f) | 0.15735 | (b) | 0.40156 | (f) | 0.15735 | (b) | 0.40156 | (f) | 0.15735 | (b) | 0.40156 | (f) | 0.15735 | (b) | 0.40156 | (f) | 0.15735 | (b) | 0.40156 | (f) | 0.15735 | (b) | 0.40156 | (f) | 0.15735 | (b) | 0.40156 | (f) | 0.15735 | (b) | 0.40156 | (f) | 0.15735 | (b) | 0.40156 | (f) | 0.15735 | (b) | 0.40156 | (f) | 0.15735 | (b) | 0.40156 | (f) | 0.15735 | (b) | 0.40156 | (f) | 0.13506 | (b) | 0.34467 | (f) | 0.13506 | (b) | 0.34467 | (f) | 0.14278 | (b) | 0.36437 | (f) | 0.14278 | (b) | 0.36437 | (f) | 0.023843 | (b) | 0.060846 | (f) | 0.15735 | (b) | 0.40156 | (f) | 0.15735 | (b) | 0.40156 | (f) | 0.15735 | (b) | 0.40156 | (f) | 0.15735 | (b) | 0.40156 | (f) | 0.15735 | (b) | 0.40156 | (f) | 0.15735 | (b) | 0.40156 | (f) | 0.15735 | (b) | 0.40156 | (f) | 0.15735 | (b) | 0.40156 | (f)
| Chlorobenzene | 108-90-7 | 0.0002 |  | 63 | (9) | 63 | (9) | 0.00015328 | (b) | 0.00039116 | (f) | 0.00015328 | (b) | 0.00039116 | (f) | 0.00015328 | (b) | 0.00039116 | (f) | 0.00015328 | (b) | 0.00039116 | (f) | 0.00015328 | (b) | 0.00039116 | (f) | 0.00015328 | (b) | 0.00039116 | (f) | 0.00012798 | (b) | 0.0003266 | (f) | 0.00012798 | (b) | 0.0003266 | (f) | 0.00012798 | (b) | 0.0003266 | (f) | 0.00017858 | (b) | 0.00045572 | (f) | 0.00017858 | (b) | 0.00045572 | (f) | 0.00017858 | (b) | 0.00045572 | (f) | 0.00017858 | (b) | 0.00045572 | (f) | 0.00017858 | (b) | 0.00045572 | (f) | 0.00017858 | (b) | 0.00045572 | (f) | 0.00017858 | (b) | 0.00045572 | (f) | 0.00017858 | (b) | 0.00045572 | (f) | 0.00017858 | (b) | 0.00045572 | (f) | 0.00017858 | (b) | 0.00045572 | (f) | 0.00017858 | (b) | 0.00045572 | (f) | 0.00017858 | (b) | 0.00045572 | (f) | 0.00017858 | (b) | 0.00045572 | (f) | 0.00017858 | (b) | 0.00045572 | (f) | 0.00017858 | (b) | 0.00045572 | (f) | 0.00017858 | (b) | 0.00045572 | (f) | 0.00017858 | (b) | 0.00045572 | (f) | 0.00017858 | (b) | 0.00045572 | (f) | 0.00017858 | (b) | 0.00045572 | (f) | 0.00017858 | (b) | 0.00045572 | (f) | 0.00017858 | (b) | 0.00045572 | (f) | 0.00015328 | (b) | 0.00039116 | (f) | 0.00015328 | (b) | 0.00039116 | (f) | 0.00015328 | (b) | 0.00039116 | (f) | 0.00015328 | (b) | 0.00039116 | (f) | 2.5596e-05 | (b) | 6.532e-05 | (f) | 0.00017858 | (b) | 0.00045572 | (f) | 0.00017858 | (b) | 0.00045572 | (f) | 0.00017858 | (b) | 0.00045572 | (f) | 0.00017858 | (b) | 0.00045572 | (f) | 0.00017858 | (b) | 0.00045572 | (f) | 0.00017858 | (b) | 0.00045572 | (f) | 0.00017858 | (b) | 0.00045572 | (f) | 0.00017858 | (b) | 0.00045572 | (f)
| Ethylbenzene | 100-41-4 | 0.0109 |  | 63 | (3) | 67 | (8) | 0.0074506 | (b) | 0.019014 | (f) | 0.0074506 | (b) | 0.019014 | (f) | 0.0074506 | (b) | 0.019014 | (f) | 0.0074506 | (b) | 0.019014 | (f) | 0.0074506 | (b) | 0.019014 | (f) | 0.0074506 | (b) | 0.019014 | (f) | 0.0062209 | (b) | 0.015875 | (f) | 0.0062209 | (b) | 0.015875 | (f) | 0.0062209 | (b) | 0.015875 | (f) | 0.0086803 | (b) | 0.022152 | (f) | 0.0086803 | (b) | 0.022152 | (f) | 0.0086803 | (b) | 0.022152 | (f) | 0.0086803 | (b) | 0.022152 | (f) | 0.0086803 | (b) | 0.022152 | (f) | 0.0086803 | (b) | 0.022152 | (f) | 0.0086803 | (b) | 0.022152 | (f) | 0.0086803 | (b) | 0.022152 | (f) | 0.0086803 | (b) | 0.022152 | (f) | 0.0086803 | (b) | 0.022152 | (f) | 0.0086803 | (b) | 0.022152 | (f) | 0.0086803 | (b) | 0.022152 | (f) | 0.0086803 | (b) | 0.022152 | (f) | 0.0086803 | (b) | 0.022152 | (f) | 0.0086803 | (b) | 0.022152 | (f) | 0.0086803 | (b) | 0.022152 | (f) | 0.0086803 | (b) | 0.022152 | (f) | 0.0086803 | (b) | 0.022152 | (f) | 0.0086803 | (b) | 0.022152 | (f) | 0.0086803 | (b) | 0.022152 | (f) | 0.0086803 | (b) | 0.022152 | (f) | 0.0074506 | (b) | 0.019014 | (f) | 0.0074506 | (b) | 0.019014 | (f) | 0.0083537 | (b) | 0.021318 | (f) | 0.0083537 | (b) | 0.021318 | (f) | 0.001395 | (b) | 0.0035599 | (f) | 0.0086803 | (b) | 0.022152 | (f) | 0.0086803 | (b) | 0.022152 | (f) | 0.0086803 | (b) | 0.022152 | (f) | 0.0086803 | (b) | 0.022152 | (f) | 0.0086803 | (b) | 0.022152 | (f) | 0.0086803 | (b) | 0.022152 | (f) | 0.0086803 | (b) | 0.022152 | (f) | 0.0086803 | (b) | 0.022152 | (f)
| Formaldehyde | 50-00-0 | 2.7131 |  | 59 | (3) | 65 | (8) | 1.9685 | (b) | 5.039 | (f) | 1.9685 | (b) | 5.039 | (f) | 1.9685 | (b) | 5.039 | (f) | 1.9685 | (b) | 5.039 | (f) | 1.9685 | (b) | 5.039 | (f) | 1.9685 | (b) | 5.039 | (f) | 1.6436 | (b) | 4.2073 | (f) | 1.6436 | (b) | 4.2073 | (f) | 1.6436 | (b) | 4.2073 | (f) | 2.2934 | (b) | 5.8706 | (f) | 2.2934 | (b) | 5.8706 | (f) | 2.2934 | (b) | 5.8706 | (f) | 2.2934 | (b) | 5.8706 | (f) | 2.2934 | (b) | 5.8706 | (f) | 2.2934 | (b) | 5.8706 | (f) | 2.2934 | (b) | 5.8706 | (f) | 2.2934 | (b) | 5.8706 | (f) | 2.2934 | (b) | 5.8706 | (f) | 2.2934 | (b) | 5.8706 | (f) | 2.2934 | (b) | 5.8706 | (f) | 2.2934 | (b) | 5.8706 | (f) | 2.2934 | (b) | 5.8706 | (f) | 2.2934 | (b) | 5.8706 | (f) | 2.2934 | (b) | 5.8706 | (f) | 2.2934 | (b) | 5.8706 | (f) | 2.2934 | (b) | 5.8706 | (f) | 2.2934 | (b) | 5.8706 | (f) | 2.2934 | (b) | 5.8706 | (f) | 2.2934 | (b) | 5.8706 | (f) | 2.2934 | (b) | 5.8706 | (f) | 1.9685 | (b) | 5.039 | (f) | 1.9685 | (b) | 5.039 | (f) | 2.306 | (b) | 5.9028 | (f) | 2.306 | (b) | 5.9028 | (f) | 0.38507 | (b) | 0.98571 | (f) | 2.2934 | (b) | 5.8706 | (f) | 2.2934 | (b) | 5.8706 | (f) | 2.2934 | (b) | 5.8706 | (f) | 2.2934 | (b) | 5.8706 | (f) | 2.2934 | (b) | 5.8706 | (f) | 2.2934 | (b) | 5.8706 | (f) | 2.2934 | (b) | 5.8706 | (f) | 2.2934 | (b) | 5.8706 | (f)
| Hexane | 110-54-3 | 0.0269 |  | 55 | (3) | 60 | (8) | 0.022288 | (b) | 0.056877 | (f) | 0.022288 | (b) | 0.056877 | (f) | 0.022288 | (b) | 0.056877 | (f) | 0.022288 | (b) | 0.056877 | (f) | 0.022288 | (b) | 0.056877 | (f) | 0.022288 | (b) | 0.056877 | (f) | 0.018609 | (b) | 0.047489 | (f) | 0.018609 | (b) | 0.047489 | (f) | 0.018609 | (b) | 0.047489 | (f) | 0.025966 | (b) | 0.066264 | (f) | 0.025966 | (b) | 0.066264 | (f) | 0.025966 | (b) | 0.066264 | (f) | 0.025966 | (b) | 0.066264 | (f) | 0.025966 | (b) | 0.066264 | (f) | 0.025966 | (b) | 0.066264 | (f) | 0.025966 | (b) | 0.066264 | (f) | 0.025966 | (b) | 0.066264 | (f) | 0.025966 | (b) | 0.066264 | (f) | 0.025966 | (b) | 0.066264 | (f) | 0.025966 | (b) | 0.066264 | (f) | 0.025966 | (b) | 0.066264 | (f) | 0.025966 | (b) | 0.066264 | (f) | 0.025966 | (b) | 0.066264 | (f) | 0.025966 | (b) | 0.066264 | (f) | 0.025966 | (b) | 0.066264 | (f) | 0.025966 | (b) | 0.066264 | (f) | 0.025966 | (b) | 0.066264 | (f) | 0.025966 | (b) | 0.066264 | (f) | 0.025966 | (b) | 0.066264 | (f) | 0.025966 | (b) | 0.066264 | (f) | 0.022288 | (b) | 0.056877 | (f) | 0.022288 | (b) | 0.056877 | (f) | 0.025073 | (b) | 0.063987 | (f) | 0.025073 | (b) | 0.063987 | (f) | 0.004187 | (b) | 0.010685 | (f) | 0.025966 | (b) | 0.066264 | (f) | 0.025966 | (b) | 0.066264 | (f) | 0.025966 | (b) | 0.066264 | (f) | 0.025966 | (b) | 0.066264 | (f) | 0.025966 | (b) | 0.066264 | (f) | 0.025966 | (b) | 0.066264 | (f) | 0.025966 | (b) | 0.066264 | (f) | 0.025966 | (b) | 0.066264 | (f)
| Propylene | 115-07-1 | 0.47 |  | 63 | (9) | 63 | (9) | 0.3602 | (b) | 0.91923 | (f) | 0.3602 | (b) | 0.91923 | (f) | 0.3602 | (b) | 0.91923 | (f) | 0.3602 | (b) | 0.91923 | (f) | 0.3602 | (b) | 0.91923 | (f) | 0.3602 | (b) | 0.91923 | (f) | 0.30075 | (b) | 0.76751 | (f) | 0.30075 | (b) | 0.76751 | (f) | 0.30075 | (b) | 0.76751 | (f) | 0.41966 | (b) | 1.0709 | (f) | 0.41966 | (b) | 1.0709 | (f) | 0.41966 | (b) | 1.0709 | (f) | 0.41966 | (b) | 1.0709 | (f) | 0.41966 | (b) | 1.0709 | (f) | 0.41966 | (b) | 1.0709 | (f) | 0.41966 | (b) | 1.0709 | (f) | 0.41966 | (b) | 1.0709 | (f) | 0.41966 | (b) | 1.0709 | (f) | 0.41966 | (b) | 1.0709 | (f) | 0.41966 | (b) | 1.0709 | (f) | 0.41966 | (b) | 1.0709 | (f) | 0.41966 | (b) | 1.0709 | (f) | 0.41966 | (b) | 1.0709 | (f) | 0.41966 | (b) | 1.0709 | (f) | 0.41966 | (b) | 1.0709 | (f) | 0.41966 | (b) | 1.0709 | (f) | 0.41966 | (b) | 1.0709 | (f) | 0.41966 | (b) | 1.0709 | (f) | 0.41966 | (b) | 1.0709 | (f) | 0.41966 | (b) | 1.0709 | (f) | 0.3602 | (b) | 0.91923 | (f) | 0.3602 | (b) | 0.91923 | (f) | 0.3602 | (b) | 0.91923 | (f) | 0.3602 | (b) | 0.91923 | (f) | 0.060151 | (b) | 0.1535 | (f) | 0.41966 | (b) | 1.0709 | (f) | 0.41966 | (b) | 1.0709 | (f) | 0.41966 | (b) | 1.0709 | (f) | 0.41966 | (b) | 1.0709 | (f) | 0.41966 | (b) | 1.0709 | (f) | 0.41966 | (b) | 1.0709 | (f) | 0.41966 | (b) | 1.0709 | (f) | 0.41966 | (b) | 1.0709 | (f)
| Toluene | 108-88-3 | 0.1054 |  | 63 | (3) | 73 | (8) | 0.058946 | (b) | 0.15043 | (f) | 0.058946 | (b) | 0.15043 | (f) | 0.058946 | (b) | 0.15043 | (f) | 0.058946 | (b) | 0.15043 | (f) | 0.058946 | (b) | 0.15043 | (f) | 0.058946 | (b) | 0.15043 | (f) | 0.049217 | (b) | 0.1256 | (f) | 0.049217 | (b) | 0.1256 | (f) | 0.049217 | (b) | 0.1256 | (f) | 0.068675 | (b) | 0.17526 | (f) | 0.068675 | (b) | 0.17526 | (f) | 0.068675 | (b) | 0.17526 | (f) | 0.068675 | (b) | 0.17526 | (f) | 0.068675 | (b) | 0.17526 | (f) | 0.068675 | (b) | 0.17526 | (f) | 0.068675 | (b) | 0.17526 | (f) | 0.068675 | (b) | 0.17526 | (f) | 0.068675 | (b) | 0.17526 | (f) | 0.068675 | (b) | 0.17526 | (f) | 0.068675 | (b) | 0.17526 | (f) | 0.068675 | (b) | 0.17526 | (f) | 0.068675 | (b) | 0.17526 | (f) | 0.068675 | (b) | 0.17526 | (f) | 0.068675 | (b) | 0.17526 | (f) | 0.068675 | (b) | 0.17526 | (f) | 0.068675 | (b) | 0.17526 | (f) | 0.068675 | (b) | 0.17526 | (f) | 0.068675 | (b) | 0.17526 | (f) | 0.068675 | (b) | 0.17526 | (f) | 0.068675 | (b) | 0.17526 | (f) | 0.058946 | (b) | 0.15043 | (f) | 0.058946 | (b) | 0.15043 | (f) | 0.080778 | (b) | 0.20614 | (f) | 0.080778 | (b) | 0.20614 | (f) | 0.013489 | (b) | 0.034424 | (f) | 0.068675 | (b) | 0.17526 | (f) | 0.068675 | (b) | 0.17526 | (f) | 0.068675 | (b) | 0.17526 | (f) | 0.068675 | (b) | 0.17526 | (f) | 0.068675 | (b) | 0.17526 | (f) | 0.068675 | (b) | 0.17526 | (f) | 0.068675 | (b) | 0.17526 | (f) | 0.068675 | (b) | 0.17526 | (f)
| Xylene (mixed isomers) | 1330-20-7 | 0.0424 |  | 63 | (3) | 66 | (8) | 0.02986 | (b) | 0.076202 | (f) | 0.02986 | (b) | 0.076202 | (f) | 0.02986 | (b) | 0.076202 | (f) | 0.02986 | (b) | 0.076202 | (f) | 0.02986 | (b) | 0.076202 | (f) | 0.02986 | (b) | 0.076202 | (f) | 0.024932 | (b) | 0.063625 | (f) | 0.024932 | (b) | 0.063625 | (f) | 0.024932 | (b) | 0.063625 | (f) | 0.034789 | (b) | 0.088779 | (f) | 0.034789 | (b) | 0.088779 | (f) | 0.034789 | (b) | 0.088779 | (f) | 0.034789 | (b) | 0.088779 | (f) | 0.034789 | (b) | 0.088779 | (f) | 0.034789 | (b) | 0.088779 | (f) | 0.034789 | (b) | 0.088779 | (f) | 0.034789 | (b) | 0.088779 | (f) | 0.034789 | (b) | 0.088779 | (f) | 0.034789 | (b) | 0.088779 | (f) | 0.034789 | (b) | 0.088779 | (f) | 0.034789 | (b) | 0.088779 | (f) | 0.034789 | (b) | 0.088779 | (f) | 0.034789 | (b) | 0.088779 | (f) | 0.034789 | (b) | 0.088779 | (f) | 0.034789 | (b) | 0.088779 | (f) | 0.034789 | (b) | 0.088779 | (f) | 0.034789 | (b) | 0.088779 | (f) | 0.034789 | (b) | 0.088779 | (f) | 0.034789 | (b) | 0.088779 | (f) | 0.034789 | (b) | 0.088779 | (f) | 0.02986 | (b) | 0.076202 | (f) | 0.02986 | (b) | 0.076202 | (f) | 0.032495 | (b) | 0.082926 | (f) | 0.032495 | (b) | 0.082926 | (f) | 0.0054264 | (b) | 0.013848 | (f) | 0.034789 | (b) | 0.088779 | (f) | 0.034789 | (b) | 0.088779 | (f) | 0.034789 | (b) | 0.088779 | (f) | 0.034789 | (b) | 0.088779 | (f) | 0.034789 | (b) | 0.088779 | (f) | 0.034789 | (b) | 0.088779 | (f) | 0.034789 | (b) | 0.088779 | (f) | 0.034789 | (b) | 0.088779 | (f)
INORGANIC COMPOUNDS
| Ammonia | 7664-41-7 | 0.8 |  | 0 |  | 0 |  | 1.6571 | (b) | 4.2288 | (f) | 1.6571 | (b) | 4.2288 | (f) | 1.6571 | (b) | 4.2288 | (f) | 1.6571 | (b) | 4.2288 | (f) | 1.6571 | (b) | 4.2288 | (f) | 1.6571 | (b) | 4.2288 | (f) | 1.3836 | (b) | 3.5308 | (f) | 1.3836 | (b) | 3.5308 | (f) | 1.3836 | (b) | 3.5308 | (f) | 1.9306 | (b) | 4.9267 | (f) | 1.9306 | (b) | 4.9267 | (f) | 1.9306 | (b) | 4.9267 | (f) | 1.9306 | (b) | 4.9267 | (f) | 1.9306 | (b) | 4.9267 | (f) | 1.9306 | (b) | 4.9267 | (f) | 1.9306 | (b) | 4.9267 | (f) | 1.9306 | (b) | 4.9267 | (f) | 1.9306 | (b) | 4.9267 | (f) | 1.9306 | (b) | 4.9267 | (f) | 1.9306 | (b) | 4.9267 | (f) | 1.9306 | (b) | 4.9267 | (f) | 1.9306 | (b) | 4.9267 | (f) | 1.9306 | (b) | 4.9267 | (f) | 1.9306 | (b) | 4.9267 | (f) | 1.9306 | (b) | 4.9267 | (f) | 1.9306 | (b) | 4.9267 | (f) | 1.9306 | (b) | 4.9267 | (f) | 1.9306 | (b) | 4.9267 | (f) | 1.9306 | (b) | 4.9267 | (f) | 1.9306 | (b) | 4.9267 | (f) | 1.6571 | (b) | 4.2288 | (f) | 1.6571 | (b) | 4.2288 | (f) | 1.6571 | (b) | 4.2288 | (f) | 1.6571 | (b) | 4.2288 | (f) | 0.27671 | (b) | 0.70616 | (f) | 1.9306 | (b) | 4.9267 | (f) | 1.9306 | (b) | 4.9267 | (f) | 1.9306 | (b) | 4.9267 | (f) | 1.9306 | (b) | 4.9267 | (f) | 1.9306 | (b) | 4.9267 | (f) | 1.9306 | (b) | 4.9267 | (f) | 1.9306 | (b) | 4.9267 | (f) | 1.9306 | (b) | 4.9267 | (f)
| Hydrochloric Acid | 7647-01-0 | 0.1863 |  | 70 | (3) | 0 |  | 0.38589 | (b) | 0.98477 | (f) | 0.38589 | (b) | 0.98477 | (f) | 0.38589 | (b) | 0.98477 | (f) | 0.38589 | (b) | 0.98477 | (f) | 0.38589 | (b) | 0.98477 | (f) | 0.38589 | (b) | 0.98477 | (f) | 0.3222 | (b) | 0.82224 | (f) | 0.3222 | (b) | 0.82224 | (f) | 0.3222 | (b) | 0.82224 | (f) | 0.44958 | (b) | 1.1473 | (f) | 0.44958 | (b) | 1.1473 | (f) | 0.44958 | (b) | 1.1473 | (f) | 0.44958 | (b) | 1.1473 | (f) | 0.44958 | (b) | 1.1473 | (f) | 0.44958 | (b) | 1.1473 | (f) | 0.44958 | (b) | 1.1473 | (f) | 0.44958 | (b) | 1.1473 | (f) | 0.44958 | (b) | 1.1473 | (f) | 0.44958 | (b) | 1.1473 | (f) | 0.44958 | (b) | 1.1473 | (f) | 0.44958 | (b) | 1.1473 | (f) | 0.44958 | (b) | 1.1473 | (f) | 0.44958 | (b) | 1.1473 | (f) | 0.44958 | (b) | 1.1473 | (f) | 0.44958 | (b) | 1.1473 | (f) | 0.44958 | (b) | 1.1473 | (f) | 0.44958 | (b) | 1.1473 | (f) | 0.44958 | (b) | 1.1473 | (f) | 0.44958 | (b) | 1.1473 | (f) | 0.44958 | (b) | 1.1473 | (f) | 0.38589 | (b) | 0.98477 | (f) | 0.38589 | (b) | 0.98477 | (f) | 0.11577 | (b) | 0.29543 | (f) | 0.11577 | (b) | 0.29543 | (f) | 0.019332 | (b) | 0.049334 | (f) | 0.44958 | (b) | 1.1473 | (f) | 0.44958 | (b) | 1.1473 | (f) | 0.44958 | (b) | 1.1473 | (f) | 0.44958 | (b) | 1.1473 | (f) | 0.44958 | (b) | 1.1473 | (f) | 0.44958 | (b) | 1.1473 | (f) | 0.44958 | (b) | 1.1473 | (f) | 0.44958 | (b) | 1.1473 | (f)
POLYCYCLIC AROMATIC HYDROCARBONS (PAH)
| Benz[a]anthracene | 56-55-3 | 4.8541e-05 |  | 63 | (3) | 63 | (8) | 3.7202e-05 | (b) | 9.4937e-05 | (f) | 3.7202e-05 | (b) | 9.4937e-05 | (f) | 3.7202e-05 | (b) | 9.4937e-05 | (f) | 3.7202e-05 | (b) | 9.4937e-05 | (f) | 3.7202e-05 | (b) | 9.4937e-05 | (f) | 3.7202e-05 | (b) | 9.4937e-05 | (f) | 3.1062e-05 | (b) | 7.9268e-05 | (f) | 3.1062e-05 | (b) | 7.9268e-05 | (f) | 3.1062e-05 | (b) | 7.9268e-05 | (f) | 4.3342e-05 | (b) | 0.00011061 | (f) | 4.3342e-05 | (b) | 0.00011061 | (f) | 4.3342e-05 | (b) | 0.00011061 | (f) | 4.3342e-05 | (b) | 0.00011061 | (f) | 4.3342e-05 | (b) | 0.00011061 | (f) | 4.3342e-05 | (b) | 0.00011061 | (f) | 4.3342e-05 | (b) | 0.00011061 | (f) | 4.3342e-05 | (b) | 0.00011061 | (f) | 4.3342e-05 | (b) | 0.00011061 | (f) | 4.3342e-05 | (b) | 0.00011061 | (f) | 4.3342e-05 | (b) | 0.00011061 | (f) | 4.3342e-05 | (b) | 0.00011061 | (f) | 4.3342e-05 | (b) | 0.00011061 | (f) | 4.3342e-05 | (b) | 0.00011061 | (f) | 4.3342e-05 | (b) | 0.00011061 | (f) | 4.3342e-05 | (b) | 0.00011061 | (f) | 4.3342e-05 | (b) | 0.00011061 | (f) | 4.3342e-05 | (b) | 0.00011061 | (f) | 4.3342e-05 | (b) | 0.00011061 | (f) | 4.3342e-05 | (b) | 0.00011061 | (f) | 4.3342e-05 | (b) | 0.00011061 | (f) | 3.7202e-05 | (b) | 9.4937e-05 | (f) | 3.7202e-05 | (b) | 9.4937e-05 | (f) | 3.7202e-05 | (b) | 9.4937e-05 | (f) | 3.7202e-05 | (b) | 9.4937e-05 | (f) | 6.2123e-06 | (b) | 1.5854e-05 | (f) | 4.3342e-05 | (b) | 0.00011061 | (f) | 4.3342e-05 | (b) | 0.00011061 | (f) | 4.3342e-05 | (b) | 0.00011061 | (f) | 4.3342e-05 | (b) | 0.00011061 | (f) | 4.3342e-05 | (b) | 0.00011061 | (f) | 4.3342e-05 | (b) | 0.00011061 | (f) | 4.3342e-05 | (b) | 0.00011061 | (f) | 4.3342e-05 | (b) | 0.00011061 | (f)
| Benzo[a]pyrene | 50-32-8 | 1.4385e-05 |  | 63 | (3) | 65 | (8) | 1.0429e-05 | (b) | 2.6614e-05 | (f) | 1.0429e-05 | (b) | 2.6614e-05 | (f) | 1.0429e-05 | (b) | 2.6614e-05 | (f) | 1.0429e-05 | (b) | 2.6614e-05 | (f) | 1.0429e-05 | (b) | 2.6614e-05 | (f) | 1.0429e-05 | (b) | 2.6614e-05 | (f) | 8.7075e-06 | (b) | 2.2221e-05 | (f) | 8.7075e-06 | (b) | 2.2221e-05 | (f) | 8.7075e-06 | (b) | 2.2221e-05 | (f) | 1.215e-05 | (b) | 3.1007e-05 | (f) | 1.215e-05 | (b) | 3.1007e-05 | (f) | 1.215e-05 | (b) | 3.1007e-05 | (f) | 1.215e-05 | (b) | 3.1007e-05 | (f) | 1.215e-05 | (b) | 3.1007e-05 | (f) | 1.215e-05 | (b) | 3.1007e-05 | (f) | 1.215e-05 | (b) | 3.1007e-05 | (f) | 1.215e-05 | (b) | 3.1007e-05 | (f) | 1.215e-05 | (b) | 3.1007e-05 | (f) | 1.215e-05 | (b) | 3.1007e-05 | (f) | 1.215e-05 | (b) | 3.1007e-05 | (f) | 1.215e-05 | (b) | 3.1007e-05 | (f) | 1.215e-05 | (b) | 3.1007e-05 | (f) | 1.215e-05 | (b) | 3.1007e-05 | (f) | 1.215e-05 | (b) | 3.1007e-05 | (f) | 1.215e-05 | (b) | 3.1007e-05 | (f) | 1.215e-05 | (b) | 3.1007e-05 | (f) | 1.215e-05 | (b) | 3.1007e-05 | (f) | 1.215e-05 | (b) | 3.1007e-05 | (f) | 1.215e-05 | (b) | 3.1007e-05 | (f) | 1.215e-05 | (b) | 3.1007e-05 | (f) | 1.0429e-05 | (b) | 2.6614e-05 | (f) | 1.0429e-05 | (b) | 2.6614e-05 | (f) | 1.1025e-05 | (b) | 2.8135e-05 | (f) | 1.1025e-05 | (b) | 2.8135e-05 | (f) | 1.841e-06 | (b) | 4.6982e-06 | (f) | 1.215e-05 | (b) | 3.1007e-05 | (f) | 1.215e-05 | (b) | 3.1007e-05 | (f) | 1.215e-05 | (b) | 3.1007e-05 | (f) | 1.215e-05 | (b) | 3.1007e-05 | (f) | 1.215e-05 | (b) | 3.1007e-05 | (f) | 1.215e-05 | (b) | 3.1007e-05 | (f) | 1.215e-05 | (b) | 3.1007e-05 | (f) | 1.215e-05 | (b) | 3.1007e-05 | (f)
| Benzo[b]fluoranthene | 205-99-2 | 4.4354e-05 |  | 63 | (3) | 63 | (8) | 3.3992e-05 | (b) | 8.6747e-05 | (f) | 3.3992e-05 | (b) | 8.6747e-05 | (f) | 3.3992e-05 | (b) | 8.6747e-05 | (f) | 3.3992e-05 | (b) | 8.6747e-05 | (f) | 3.3992e-05 | (b) | 8.6747e-05 | (f) | 3.3992e-05 | (b) | 8.6747e-05 | (f) | 2.8382e-05 | (b) | 7.2429e-05 | (f) | 2.8382e-05 | (b) | 7.2429e-05 | (f) | 2.8382e-05 | (b) | 7.2429e-05 | (f) | 3.9603e-05 | (b) | 0.00010106 | (f) | 3.9603e-05 | (b) | 0.00010106 | (f) | 3.9603e-05 | (b) | 0.00010106 | (f) | 3.9603e-05 | (b) | 0.00010106 | (f) | 3.9603e-05 | (b) | 0.00010106 | (f) | 3.9603e-05 | (b) | 0.00010106 | (f) | 3.9603e-05 | (b) | 0.00010106 | (f) | 3.9603e-05 | (b) | 0.00010106 | (f) | 3.9603e-05 | (b) | 0.00010106 | (f) | 3.9603e-05 | (b) | 0.00010106 | (f) | 3.9603e-05 | (b) | 0.00010106 | (f) | 3.9603e-05 | (b) | 0.00010106 | (f) | 3.9603e-05 | (b) | 0.00010106 | (f) | 3.9603e-05 | (b) | 0.00010106 | (f) | 3.9603e-05 | (b) | 0.00010106 | (f) | 3.9603e-05 | (b) | 0.00010106 | (f) | 3.9603e-05 | (b) | 0.00010106 | (f) | 3.9603e-05 | (b) | 0.00010106 | (f) | 3.9603e-05 | (b) | 0.00010106 | (f) | 3.9603e-05 | (b) | 0.00010106 | (f) | 3.9603e-05 | (b) | 0.00010106 | (f) | 3.3992e-05 | (b) | 8.6747e-05 | (f) | 3.3992e-05 | (b) | 8.6747e-05 | (f) | 3.3992e-05 | (b) | 8.6747e-05 | (f) | 3.3992e-05 | (b) | 8.6747e-05 | (f) | 5.6764e-06 | (b) | 1.4486e-05 | (f) | 3.9603e-05 | (b) | 0.00010106 | (f) | 3.9603e-05 | (b) | 0.00010106 | (f) | 3.9603e-05 | (b) | 0.00010106 | (f) | 3.9603e-05 | (b) | 0.00010106 | (f) | 3.9603e-05 | (b) | 0.00010106 | (f) | 3.9603e-05 | (b) | 0.00010106 | (f) | 3.9603e-05 | (b) | 0.00010106 | (f) | 3.9603e-05 | (b) | 0.00010106 | (f)
| Benzo[e]pyrene | 192-97-2 | 3.2868e-05 |  | 63 | (3) | 65 | (8) | 2.3828e-05 | (b) | 6.0809e-05 | (f) | 2.3828e-05 | (b) | 6.0809e-05 | (f) | 2.3828e-05 | (b) | 6.0809e-05 | (f) | 2.3828e-05 | (b) | 6.0809e-05 | (f) | 2.3828e-05 | (b) | 6.0809e-05 | (f) | 2.3828e-05 | (b) | 6.0809e-05 | (f) | 1.9896e-05 | (b) | 5.0773e-05 | (f) | 1.9896e-05 | (b) | 5.0773e-05 | (f) | 1.9896e-05 | (b) | 5.0773e-05 | (f) | 2.7761e-05 | (b) | 7.0846e-05 | (f) | 2.7761e-05 | (b) | 7.0846e-05 | (f) | 2.7761e-05 | (b) | 7.0846e-05 | (f) | 2.7761e-05 | (b) | 7.0846e-05 | (f) | 2.7761e-05 | (b) | 7.0846e-05 | (f) | 2.7761e-05 | (b) | 7.0846e-05 | (f) | 2.7761e-05 | (b) | 7.0846e-05 | (f) | 2.7761e-05 | (b) | 7.0846e-05 | (f) | 2.7761e-05 | (b) | 7.0846e-05 | (f) | 2.7761e-05 | (b) | 7.0846e-05 | (f) | 2.7761e-05 | (b) | 7.0846e-05 | (f) | 2.7761e-05 | (b) | 7.0846e-05 | (f) | 2.7761e-05 | (b) | 7.0846e-05 | (f) | 2.7761e-05 | (b) | 7.0846e-05 | (f) | 2.7761e-05 | (b) | 7.0846e-05 | (f) | 2.7761e-05 | (b) | 7.0846e-05 | (f) | 2.7761e-05 | (b) | 7.0846e-05 | (f) | 2.7761e-05 | (b) | 7.0846e-05 | (f) | 2.7761e-05 | (b) | 7.0846e-05 | (f) | 2.7761e-05 | (b) | 7.0846e-05 | (f) | 2.7761e-05 | (b) | 7.0846e-05 | (f) | 2.3828e-05 | (b) | 6.0809e-05 | (f) | 2.3828e-05 | (b) | 6.0809e-05 | (f) | 2.519e-05 | (b) | 6.4284e-05 | (f) | 2.519e-05 | (b) | 6.4284e-05 | (f) | 4.2065e-06 | (b) | 1.0735e-05 | (f) | 2.7761e-05 | (b) | 7.0846e-05 | (f) | 2.7761e-05 | (b) | 7.0846e-05 | (f) | 2.7761e-05 | (b) | 7.0846e-05 | (f) | 2.7761e-05 | (b) | 7.0846e-05 | (f) | 2.7761e-05 | (b) | 7.0846e-05 | (f) | 2.7761e-05 | (b) | 7.0846e-05 | (f) | 2.7761e-05 | (b) | 7.0846e-05 | (f) | 2.7761e-05 | (b) | 7.0846e-05 | (f)
| Benzo[g,h,i]perylene | 191-24-2 | 2.1874e-05 |  | 63 | (3) | 63 | (8) | 1.6764e-05 | (b) | 4.2782e-05 | (f) | 1.6764e-05 | (b) | 4.2782e-05 | (f) | 1.6764e-05 | (b) | 4.2782e-05 | (f) | 1.6764e-05 | (b) | 4.2782e-05 | (f) | 1.6764e-05 | (b) | 4.2782e-05 | (f) | 1.6764e-05 | (b) | 4.2782e-05 | (f) | 1.3997e-05 | (b) | 3.5721e-05 | (f) | 1.3997e-05 | (b) | 3.5721e-05 | (f) | 1.3997e-05 | (b) | 3.5721e-05 | (f) | 1.9531e-05 | (b) | 4.9843e-05 | (f) | 1.9531e-05 | (b) | 4.9843e-05 | (f) | 1.9531e-05 | (b) | 4.9843e-05 | (f) | 1.9531e-05 | (b) | 4.9843e-05 | (f) | 1.9531e-05 | (b) | 4.9843e-05 | (f) | 1.9531e-05 | (b) | 4.9843e-05 | (f) | 1.9531e-05 | (b) | 4.9843e-05 | (f) | 1.9531e-05 | (b) | 4.9843e-05 | (f) | 1.9531e-05 | (b) | 4.9843e-05 | (f) | 1.9531e-05 | (b) | 4.9843e-05 | (f) | 1.9531e-05 | (b) | 4.9843e-05 | (f) | 1.9531e-05 | (b) | 4.9843e-05 | (f) | 1.9531e-05 | (b) | 4.9843e-05 | (f) | 1.9531e-05 | (b) | 4.9843e-05 | (f) | 1.9531e-05 | (b) | 4.9843e-05 | (f) | 1.9531e-05 | (b) | 4.9843e-05 | (f) | 1.9531e-05 | (b) | 4.9843e-05 | (f) | 1.9531e-05 | (b) | 4.9843e-05 | (f) | 1.9531e-05 | (b) | 4.9843e-05 | (f) | 1.9531e-05 | (b) | 4.9843e-05 | (f) | 1.9531e-05 | (b) | 4.9843e-05 | (f) | 1.6764e-05 | (b) | 4.2782e-05 | (f) | 1.6764e-05 | (b) | 4.2782e-05 | (f) | 1.6764e-05 | (b) | 4.2782e-05 | (f) | 1.6764e-05 | (b) | 4.2782e-05 | (f) | 2.7995e-06 | (b) | 7.1442e-06 | (f) | 1.9531e-05 | (b) | 4.9843e-05 | (f) | 1.9531e-05 | (b) | 4.9843e-05 | (f) | 1.9531e-05 | (b) | 4.9843e-05 | (f) | 1.9531e-05 | (b) | 4.9843e-05 | (f) | 1.9531e-05 | (b) | 4.9843e-05 | (f) | 1.9531e-05 | (b) | 4.9843e-05 | (f) | 1.9531e-05 | (b) | 4.9843e-05 | (f) | 1.9531e-05 | (b) | 4.9843e-05 | (f)
| Benzo[k]fluoranthene | 207-08-9 | 1.3054e-05 |  | 63 | (3) | 63 | (8) | 1.0005e-05 | (b) | 2.5532e-05 | (f) | 1.0005e-05 | (b) | 2.5532e-05 | (f) | 1.0005e-05 | (b) | 2.5532e-05 | (f) | 1.0005e-05 | (b) | 2.5532e-05 | (f) | 1.0005e-05 | (b) | 2.5532e-05 | (f) | 1.0005e-05 | (b) | 2.5532e-05 | (f) | 8.3535e-06 | (b) | 2.1318e-05 | (f) | 8.3535e-06 | (b) | 2.1318e-05 | (f) | 8.3535e-06 | (b) | 2.1318e-05 | (f) | 1.1656e-05 | (b) | 2.9746e-05 | (f) | 1.1656e-05 | (b) | 2.9746e-05 | (f) | 1.1656e-05 | (b) | 2.9746e-05 | (f) | 1.1656e-05 | (b) | 2.9746e-05 | (f) | 1.1656e-05 | (b) | 2.9746e-05 | (f) | 1.1656e-05 | (b) | 2.9746e-05 | (f) | 1.1656e-05 | (b) | 2.9746e-05 | (f) | 1.1656e-05 | (b) | 2.9746e-05 | (f) | 1.1656e-05 | (b) | 2.9746e-05 | (f) | 1.1656e-05 | (b) | 2.9746e-05 | (f) | 1.1656e-05 | (b) | 2.9746e-05 | (f) | 1.1656e-05 | (b) | 2.9746e-05 | (f) | 1.1656e-05 | (b) | 2.9746e-05 | (f) | 1.1656e-05 | (b) | 2.9746e-05 | (f) | 1.1656e-05 | (b) | 2.9746e-05 | (f) | 1.1656e-05 | (b) | 2.9746e-05 | (f) | 1.1656e-05 | (b) | 2.9746e-05 | (f) | 1.1656e-05 | (b) | 2.9746e-05 | (f) | 1.1656e-05 | (b) | 2.9746e-05 | (f) | 1.1656e-05 | (b) | 2.9746e-05 | (f) | 1.1656e-05 | (b) | 2.9746e-05 | (f) | 1.0005e-05 | (b) | 2.5532e-05 | (f) | 1.0005e-05 | (b) | 2.5532e-05 | (f) | 1.0005e-05 | (b) | 2.5532e-05 | (f) | 1.0005e-05 | (b) | 2.5532e-05 | (f) | 1.6707e-06 | (b) | 4.2636e-06 | (f) | 1.1656e-05 | (b) | 2.9746e-05 | (f) | 1.1656e-05 | (b) | 2.9746e-05 | (f) | 1.1656e-05 | (b) | 2.9746e-05 | (f) | 1.1656e-05 | (b) | 2.9746e-05 | (f) | 1.1656e-05 | (b) | 2.9746e-05 | (f) | 1.1656e-05 | (b) | 2.9746e-05 | (f) | 1.1656e-05 | (b) | 2.9746e-05 | (f) | 1.1656e-05 | (b) | 2.9746e-05 | (f)
| Chrysene | 218-01-9 | 6.7e-05 |  | 63 | (3) | 65 | (8) | 4.8573e-05 | (b) | 0.00012396 | (f) | 4.8573e-05 | (b) | 0.00012396 | (f) | 4.8573e-05 | (b) | 0.00012396 | (f) | 4.8573e-05 | (b) | 0.00012396 | (f) | 4.8573e-05 | (b) | 0.00012396 | (f) | 4.8573e-05 | (b) | 0.00012396 | (f) | 4.0556e-05 | (b) | 0.0001035 | (f) | 4.0556e-05 | (b) | 0.0001035 | (f) | 4.0556e-05 | (b) | 0.0001035 | (f) | 5.6589e-05 | (b) | 0.00014441 | (f) | 5.6589e-05 | (b) | 0.00014441 | (f) | 5.6589e-05 | (b) | 0.00014441 | (f) | 5.6589e-05 | (b) | 0.00014441 | (f) | 5.6589e-05 | (b) | 0.00014441 | (f) | 5.6589e-05 | (b) | 0.00014441 | (f) | 5.6589e-05 | (b) | 0.00014441 | (f) | 5.6589e-05 | (b) | 0.00014441 | (f) | 5.6589e-05 | (b) | 0.00014441 | (f) | 5.6589e-05 | (b) | 0.00014441 | (f) | 5.6589e-05 | (b) | 0.00014441 | (f) | 5.6589e-05 | (b) | 0.00014441 | (f) | 5.6589e-05 | (b) | 0.00014441 | (f) | 5.6589e-05 | (b) | 0.00014441 | (f) | 5.6589e-05 | (b) | 0.00014441 | (f) | 5.6589e-05 | (b) | 0.00014441 | (f) | 5.6589e-05 | (b) | 0.00014441 | (f) | 5.6589e-05 | (b) | 0.00014441 | (f) | 5.6589e-05 | (b) | 0.00014441 | (f) | 5.6589e-05 | (b) | 0.00014441 | (f) | 5.6589e-05 | (b) | 0.00014441 | (f) | 4.8573e-05 | (b) | 0.00012396 | (f) | 4.8573e-05 | (b) | 0.00012396 | (f) | 5.1348e-05 | (b) | 0.00013104 | (f) | 5.1348e-05 | (b) | 0.00013104 | (f) | 8.5747e-06 | (b) | 2.1882e-05 | (f) | 5.6589e-05 | (b) | 0.00014441 | (f) | 5.6589e-05 | (b) | 0.00014441 | (f) | 5.6589e-05 | (b) | 0.00014441 | (f) | 5.6589e-05 | (b) | 0.00014441 | (f) | 5.6589e-05 | (b) | 0.00014441 | (f) | 5.6589e-05 | (b) | 0.00014441 | (f) | 5.6589e-05 | (b) | 0.00014441 | (f) | 5.6589e-05 | (b) | 0.00014441 | (f)
| Dibenz[a,h]anthracene | 53-70-3 | 1.037e-06 |  | 63 | (3) | 65 | (8) | 7.5178e-07 | (b) | 1.9185e-06 | (f) | 7.5178e-07 | (b) | 1.9185e-06 | (f) | 7.5178e-07 | (b) | 1.9185e-06 | (f) | 7.5178e-07 | (b) | 1.9185e-06 | (f) | 7.5178e-07 | (b) | 1.9185e-06 | (f) | 7.5178e-07 | (b) | 1.9185e-06 | (f) | 6.277e-07 | (b) | 1.6019e-06 | (f) | 6.277e-07 | (b) | 1.6019e-06 | (f) | 6.277e-07 | (b) | 1.6019e-06 | (f) | 8.7586e-07 | (b) | 2.2352e-06 | (f) | 8.7586e-07 | (b) | 2.2352e-06 | (f) | 8.7586e-07 | (b) | 2.2352e-06 | (f) | 8.7586e-07 | (b) | 2.2352e-06 | (f) | 8.7586e-07 | (b) | 2.2352e-06 | (f) | 8.7586e-07 | (b) | 2.2352e-06 | (f) | 8.7586e-07 | (b) | 2.2352e-06 | (f) | 8.7586e-07 | (b) | 2.2352e-06 | (f) | 8.7586e-07 | (b) | 2.2352e-06 | (f) | 8.7586e-07 | (b) | 2.2352e-06 | (f) | 8.7586e-07 | (b) | 2.2352e-06 | (f) | 8.7586e-07 | (b) | 2.2352e-06 | (f) | 8.7586e-07 | (b) | 2.2352e-06 | (f) | 8.7586e-07 | (b) | 2.2352e-06 | (f) | 8.7586e-07 | (b) | 2.2352e-06 | (f) | 8.7586e-07 | (b) | 2.2352e-06 | (f) | 8.7586e-07 | (b) | 2.2352e-06 | (f) | 8.7586e-07 | (b) | 2.2352e-06 | (f) | 8.7586e-07 | (b) | 2.2352e-06 | (f) | 8.7586e-07 | (b) | 2.2352e-06 | (f) | 8.7586e-07 | (b) | 2.2352e-06 | (f) | 7.5178e-07 | (b) | 1.9185e-06 | (f) | 7.5178e-07 | (b) | 1.9185e-06 | (f) | 7.9474e-07 | (b) | 2.0281e-06 | (f) | 7.9474e-07 | (b) | 2.0281e-06 | (f) | 1.3271e-07 | (b) | 3.3868e-07 | (f) | 8.7586e-07 | (b) | 2.2352e-06 | (f) | 8.7586e-07 | (b) | 2.2352e-06 | (f) | 8.7586e-07 | (b) | 2.2352e-06 | (f) | 8.7586e-07 | (b) | 2.2352e-06 | (f) | 8.7586e-07 | (b) | 2.2352e-06 | (f) | 8.7586e-07 | (b) | 2.2352e-06 | (f) | 8.7586e-07 | (b) | 2.2352e-06 | (f) | 8.7586e-07 | (b) | 2.2352e-06 | (f)
| Fluoranthene | 206-44-0 | 0.00036995 |  | 63 | (3) | 68 | (8) | 0.00024521 | (b) | 0.00062578 | (f) | 0.00024521 | (b) | 0.00062578 | (f) | 0.00024521 | (b) | 0.00062578 | (f) | 0.00024521 | (b) | 0.00062578 | (f) | 0.00024521 | (b) | 0.00062578 | (f) | 0.00024521 | (b) | 0.00062578 | (f) | 0.00020474 | (b) | 0.00052249 | (f) | 0.00020474 | (b) | 0.00052249 | (f) | 0.00020474 | (b) | 0.00052249 | (f) | 0.00028569 | (b) | 0.00072906 | (f) | 0.00028569 | (b) | 0.00072906 | (f) | 0.00028569 | (b) | 0.00072906 | (f) | 0.00028569 | (b) | 0.00072906 | (f) | 0.00028569 | (b) | 0.00072906 | (f) | 0.00028569 | (b) | 0.00072906 | (f) | 0.00028569 | (b) | 0.00072906 | (f) | 0.00028569 | (b) | 0.00072906 | (f) | 0.00028569 | (b) | 0.00072906 | (f) | 0.00028569 | (b) | 0.00072906 | (f) | 0.00028569 | (b) | 0.00072906 | (f) | 0.00028569 | (b) | 0.00072906 | (f) | 0.00028569 | (b) | 0.00072906 | (f) | 0.00028569 | (b) | 0.00072906 | (f) | 0.00028569 | (b) | 0.00072906 | (f) | 0.00028569 | (b) | 0.00072906 | (f) | 0.00028569 | (b) | 0.00072906 | (f) | 0.00028569 | (b) | 0.00072906 | (f) | 0.00028569 | (b) | 0.00072906 | (f) | 0.00028569 | (b) | 0.00072906 | (f) | 0.00028569 | (b) | 0.00072906 | (f) | 0.00024521 | (b) | 0.00062578 | (f) | 0.00024521 | (b) | 0.00062578 | (f) | 0.00028353 | (b) | 0.00072356 | (f) | 0.00028353 | (b) | 0.00072356 | (f) | 4.7347e-05 | (b) | 0.00012083 | (f) | 0.00028569 | (b) | 0.00072906 | (f) | 0.00028569 | (b) | 0.00072906 | (f) | 0.00028569 | (b) | 0.00072906 | (f) | 0.00028569 | (b) | 0.00072906 | (f) | 0.00028569 | (b) | 0.00072906 | (f) | 0.00028569 | (b) | 0.00072906 | (f) | 0.00028569 | (b) | 0.00072906 | (f) | 0.00028569 | (b) | 0.00072906 | (f)
| Fluorene | 86-73-7 | 0.0021844 |  | 63 | (3) | 68 | (8) | 0.0014479 | (b) | 0.0036949 | (f) | 0.0014479 | (b) | 0.0036949 | (f) | 0.0014479 | (b) | 0.0036949 | (f) | 0.0014479 | (b) | 0.0036949 | (f) | 0.0014479 | (b) | 0.0036949 | (f) | 0.0014479 | (b) | 0.0036949 | (f) | 0.0012089 | (b) | 0.0030851 | (f) | 0.0012089 | (b) | 0.0030851 | (f) | 0.0012089 | (b) | 0.0030851 | (f) | 0.0016868 | (b) | 0.0043048 | (f) | 0.0016868 | (b) | 0.0043048 | (f) | 0.0016868 | (b) | 0.0043048 | (f) | 0.0016868 | (b) | 0.0043048 | (f) | 0.0016868 | (b) | 0.0043048 | (f) | 0.0016868 | (b) | 0.0043048 | (f) | 0.0016868 | (b) | 0.0043048 | (f) | 0.0016868 | (b) | 0.0043048 | (f) | 0.0016868 | (b) | 0.0043048 | (f) | 0.0016868 | (b) | 0.0043048 | (f) | 0.0016868 | (b) | 0.0043048 | (f) | 0.0016868 | (b) | 0.0043048 | (f) | 0.0016868 | (b) | 0.0043048 | (f) | 0.0016868 | (b) | 0.0043048 | (f) | 0.0016868 | (b) | 0.0043048 | (f) | 0.0016868 | (b) | 0.0043048 | (f) | 0.0016868 | (b) | 0.0043048 | (f) | 0.0016868 | (b) | 0.0043048 | (f) | 0.0016868 | (b) | 0.0043048 | (f) | 0.0016868 | (b) | 0.0043048 | (f) | 0.0016868 | (b) | 0.0043048 | (f) | 0.0014479 | (b) | 0.0036949 | (f) | 0.0014479 | (b) | 0.0036949 | (f) | 0.0016741 | (b) | 0.0042723 | (f) | 0.0016741 | (b) | 0.0042723 | (f) | 0.00027956 | (b) | 0.00071343 | (f) | 0.0016868 | (b) | 0.0043048 | (f) | 0.0016868 | (b) | 0.0043048 | (f) | 0.0016868 | (b) | 0.0043048 | (f) | 0.0016868 | (b) | 0.0043048 | (f) | 0.0016868 | (b) | 0.0043048 | (f) | 0.0016868 | (b) | 0.0043048 | (f) | 0.0016868 | (b) | 0.0043048 | (f) | 0.0016868 | (b) | 0.0043048 | (f)
| Indeno[1,2,3-cd]pyrene | 193-39-5 | 1.0711e-05 |  | 63 | (3) | 70 | (8) | 6.6558e-06 | (b) | 1.6985e-05 | (f) | 6.6558e-06 | (b) | 1.6985e-05 | (f) | 6.6558e-06 | (b) | 1.6985e-05 | (f) | 6.6558e-06 | (b) | 1.6985e-05 | (f) | 6.6558e-06 | (b) | 1.6985e-05 | (f) | 6.6558e-06 | (b) | 1.6985e-05 | (f) | 5.5573e-06 | (b) | 1.4182e-05 | (f) | 5.5573e-06 | (b) | 1.4182e-05 | (f) | 5.5573e-06 | (b) | 1.4182e-05 | (f) | 7.7543e-06 | (b) | 1.9789e-05 | (f) | 7.7543e-06 | (b) | 1.9789e-05 | (f) | 7.7543e-06 | (b) | 1.9789e-05 | (f) | 7.7543e-06 | (b) | 1.9789e-05 | (f) | 7.7543e-06 | (b) | 1.9789e-05 | (f) | 7.7543e-06 | (b) | 1.9789e-05 | (f) | 7.7543e-06 | (b) | 1.9789e-05 | (f) | 7.7543e-06 | (b) | 1.9789e-05 | (f) | 7.7543e-06 | (b) | 1.9789e-05 | (f) | 7.7543e-06 | (b) | 1.9789e-05 | (f) | 7.7543e-06 | (b) | 1.9789e-05 | (f) | 7.7543e-06 | (b) | 1.9789e-05 | (f) | 7.7543e-06 | (b) | 1.9789e-05 | (f) | 7.7543e-06 | (b) | 1.9789e-05 | (f) | 7.7543e-06 | (b) | 1.9789e-05 | (f) | 7.7543e-06 | (b) | 1.9789e-05 | (f) | 7.7543e-06 | (b) | 1.9789e-05 | (f) | 7.7543e-06 | (b) | 1.9789e-05 | (f) | 7.7543e-06 | (b) | 1.9789e-05 | (f) | 7.7543e-06 | (b) | 1.9789e-05 | (f) | 7.7543e-06 | (b) | 1.9789e-05 | (f) | 6.6558e-06 | (b) | 1.6985e-05 | (f) | 6.6558e-06 | (b) | 1.6985e-05 | (f) | 8.2088e-06 | (b) | 2.0949e-05 | (f) | 8.2088e-06 | (b) | 2.0949e-05 | (f) | 1.3708e-06 | (b) | 3.4982e-06 | (f) | 7.7543e-06 | (b) | 1.9789e-05 | (f) | 7.7543e-06 | (b) | 1.9789e-05 | (f) | 7.7543e-06 | (b) | 1.9789e-05 | (f) | 7.7543e-06 | (b) | 1.9789e-05 | (f) | 7.7543e-06 | (b) | 1.9789e-05 | (f) | 7.7543e-06 | (b) | 1.9789e-05 | (f) | 7.7543e-06 | (b) | 1.9789e-05 | (f) | 7.7543e-06 | (b) | 1.9789e-05 | (f)
| Naphthalene | 91-20-3 | 0.026352 |  | 63 | (3) | 65 | (8) | 0.019105 | (b) | 0.048754 | (f) | 0.019105 | (b) | 0.048754 | (f) | 0.019105 | (b) | 0.048754 | (f) | 0.019105 | (b) | 0.048754 | (f) | 0.019105 | (b) | 0.048754 | (f) | 0.019105 | (b) | 0.048754 | (f) | 0.015951 | (b) | 0.040707 | (f) | 0.015951 | (b) | 0.040707 | (f) | 0.015951 | (b) | 0.040707 | (f) | 0.022258 | (b) | 0.056801 | (f) | 0.022258 | (b) | 0.056801 | (f) | 0.022258 | (b) | 0.056801 | (f) | 0.022258 | (b) | 0.056801 | (f) | 0.022258 | (b) | 0.056801 | (f) | 0.022258 | (b) | 0.056801 | (f) | 0.022258 | (b) | 0.056801 | (f) | 0.022258 | (b) | 0.056801 | (f) | 0.022258 | (b) | 0.056801 | (f) | 0.022258 | (b) | 0.056801 | (f) | 0.022258 | (b) | 0.056801 | (f) | 0.022258 | (b) | 0.056801 | (f) | 0.022258 | (b) | 0.056801 | (f) | 0.022258 | (b) | 0.056801 | (f) | 0.022258 | (b) | 0.056801 | (f) | 0.022258 | (b) | 0.056801 | (f) | 0.022258 | (b) | 0.056801 | (f) | 0.022258 | (b) | 0.056801 | (f) | 0.022258 | (b) | 0.056801 | (f) | 0.022258 | (b) | 0.056801 | (f) | 0.022258 | (b) | 0.056801 | (f) | 0.019105 | (b) | 0.048754 | (f) | 0.019105 | (b) | 0.048754 | (f) | 0.020196 | (b) | 0.05154 | (f) | 0.020196 | (b) | 0.05154 | (f) | 0.0033726 | (b) | 0.0086067 | (f) | 0.022258 | (b) | 0.056801 | (f) | 0.022258 | (b) | 0.056801 | (f) | 0.022258 | (b) | 0.056801 | (f) | 0.022258 | (b) | 0.056801 | (f) | 0.022258 | (b) | 0.056801 | (f) | 0.022258 | (b) | 0.056801 | (f) | 0.022258 | (b) | 0.056801 | (f) | 0.022258 | (b) | 0.056801 | (f)
| Perylene | 198-55-0 | 1.1782e-06 |  | 63 | (3) | 63 | (8) | 9.03e-07 | (b) | 2.3044e-06 | (f) | 9.03e-07 | (b) | 2.3044e-06 | (f) | 9.03e-07 | (b) | 2.3044e-06 | (f) | 9.03e-07 | (b) | 2.3044e-06 | (f) | 9.03e-07 | (b) | 2.3044e-06 | (f) | 9.03e-07 | (b) | 2.3044e-06 | (f) | 7.5396e-07 | (b) | 1.9241e-06 | (f) | 7.5396e-07 | (b) | 1.9241e-06 | (f) | 7.5396e-07 | (b) | 1.9241e-06 | (f) | 1.052e-06 | (b) | 2.6848e-06 | (f) | 1.052e-06 | (b) | 2.6848e-06 | (f) | 1.052e-06 | (b) | 2.6848e-06 | (f) | 1.052e-06 | (b) | 2.6848e-06 | (f) | 1.052e-06 | (b) | 2.6848e-06 | (f) | 1.052e-06 | (b) | 2.6848e-06 | (f) | 1.052e-06 | (b) | 2.6848e-06 | (f) | 1.052e-06 | (b) | 2.6848e-06 | (f) | 1.052e-06 | (b) | 2.6848e-06 | (f) | 1.052e-06 | (b) | 2.6848e-06 | (f) | 1.052e-06 | (b) | 2.6848e-06 | (f) | 1.052e-06 | (b) | 2.6848e-06 | (f) | 1.052e-06 | (b) | 2.6848e-06 | (f) | 1.052e-06 | (b) | 2.6848e-06 | (f) | 1.052e-06 | (b) | 2.6848e-06 | (f) | 1.052e-06 | (b) | 2.6848e-06 | (f) | 1.052e-06 | (b) | 2.6848e-06 | (f) | 1.052e-06 | (b) | 2.6848e-06 | (f) | 1.052e-06 | (b) | 2.6848e-06 | (f) | 1.052e-06 | (b) | 2.6848e-06 | (f) | 1.052e-06 | (b) | 2.6848e-06 | (f) | 9.03e-07 | (b) | 2.3044e-06 | (f) | 9.03e-07 | (b) | 2.3044e-06 | (f) | 9.03e-07 | (b) | 2.3044e-06 | (f) | 9.03e-07 | (b) | 2.3044e-06 | (f) | 1.5079e-07 | (b) | 3.8482e-07 | (f) | 1.052e-06 | (b) | 2.6848e-06 | (f) | 1.052e-06 | (b) | 2.6848e-06 | (f) | 1.052e-06 | (b) | 2.6848e-06 | (f) | 1.052e-06 | (b) | 2.6848e-06 | (f) | 1.052e-06 | (b) | 2.6848e-06 | (f) | 1.052e-06 | (b) | 2.6848e-06 | (f) | 1.052e-06 | (b) | 2.6848e-06 | (f) | 1.052e-06 | (b) | 2.6848e-06 | (f)
| Phenanthrene | 85-01-8 | 0.0045419 |  | 63 | (3) | 63 | (8) | 0.0034809 | (b) | 0.0088832 | (f) | 0.0034809 | (b) | 0.0088832 | (f) | 0.0034809 | (b) | 0.0088832 | (f) | 0.0034809 | (b) | 0.0088832 | (f) | 0.0034809 | (b) | 0.0088832 | (f) | 0.0034809 | (b) | 0.0088832 | (f) | 0.0029064 | (b) | 0.007417 | (f) | 0.0029064 | (b) | 0.007417 | (f) | 0.0029064 | (b) | 0.007417 | (f) | 0.0040554 | (b) | 0.010349 | (f) | 0.0040554 | (b) | 0.010349 | (f) | 0.0040554 | (b) | 0.010349 | (f) | 0.0040554 | (b) | 0.010349 | (f) | 0.0040554 | (b) | 0.010349 | (f) | 0.0040554 | (b) | 0.010349 | (f) | 0.0040554 | (b) | 0.010349 | (f) | 0.0040554 | (b) | 0.010349 | (f) | 0.0040554 | (b) | 0.010349 | (f) | 0.0040554 | (b) | 0.010349 | (f) | 0.0040554 | (b) | 0.010349 | (f) | 0.0040554 | (b) | 0.010349 | (f) | 0.0040554 | (b) | 0.010349 | (f) | 0.0040554 | (b) | 0.010349 | (f) | 0.0040554 | (b) | 0.010349 | (f) | 0.0040554 | (b) | 0.010349 | (f) | 0.0040554 | (b) | 0.010349 | (f) | 0.0040554 | (b) | 0.010349 | (f) | 0.0040554 | (b) | 0.010349 | (f) | 0.0040554 | (b) | 0.010349 | (f) | 0.0040554 | (b) | 0.010349 | (f) | 0.0034809 | (b) | 0.0088832 | (f) | 0.0034809 | (b) | 0.0088832 | (f) | 0.0034809 | (b) | 0.0088832 | (f) | 0.0034809 | (b) | 0.0088832 | (f) | 0.00058128 | (b) | 0.0014834 | (f) | 0.0040554 | (b) | 0.010349 | (f) | 0.0040554 | (b) | 0.010349 | (f) | 0.0040554 | (b) | 0.010349 | (f) | 0.0040554 | (b) | 0.010349 | (f) | 0.0040554 | (b) | 0.010349 | (f) | 0.0040554 | (b) | 0.010349 | (f) | 0.0040554 | (b) | 0.010349 | (f) | 0.0040554 | (b) | 0.010349 | (f)
| Pyrene | 129-00-0 | 0.00125 |  | 63 | (3) | 63 | (8) | 0.00095799 | (b) | 0.0024448 | (f) | 0.00095799 | (b) | 0.0024448 | (f) | 0.00095799 | (b) | 0.0024448 | (f) | 0.00095799 | (b) | 0.0024448 | (f) | 0.00095799 | (b) | 0.0024448 | (f) | 0.00095799 | (b) | 0.0024448 | (f) | 0.00079988 | (b) | 0.0020413 | (f) | 0.00079988 | (b) | 0.0020413 | (f) | 0.00079988 | (b) | 0.0020413 | (f) | 0.0011161 | (b) | 0.0028483 | (f) | 0.0011161 | (b) | 0.0028483 | (f) | 0.0011161 | (b) | 0.0028483 | (f) | 0.0011161 | (b) | 0.0028483 | (f) | 0.0011161 | (b) | 0.0028483 | (f) | 0.0011161 | (b) | 0.0028483 | (f) | 0.0011161 | (b) | 0.0028483 | (f) | 0.0011161 | (b) | 0.0028483 | (f) | 0.0011161 | (b) | 0.0028483 | (f) | 0.0011161 | (b) | 0.0028483 | (f) | 0.0011161 | (b) | 0.0028483 | (f) | 0.0011161 | (b) | 0.0028483 | (f) | 0.0011161 | (b) | 0.0028483 | (f) | 0.0011161 | (b) | 0.0028483 | (f) | 0.0011161 | (b) | 0.0028483 | (f) | 0.0011161 | (b) | 0.0028483 | (f) | 0.0011161 | (b) | 0.0028483 | (f) | 0.0011161 | (b) | 0.0028483 | (f) | 0.0011161 | (b) | 0.0028483 | (f) | 0.0011161 | (b) | 0.0028483 | (f) | 0.0011161 | (b) | 0.0028483 | (f) | 0.00095799 | (b) | 0.0024448 | (f) | 0.00095799 | (b) | 0.0024448 | (f) | 0.00095799 | (b) | 0.0024448 | (f) | 0.00095799 | (b) | 0.0024448 | (f) | 0.00015998 | (b) | 0.00040825 | (f) | 0.0011161 | (b) | 0.0028483 | (f) | 0.0011161 | (b) | 0.0028483 | (f) | 0.0011161 | (b) | 0.0028483 | (f) | 0.0011161 | (b) | 0.0028483 | (f) | 0.0011161 | (b) | 0.0028483 | (f) | 0.0011161 | (b) | 0.0028483 | (f) | 0.0011161 | (b) | 0.0028483 | (f) | 0.0011161 | (b) | 0.0028483 | (f)
DIESEL PARTICULATE MATTER (DPM)
| DPM | 200 | 16.9752 |  | 90 | (10) | 93 | (11) | 2.4613 | (b) | 6.2811 | (f) | 2.4613 | (b) | 6.2811 | (f) | 2.4613 | (b) | 6.2811 | (f) | 2.4613 | (b) | 6.2811 | (f) | 2.4613 | (b) | 6.2811 | (f) | 2.4613 | (b) | 6.2811 | (f) | 2.0551 | (b) | 5.2444 | (f) | 2.0551 | (b) | 5.2444 | (f) | 2.0551 | (b) | 5.2444 | (f) | 2.8675 | (b) | 7.3178 | (f) | 2.8675 | (b) | 7.3178 | (f) | 2.8675 | (b) | 7.3178 | (f) | 2.8675 | (b) | 7.3178 | (f) | 2.8675 | (b) | 7.3178 | (f) | 2.8675 | (b) | 7.3178 | (f) | 2.8675 | (b) | 7.3178 | (f) | 2.8675 | (b) | 7.3178 | (f) | 2.8675 | (b) | 7.3178 | (f) | 2.8675 | (b) | 7.3178 | (f) | 2.8675 | (b) | 7.3178 | (f) | 2.8675 | (b) | 7.3178 | (f) | 2.8675 | (b) | 7.3178 | (f) | 2.8675 | (b) | 7.3178 | (f) | 2.8675 | (b) | 7.3178 | (f) | 2.8675 | (b) | 7.3178 | (f) | 2.8675 | (b) | 7.3178 | (f) | 2.8675 | (b) | 7.3178 | (f) | 2.8675 | (b) | 7.3178 | (f) | 2.8675 | (b) | 7.3178 | (f) | 2.8675 | (b) | 7.3178 | (f) | 2.4613 | (b) | 6.2811 | (f) | 2.4613 | (b) | 6.2811 | (f) | 3.5161 | (b) | 8.973 | (f) | 3.5161 | (b) | 8.973 | (f) | 0.58716 | (b) | 1.4984 | (f) | 2.8675 | (b) | 7.3178 | (f) | 2.8675 | (b) | 7.3178 | (f) | 2.8675 | (b) | 7.3178 | (f) | 2.8675 | (b) | 7.3178 | (f) | 2.8675 | (b) | 7.3178 | (f) | 2.8675 | (b) | 7.3178 | (f) | 2.8675 | (b) | 7.3178 | (f) | 2.8675 | (b) | 7.3178 | (f)
Notes
DPF = Diesel Particulate Filter; HAP = Hazardous Air Pollutant; Mgal = 1,000 gallons; TAC = Toxic Air Contaminant.
(a) | Daily emissions estimate (lb/day) = ([emission factor {lb/Mgal}] x [fuel consumption {gal/hr}] x [daily hours of operation {hrs/day}] x [Mgal/1,000 gal]
x (1 - [DPF control efficiency {%}] / 100))
(b) | Daily emissions estimate (lb/day) = ([emission factor {lb/Mgal}] x [fuel consumption {gal/hr}] x [daily hours of operation {hrs/day}] x [Mgal/1,000 gal]
| + [cold start emissions {lb/minute}] x [number of cold starts per day] - [emissions per minute, normal operation {lb/minute}] x [number of cold starts per day]) | [13 empty] | (c), (d)
| x (1 - [DPF control efficiency {%}] / 100)) | [13 empty] | (5)
|  | Cold start adjustment factor = | 4.3 | (6)
|  | Cold start adjustment factor (formaldehyde) = | 4.8 | (6)
|  | Number of cold starts per day = | 1 | (7)
(c) | Cold start emissions (lb/minute) = (emission factor [lb/Mgal]) x [Mgal/1,000 gal] x (cold start adjustment factor) x (hourly fuel consumption [gal/hr]) / 60
(d) | Emissions per minute, normal operation (lb/minute) = (emission factor [lb/Mgal]) x (hourly fuel consumption [gal/hr]) / 60
(e) | Annual emissions estimate (lb/yr) = ([emission factor {lb/Mgal}] x [fuel consumption {gal/hr}] x [annual hours of operation {hrs/yr}] x [Mgal/1,000 gal]
x (1 - [DPF control efficiency {%}] / 100))
(f) | Annual emissions estimate (lb/yr) = ([emission factor {lb/Mgal}] x [fuel consumption {gal/hr}] x [annual hours of operation {hrs/yr}] x [Mgal/1,000 gal] | [14 empty] | (c), (d)
+ [cold start emissions {lb/minute}] x [number of cold starts per year] - [emissions per minute, normal operation {lb/minute}] x [number of cold starts per year])
| x (1 - [DPF control efficiency {%}] / 100)) | [14 empty] | (5)
|  | Cold start adjustment factor = | 4.3 | (6)
|  | Cold start adjustment factor (formaldehyde) = | 4.8 | (6)
|  | Number of cold starts per year = | 12 | (7)
References
(1) | See Table 1, Input Emergency Generator Rates and Parameters
(2) | Emission Factors from the Oregon Department of Environmental Quality, AQ104B, diesel internal combustion, greater
than 750 hp. Ammonia emission factor assumes value for no SNCR or SCR control. DEQ reference CAO Diesel RICE (b).
(3) | Information provided by Rypos, Inc.
(4) | Assumed 70 percent per DEQ guidance.
(5) | Time allotted for cold stats was omitted from the daily/annual operating capacity in emission calculations. Cold start adjustments are not required for metals.
(6) | Cold start adjustment factors provided by the Oregon Department of Environmental Quality. All applicable pollutants, except
formaldehyde, share the same adjustment factor. Cold start adjustments are not required for metals.
(7) | Information provided by Intel based on one cold start per month per engine.
(8) | Information provided by Johnson Matthey. If a range was provided, the value assumes the midpoint of the range.
(9) | Value based on similar TAC.
(10) | Value based on filterable PM efficiency provided by Rypos.
(11) | Value based on filterable PM efficiency provided by Johnson Matthey.

## EGENnoDPF_a_RONLER
Table 4
Emergency Generator—No DPF, Pre-2006, or < 750 hp TAC Emission Estimates—Ronler Acres
Intel Corporation
Emission Unit ID |  |  |  |  | RA1-ELEC-CPS-GEN01 |  |  |  | RA1-ELEC-CPS-GEN02 |  |  |  | RA1-ELEC-CPS-GEN03 |  |  |  | RA1-ELEC-CPS-GEN04 |  |  |  | D1C-CPS-GEN01 |  |  |  | D1C-CPS-GEN02 |  |  |  | D1C-CPS-GEN03 |  |  |  | D1C-EPS-GEN01 |  |  |  | D1C-EPS-GEN02 |  |  |  | RB1-EPS-GEN01 |  |  |  | RP1-EPS-GEN01 |  |  |  | EPS-GEN01 |  |  |  | EPS-GEN02 |  |  |  | EPS-GEN03 |  |  |  | EPS-GEN04 |  |  |  | EPS-GEN05 |  |  |  | EPS-GEN06 |  |  |  | RS4-ELEC-EG-4-1 |  |  |  | RS6-ELEC-EG-6-1 |  |  |  | F20-CPS-1 |  |  |  | MAX-EGEN
Fuel Consumption (gal/hr) |  |  |  | (1) | 113.51 |  |  |  | 113.51 |  |  |  | 113.51 |  |  |  | 113.51 |  |  |  | 89.71 |  |  |  | 89.71 |  |  |  | 89.71 |  |  |  | 123 |  |  |  | 123 |  |  |  | 137.5 |  |  |  | 145.4 |  |  |  | 147.46 |  |  |  | 147.46 |  |  |  | 147.46 |  |  |  | 147.46 |  |  |  | 147.46 |  |  |  | 147.46 |  |  |  | 22.9 |  |  |  | 22.9 |  |  |  | 46.4 |  |  |  | 19.4
Daily Hours of Operation (hrs/day) |  |  |  | (1) | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10
Annual Hours of Operation (hrs/yr) |  |  |  | (1) | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25
Pollutant |  | CAS | Emission Factor (2) (lb/Mgal) |  | Emissions Estimate | [67 empty] | Emissions Estimate (a)
[5 empty] | RA1-ELEC-CPS-GEN01 |  |  |  | RA1-ELEC-CPS-GEN02 |  |  |  | RA1-ELEC-CPS-GEN03 |  |  |  | RA1-ELEC-CPS-GEN04 |  |  |  | D1C-CPS-GEN01 |  |  |  | D1C-CPS-GEN02 |  |  |  | D1C-CPS-GEN03 |  |  |  | D1C-EPS-GEN01 |  |  |  | D1C-EPS-GEN02 |  |  |  | RB1-EPS-GEN01 |  |  |  | RP1-EPS-GEN01 |  |  |  | EPS-GEN01 |  |  |  | EPS-GEN02 |  |  |  | EPS-GEN03 |  |  |  | EPS-GEN04 |  |  |  | EPS-GEN05 |  |  |  | EPS-GEN06 |  |  |  | RS4-ELEC-EG-4-1 |  |  |  | RS6-ELEC-EG-6-1 |  |  |  | F20-CPS-1 |  |  |  | MAX-EGEN
[5 empty] | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr)
METALS
| Antimony and Compounds | 7440-36-0 | 0.00031819 |  | 0.00036117 | (a) | 0.00090294 | (e) | 0.00036117 | (a) | 0.00090294 | (e) | 0.00036117 | (a) | 0.00090294 | (e) | 0.00036117 | (a) | 0.00090294 | (e) | 0.00028545 | (a) | 0.00071361 | (e) | 0.00028545 | (a) | 0.00071361 | (e) | 0.00028545 | (a) | 0.00071361 | (e) | 0.00039137 | (a) | 0.00097843 | (e) | 0.00039137 | (a) | 0.00097843 | (e) | 0.00043751 | (a) | 0.0010938 | (e) | 0.00046264 | (a) | 0.0011566 | (e) | 0.0004692 | (a) | 0.001173 | (e) | 0.0004692 | (a) | 0.001173 | (e) | 0.0004692 | (a) | 0.001173 | (e) | 0.0004692 | (a) | 0.001173 | (e) | 0.0004692 | (a) | 0.001173 | (e) | 0.0004692 | (a) | 0.001173 | (e) | 7.2865e-05 | (a) | 0.00018216 | (e) | 7.2865e-05 | (a) | 0.00018216 | (e) | 0.00014764 | (a) | 0.0003691 | (e) | 6.1728e-05 | (a) | 0.00015432 | (e)
| Arsenic and Compounds | 7440-38-2 | 0.0016 |  | 0.0018162 | (a) | 0.0045404 | (e) | 0.0018162 | (a) | 0.0045404 | (e) | 0.0018162 | (a) | 0.0045404 | (e) | 0.0018162 | (a) | 0.0045404 | (e) | 0.0014354 | (a) | 0.0035884 | (e) | 0.0014354 | (a) | 0.0035884 | (e) | 0.0014354 | (a) | 0.0035884 | (e) | 0.001968 | (a) | 0.00492 | (e) | 0.001968 | (a) | 0.00492 | (e) | 0.0022 | (a) | 0.0055 | (e) | 0.0023264 | (a) | 0.005816 | (e) | 0.0023594 | (a) | 0.0058984 | (e) | 0.0023594 | (a) | 0.0058984 | (e) | 0.0023594 | (a) | 0.0058984 | (e) | 0.0023594 | (a) | 0.0058984 | (e) | 0.0023594 | (a) | 0.0058984 | (e) | 0.0023594 | (a) | 0.0058984 | (e) | 0.0003664 | (a) | 0.000916 | (e) | 0.0003664 | (a) | 0.000916 | (e) | 0.0007424 | (a) | 0.001856 | (e) | 0.0003104 | (a) | 0.000776 | (e)
| Barium and Compounds | 7440-39-3 | 0.00037389 |  | 0.00042441 | (a) | 0.001061 | (e) | 0.00042441 | (a) | 0.001061 | (e) | 0.00042441 | (a) | 0.001061 | (e) | 0.00042441 | (a) | 0.001061 | (e) | 0.00033542 | (a) | 0.00083855 | (e) | 0.00033542 | (a) | 0.00083855 | (e) | 0.00033542 | (a) | 0.00083855 | (e) | 0.00045989 | (a) | 0.0011497 | (e) | 0.00045989 | (a) | 0.0011497 | (e) | 0.0005141 | (a) | 0.0012853 | (e) | 0.00054364 | (a) | 0.0013591 | (e) | 0.00055134 | (a) | 0.0013784 | (e) | 0.00055134 | (a) | 0.0013784 | (e) | 0.00055134 | (a) | 0.0013784 | (e) | 0.00055134 | (a) | 0.0013784 | (e) | 0.00055134 | (a) | 0.0013784 | (e) | 0.00055134 | (a) | 0.0013784 | (e) | 8.5622e-05 | (a) | 0.00021405 | (e) | 8.5622e-05 | (a) | 0.00021405 | (e) | 0.00017349 | (a) | 0.00043372 | (e) | 7.2535e-05 | (a) | 0.00018134 | (e)
| Beryllium and compounds | 7440-41-7 | 4.7708e-06 |  | 5.4154e-06 | (a) | 1.3538e-05 | (e) | 5.4154e-06 | (a) | 1.3538e-05 | (e) | 5.4154e-06 | (a) | 1.3538e-05 | (e) | 5.4154e-06 | (a) | 1.3538e-05 | (e) | 4.2799e-06 | (a) | 1.07e-05 | (e) | 4.2799e-06 | (a) | 1.07e-05 | (e) | 4.2799e-06 | (a) | 1.07e-05 | (e) | 5.8681e-06 | (a) | 1.467e-05 | (e) | 5.8681e-06 | (a) | 1.467e-05 | (e) | 6.5599e-06 | (a) | 1.64e-05 | (e) | 6.9368e-06 | (a) | 1.7342e-05 | (e) | 7.0351e-06 | (a) | 1.7588e-05 | (e) | 7.0351e-06 | (a) | 1.7588e-05 | (e) | 7.0351e-06 | (a) | 1.7588e-05 | (e) | 7.0351e-06 | (a) | 1.7588e-05 | (e) | 7.0351e-06 | (a) | 1.7588e-05 | (e) | 7.0351e-06 | (a) | 1.7588e-05 | (e) | 1.0925e-06 | (a) | 2.7313e-06 | (e) | 1.0925e-06 | (a) | 2.7313e-06 | (e) | 2.2137e-06 | (a) | 5.5342e-06 | (e) | 9.2554e-07 | (a) | 2.3139e-06 | (e)
| Cadmium and Compounds | 7440-43-9 | 0.0015 |  | 0.0017026 | (a) | 0.0042566 | (e) | 0.0017026 | (a) | 0.0042566 | (e) | 0.0017026 | (a) | 0.0042566 | (e) | 0.0017026 | (a) | 0.0042566 | (e) | 0.0013457 | (a) | 0.0033641 | (e) | 0.0013457 | (a) | 0.0033641 | (e) | 0.0013457 | (a) | 0.0033641 | (e) | 0.001845 | (a) | 0.0046125 | (e) | 0.001845 | (a) | 0.0046125 | (e) | 0.0020625 | (a) | 0.0051563 | (e) | 0.002181 | (a) | 0.0054525 | (e) | 0.0022119 | (a) | 0.0055298 | (e) | 0.0022119 | (a) | 0.0055298 | (e) | 0.0022119 | (a) | 0.0055298 | (e) | 0.0022119 | (a) | 0.0055298 | (e) | 0.0022119 | (a) | 0.0055298 | (e) | 0.0022119 | (a) | 0.0055298 | (e) | 0.0003435 | (a) | 0.00085875 | (e) | 0.0003435 | (a) | 0.00085875 | (e) | 0.000696 | (a) | 0.00174 | (e) | 0.000291 | (a) | 0.0007275 | (e)
| Chromium VI | 18540-29-9 | 0.0001 |  | 0.00011351 | (a) | 0.00028378 | (e) | 0.00011351 | (a) | 0.00028378 | (e) | 0.00011351 | (a) | 0.00028378 | (e) | 0.00011351 | (a) | 0.00028378 | (e) | 8.971e-05 | (a) | 0.00022427 | (e) | 8.971e-05 | (a) | 0.00022427 | (e) | 8.971e-05 | (a) | 0.00022427 | (e) | 0.000123 | (a) | 0.0003075 | (e) | 0.000123 | (a) | 0.0003075 | (e) | 0.0001375 | (a) | 0.00034375 | (e) | 0.0001454 | (a) | 0.0003635 | (e) | 0.00014746 | (a) | 0.00036865 | (e) | 0.00014746 | (a) | 0.00036865 | (e) | 0.00014746 | (a) | 0.00036865 | (e) | 0.00014746 | (a) | 0.00036865 | (e) | 0.00014746 | (a) | 0.00036865 | (e) | 0.00014746 | (a) | 0.00036865 | (e) | 2.29e-05 | (a) | 5.725e-05 | (e) | 2.29e-05 | (a) | 5.725e-05 | (e) | 4.64e-05 | (a) | 0.000116 | (e) | 1.94e-05 | (a) | 4.85e-05 | (e)
| Copper and Compounds | 7440-50-8 | 0.0041 |  | 0.0046539 | (a) | 0.011635 | (e) | 0.0046539 | (a) | 0.011635 | (e) | 0.0046539 | (a) | 0.011635 | (e) | 0.0046539 | (a) | 0.011635 | (e) | 0.0036781 | (a) | 0.0091953 | (e) | 0.0036781 | (a) | 0.0091953 | (e) | 0.0036781 | (a) | 0.0091953 | (e) | 0.005043 | (a) | 0.012608 | (e) | 0.005043 | (a) | 0.012608 | (e) | 0.0056375 | (a) | 0.014094 | (e) | 0.0059614 | (a) | 0.014904 | (e) | 0.0060459 | (a) | 0.015115 | (e) | 0.0060459 | (a) | 0.015115 | (e) | 0.0060459 | (a) | 0.015115 | (e) | 0.0060459 | (a) | 0.015115 | (e) | 0.0060459 | (a) | 0.015115 | (e) | 0.0060459 | (a) | 0.015115 | (e) | 0.0009389 | (a) | 0.0023472 | (e) | 0.0009389 | (a) | 0.0023472 | (e) | 0.0019024 | (a) | 0.004756 | (e) | 0.0007954 | (a) | 0.0019885 | (e)
| Cobalt and compounds | 7440-48-4 | 1.5751e-05 |  | 1.7879e-05 | (a) | 4.4698e-05 | (e) | 1.7879e-05 | (a) | 4.4698e-05 | (e) | 1.7879e-05 | (a) | 4.4698e-05 | (e) | 1.7879e-05 | (a) | 4.4698e-05 | (e) | 1.413e-05 | (a) | 3.5326e-05 | (e) | 1.413e-05 | (a) | 3.5326e-05 | (e) | 1.413e-05 | (a) | 3.5326e-05 | (e) | 1.9374e-05 | (a) | 4.8435e-05 | (e) | 1.9374e-05 | (a) | 4.8435e-05 | (e) | 2.1658e-05 | (a) | 5.4145e-05 | (e) | 2.2902e-05 | (a) | 5.7255e-05 | (e) | 2.3227e-05 | (a) | 5.8067e-05 | (e) | 2.3227e-05 | (a) | 5.8067e-05 | (e) | 2.3227e-05 | (a) | 5.8067e-05 | (e) | 2.3227e-05 | (a) | 5.8067e-05 | (e) | 2.3227e-05 | (a) | 5.8067e-05 | (e) | 2.3227e-05 | (a) | 5.8067e-05 | (e) | 3.607e-06 | (a) | 9.0175e-06 | (e) | 3.607e-06 | (a) | 9.0175e-06 | (e) | 7.3085e-06 | (a) | 1.8271e-05 | (e) | 3.0557e-06 | (a) | 7.6393e-06 | (e)
| Lead and Compounds | 7439-92-1 | 0.0083 |  | 0.0094213 | (a) | 0.023553 | (e) | 0.0094213 | (a) | 0.023553 | (e) | 0.0094213 | (a) | 0.023553 | (e) | 0.0094213 | (a) | 0.023553 | (e) | 0.0074459 | (a) | 0.018615 | (e) | 0.0074459 | (a) | 0.018615 | (e) | 0.0074459 | (a) | 0.018615 | (e) | 0.010209 | (a) | 0.025522 | (e) | 0.010209 | (a) | 0.025522 | (e) | 0.011413 | (a) | 0.028531 | (e) | 0.012068 | (a) | 0.03017 | (e) | 0.012239 | (a) | 0.030598 | (e) | 0.012239 | (a) | 0.030598 | (e) | 0.012239 | (a) | 0.030598 | (e) | 0.012239 | (a) | 0.030598 | (e) | 0.012239 | (a) | 0.030598 | (e) | 0.012239 | (a) | 0.030598 | (e) | 0.0019007 | (a) | 0.0047517 | (e) | 0.0019007 | (a) | 0.0047517 | (e) | 0.0038512 | (a) | 0.009628 | (e) | 0.0016102 | (a) | 0.0040255 | (e)
| Manganese and Compounds | 7439-96-5 | 0.0031 |  | 0.0035188 | (a) | 0.008797 | (e) | 0.0035188 | (a) | 0.008797 | (e) | 0.0035188 | (a) | 0.008797 | (e) | 0.0035188 | (a) | 0.008797 | (e) | 0.002781 | (a) | 0.0069525 | (e) | 0.002781 | (a) | 0.0069525 | (e) | 0.002781 | (a) | 0.0069525 | (e) | 0.003813 | (a) | 0.0095325 | (e) | 0.003813 | (a) | 0.0095325 | (e) | 0.0042625 | (a) | 0.010656 | (e) | 0.0045074 | (a) | 0.011269 | (e) | 0.0045713 | (a) | 0.011428 | (e) | 0.0045713 | (a) | 0.011428 | (e) | 0.0045713 | (a) | 0.011428 | (e) | 0.0045713 | (a) | 0.011428 | (e) | 0.0045713 | (a) | 0.011428 | (e) | 0.0045713 | (a) | 0.011428 | (e) | 0.0007099 | (a) | 0.0017748 | (e) | 0.0007099 | (a) | 0.0017748 | (e) | 0.0014384 | (a) | 0.003596 | (e) | 0.0006014 | (a) | 0.0015035 | (e)
| Mercury and Compounds | 7439-97-6 | 0.002 |  | 0.0022702 | (a) | 0.0056755 | (e) | 0.0022702 | (a) | 0.0056755 | (e) | 0.0022702 | (a) | 0.0056755 | (e) | 0.0022702 | (a) | 0.0056755 | (e) | 0.0017942 | (a) | 0.0044855 | (e) | 0.0017942 | (a) | 0.0044855 | (e) | 0.0017942 | (a) | 0.0044855 | (e) | 0.00246 | (a) | 0.00615 | (e) | 0.00246 | (a) | 0.00615 | (e) | 0.00275 | (a) | 0.006875 | (e) | 0.002908 | (a) | 0.00727 | (e) | 0.0029492 | (a) | 0.007373 | (e) | 0.0029492 | (a) | 0.007373 | (e) | 0.0029492 | (a) | 0.007373 | (e) | 0.0029492 | (a) | 0.007373 | (e) | 0.0029492 | (a) | 0.007373 | (e) | 0.0029492 | (a) | 0.007373 | (e) | 0.000458 | (a) | 0.001145 | (e) | 0.000458 | (a) | 0.001145 | (e) | 0.000928 | (a) | 0.00232 | (e) | 0.000388 | (a) | 0.00097 | (e)
| Nickel and Compounds | 7440-02-0 | 0.0039 |  | 0.0044269 | (a) | 0.011067 | (e) | 0.0044269 | (a) | 0.011067 | (e) | 0.0044269 | (a) | 0.011067 | (e) | 0.0044269 | (a) | 0.011067 | (e) | 0.0034987 | (a) | 0.0087467 | (e) | 0.0034987 | (a) | 0.0087467 | (e) | 0.0034987 | (a) | 0.0087467 | (e) | 0.004797 | (a) | 0.011992 | (e) | 0.004797 | (a) | 0.011992 | (e) | 0.0053625 | (a) | 0.013406 | (e) | 0.0056706 | (a) | 0.014177 | (e) | 0.0057509 | (a) | 0.014377 | (e) | 0.0057509 | (a) | 0.014377 | (e) | 0.0057509 | (a) | 0.014377 | (e) | 0.0057509 | (a) | 0.014377 | (e) | 0.0057509 | (a) | 0.014377 | (e) | 0.0057509 | (a) | 0.014377 | (e) | 0.0008931 | (a) | 0.0022327 | (e) | 0.0008931 | (a) | 0.0022327 | (e) | 0.0018096 | (a) | 0.004524 | (e) | 0.0007566 | (a) | 0.0018915 | (e)
| Phosphorus and compounds | 504 | 0.008404 |  | 0.0095394 | (a) | 0.023848 | (e) | 0.0095394 | (a) | 0.023848 | (e) | 0.0095394 | (a) | 0.023848 | (e) | 0.0095394 | (a) | 0.023848 | (e) | 0.0075392 | (a) | 0.018848 | (e) | 0.0075392 | (a) | 0.018848 | (e) | 0.0075392 | (a) | 0.018848 | (e) | 0.010337 | (a) | 0.025842 | (e) | 0.010337 | (a) | 0.025842 | (e) | 0.011555 | (a) | 0.028889 | (e) | 0.012219 | (a) | 0.030548 | (e) | 0.012393 | (a) | 0.030981 | (e) | 0.012393 | (a) | 0.030981 | (e) | 0.012393 | (a) | 0.030981 | (e) | 0.012393 | (a) | 0.030981 | (e) | 0.012393 | (a) | 0.030981 | (e) | 0.012393 | (a) | 0.030981 | (e) | 0.0019245 | (a) | 0.0048113 | (e) | 0.0019245 | (a) | 0.0048113 | (e) | 0.0038994 | (a) | 0.0097486 | (e) | 0.0016304 | (a) | 0.0040759 | (e)
| Selenium and Compounds | 7782-49-2 | 0.0022 |  | 0.0024972 | (a) | 0.0062431 | (e) | 0.0024972 | (a) | 0.0062431 | (e) | 0.0024972 | (a) | 0.0062431 | (e) | 0.0024972 | (a) | 0.0062431 | (e) | 0.0019736 | (a) | 0.004934 | (e) | 0.0019736 | (a) | 0.004934 | (e) | 0.0019736 | (a) | 0.004934 | (e) | 0.002706 | (a) | 0.006765 | (e) | 0.002706 | (a) | 0.006765 | (e) | 0.003025 | (a) | 0.0075625 | (e) | 0.0031988 | (a) | 0.007997 | (e) | 0.0032441 | (a) | 0.0081103 | (e) | 0.0032441 | (a) | 0.0081103 | (e) | 0.0032441 | (a) | 0.0081103 | (e) | 0.0032441 | (a) | 0.0081103 | (e) | 0.0032441 | (a) | 0.0081103 | (e) | 0.0032441 | (a) | 0.0081103 | (e) | 0.0005038 | (a) | 0.0012595 | (e) | 0.0005038 | (a) | 0.0012595 | (e) | 0.0010208 | (a) | 0.002552 | (e) | 0.0004268 | (a) | 0.001067 | (e)
| Silver and compounds | 7440-22-4 | 4.8013e-05 |  | 5.45e-05 | (a) | 0.00013625 | (e) | 5.45e-05 | (a) | 0.00013625 | (e) | 5.45e-05 | (a) | 0.00013625 | (e) | 5.45e-05 | (a) | 0.00013625 | (e) | 4.3072e-05 | (a) | 0.00010768 | (e) | 4.3072e-05 | (a) | 0.00010768 | (e) | 4.3072e-05 | (a) | 0.00010768 | (e) | 5.9056e-05 | (a) | 0.00014764 | (e) | 5.9056e-05 | (a) | 0.00014764 | (e) | 6.6018e-05 | (a) | 0.00016504 | (e) | 6.9811e-05 | (a) | 0.00017453 | (e) | 7.08e-05 | (a) | 0.000177 | (e) | 7.08e-05 | (a) | 0.000177 | (e) | 7.08e-05 | (a) | 0.000177 | (e) | 7.08e-05 | (a) | 0.000177 | (e) | 7.08e-05 | (a) | 0.000177 | (e) | 7.08e-05 | (a) | 0.000177 | (e) | 1.0995e-05 | (a) | 2.7487e-05 | (e) | 1.0995e-05 | (a) | 2.7487e-05 | (e) | 2.2278e-05 | (a) | 5.5695e-05 | (e) | 9.3145e-06 | (a) | 2.3286e-05 | (e)
| Thallium and compounds | 7440-28-0 | 0.00024009 |  | 0.00027253 | (a) | 0.00068133 | (e) | 0.00027253 | (a) | 0.00068133 | (e) | 0.00027253 | (a) | 0.00068133 | (e) | 0.00027253 | (a) | 0.00068133 | (e) | 0.00021539 | (a) | 0.00053847 | (e) | 0.00021539 | (a) | 0.00053847 | (e) | 0.00021539 | (a) | 0.00053847 | (e) | 0.00029532 | (a) | 0.00073829 | (e) | 0.00029532 | (a) | 0.00073829 | (e) | 0.00033013 | (a) | 0.00082532 | (e) | 0.0003491 | (a) | 0.00087274 | (e) | 0.00035404 | (a) | 0.00088511 | (e) | 0.00035404 | (a) | 0.00088511 | (e) | 0.00035404 | (a) | 0.00088511 | (e) | 0.00035404 | (a) | 0.00088511 | (e) | 0.00035404 | (a) | 0.00088511 | (e) | 0.00035404 | (a) | 0.00088511 | (e) | 5.4981e-05 | (a) | 0.00013745 | (e) | 5.4981e-05 | (a) | 0.00013745 | (e) | 0.0001114 | (a) | 0.00027851 | (e) | 4.6578e-05 | (a) | 0.00011645 | (e)
| Zinc and compounds | 7440-66-6 | 0.0052262 |  | 0.0059322 | (a) | 0.014831 | (e) | 0.0059322 | (a) | 0.014831 | (e) | 0.0059322 | (a) | 0.014831 | (e) | 0.0059322 | (a) | 0.014831 | (e) | 0.0046884 | (a) | 0.011721 | (e) | 0.0046884 | (a) | 0.011721 | (e) | 0.0046884 | (a) | 0.011721 | (e) | 0.0064282 | (a) | 0.01607 | (e) | 0.0064282 | (a) | 0.01607 | (e) | 0.007186 | (a) | 0.017965 | (e) | 0.0075989 | (a) | 0.018997 | (e) | 0.0077065 | (a) | 0.019266 | (e) | 0.0077065 | (a) | 0.019266 | (e) | 0.0077065 | (a) | 0.019266 | (e) | 0.0077065 | (a) | 0.019266 | (e) | 0.0077065 | (a) | 0.019266 | (e) | 0.0077065 | (a) | 0.019266 | (e) | 0.0011968 | (a) | 0.002992 | (e) | 0.0011968 | (a) | 0.002992 | (e) | 0.0024249 | (a) | 0.0060624 | (e) | 0.0010139 | (a) | 0.0025347 | (e)
ORGANIC COMPOUNDS
| 1,3-Butadiene | 106-99-0 | 0.2174 |  | 0.24813 | (b) | 0.63321 | (f) | 0.24813 | (b) | 0.63321 | (f) | 0.24813 | (b) | 0.63321 | (f) | 0.24813 | (b) | 0.63321 | (f) | 0.1961 | (b) | 0.50045 | (f) | 0.1961 | (b) | 0.50045 | (f) | 0.1961 | (b) | 0.50045 | (f) | 0.26887 | (b) | 0.68615 | (f) | 0.26887 | (b) | 0.68615 | (f) | 0.30057 | (b) | 0.76704 | (f) | 0.31784 | (b) | 0.81111 | (f) | 0.32234 | (b) | 0.8226 | (f) | 0.32234 | (b) | 0.8226 | (f) | 0.32234 | (b) | 0.8226 | (f) | 0.32234 | (b) | 0.8226 | (f) | 0.32234 | (b) | 0.8226 | (f) | 0.32234 | (b) | 0.8226 | (f) | 0.050058 | (b) | 0.12775 | (f) | 0.050058 | (b) | 0.12775 | (f) | 0.10143 | (b) | 0.25884 | (f) | 0.042408 | (b) | 0.10822 | (f)
| Acetaldehyde | 75-07-0 | 0.7833 |  | 0.89401 | (b) | 2.2815 | (f) | 0.89401 | (b) | 2.2815 | (f) | 0.89401 | (b) | 2.2815 | (f) | 0.89401 | (b) | 2.2815 | (f) | 0.70656 | (b) | 1.8031 | (f) | 0.70656 | (b) | 1.8031 | (f) | 0.70656 | (b) | 1.8031 | (f) | 0.96876 | (b) | 2.4722 | (f) | 0.96876 | (b) | 2.4722 | (f) | 1.083 | (b) | 2.7637 | (f) | 1.1452 | (b) | 2.9225 | (f) | 1.1614 | (b) | 2.9639 | (f) | 1.1614 | (b) | 2.9639 | (f) | 1.1614 | (b) | 2.9639 | (f) | 1.1614 | (b) | 2.9639 | (f) | 1.1614 | (b) | 2.9639 | (f) | 1.1614 | (b) | 2.9639 | (f) | 0.18036 | (b) | 0.46028 | (f) | 0.18036 | (b) | 0.46028 | (f) | 0.36545 | (b) | 0.93262 | (f) | 0.1528 | (b) | 0.38993 | (f)
| Acrolein | 107-02-8 | 0.0339 |  | 0.038692 | (b) | 0.098739 | (f) | 0.038692 | (b) | 0.098739 | (f) | 0.038692 | (b) | 0.098739 | (f) | 0.038692 | (b) | 0.098739 | (f) | 0.030579 | (b) | 0.078036 | (f) | 0.030579 | (b) | 0.078036 | (f) | 0.030579 | (b) | 0.078036 | (f) | 0.041926 | (b) | 0.10699 | (f) | 0.041926 | (b) | 0.10699 | (f) | 0.046869 | (b) | 0.11961 | (f) | 0.049562 | (b) | 0.12648 | (f) | 0.050264 | (b) | 0.12827 | (f) | 0.050264 | (b) | 0.12827 | (f) | 0.050264 | (b) | 0.12827 | (f) | 0.050264 | (b) | 0.12827 | (f) | 0.050264 | (b) | 0.12827 | (f) | 0.050264 | (b) | 0.12827 | (f) | 0.0078058 | (b) | 0.01992 | (f) | 0.0078058 | (b) | 0.01992 | (f) | 0.015816 | (b) | 0.040362 | (f) | 0.0066128 | (b) | 0.016876 | (f)
| Benzene | 71-43-2 | 0.1863 |  | 0.21263 | (b) | 0.54263 | (f) | 0.21263 | (b) | 0.54263 | (f) | 0.21263 | (b) | 0.54263 | (f) | 0.21263 | (b) | 0.54263 | (f) | 0.16805 | (b) | 0.42885 | (f) | 0.16805 | (b) | 0.42885 | (f) | 0.16805 | (b) | 0.42885 | (f) | 0.23041 | (b) | 0.588 | (f) | 0.23041 | (b) | 0.588 | (f) | 0.25757 | (b) | 0.65731 | (f) | 0.27237 | (b) | 0.69508 | (f) | 0.27623 | (b) | 0.70493 | (f) | 0.27623 | (b) | 0.70493 | (f) | 0.27623 | (b) | 0.70493 | (f) | 0.27623 | (b) | 0.70493 | (f) | 0.27623 | (b) | 0.70493 | (f) | 0.27623 | (b) | 0.70493 | (f) | 0.042897 | (b) | 0.10947 | (f) | 0.042897 | (b) | 0.10947 | (f) | 0.086919 | (b) | 0.22181 | (f) | 0.036341 | (b) | 0.092741 | (f)
| Chlorobenzene | 108-90-7 | 0.0002 |  | 0.00022827 | (b) | 0.00058253 | (f) | 0.00022827 | (b) | 0.00058253 | (f) | 0.00022827 | (b) | 0.00058253 | (f) | 0.00022827 | (b) | 0.00058253 | (f) | 0.00018041 | (b) | 0.00046039 | (f) | 0.00018041 | (b) | 0.00046039 | (f) | 0.00018041 | (b) | 0.00046039 | (f) | 0.00024735 | (b) | 0.00063124 | (f) | 0.00024735 | (b) | 0.00063124 | (f) | 0.00027651 | (b) | 0.00070565 | (f) | 0.0002924 | (b) | 0.00074619 | (f) | 0.00029654 | (b) | 0.00075676 | (f) | 0.00029654 | (b) | 0.00075676 | (f) | 0.00029654 | (b) | 0.00075676 | (f) | 0.00029654 | (b) | 0.00075676 | (f) | 0.00029654 | (b) | 0.00075676 | (f) | 0.00029654 | (b) | 0.00075676 | (f) | 4.6052e-05 | (b) | 0.00011752 | (f) | 4.6052e-05 | (b) | 0.00011752 | (f) | 9.331e-05 | (b) | 0.00023812 | (f) | 3.9013e-05 | (b) | 9.9561e-05 | (f)
| Ethylbenzene | 100-41-4 | 0.0109 |  | 0.012441 | (b) | 0.031748 | (f) | 0.012441 | (b) | 0.031748 | (f) | 0.012441 | (b) | 0.031748 | (f) | 0.012441 | (b) | 0.031748 | (f) | 0.0098322 | (b) | 0.025091 | (f) | 0.0098322 | (b) | 0.025091 | (f) | 0.0098322 | (b) | 0.025091 | (f) | 0.013481 | (b) | 0.034402 | (f) | 0.013481 | (b) | 0.034402 | (f) | 0.01507 | (b) | 0.038458 | (f) | 0.015936 | (b) | 0.040668 | (f) | 0.016162 | (b) | 0.041244 | (f) | 0.016162 | (b) | 0.041244 | (f) | 0.016162 | (b) | 0.041244 | (f) | 0.016162 | (b) | 0.041244 | (f) | 0.016162 | (b) | 0.041244 | (f) | 0.016162 | (b) | 0.041244 | (f) | 0.0025098 | (b) | 0.006405 | (f) | 0.0025098 | (b) | 0.006405 | (f) | 0.0050854 | (b) | 0.012978 | (f) | 0.0021262 | (b) | 0.0054261 | (f)
| Formaldehyde | 50-00-0 | 1.7261 |  | 1.9717 | (b) | 5.0471 | (f) | 1.9717 | (b) | 5.0471 | (f) | 1.9717 | (b) | 5.0471 | (f) | 1.9717 | (b) | 5.0471 | (f) | 1.5583 | (b) | 3.9889 | (f) | 1.5583 | (b) | 3.9889 | (f) | 1.5583 | (b) | 3.9889 | (f) | 2.1365 | (b) | 5.4691 | (f) | 2.1365 | (b) | 5.4691 | (f) | 2.3884 | (b) | 6.1138 | (f) | 2.5256 | (b) | 6.4651 | (f) | 2.5614 | (b) | 6.5567 | (f) | 2.5614 | (b) | 6.5567 | (f) | 2.5614 | (b) | 6.5567 | (f) | 2.5614 | (b) | 6.5567 | (f) | 2.5614 | (b) | 6.5567 | (f) | 2.5614 | (b) | 6.5567 | (f) | 0.39778 | (b) | 1.0182 | (f) | 0.39778 | (b) | 1.0182 | (f) | 0.80598 | (b) | 2.0631 | (f) | 0.33698 | (b) | 0.86261 | (f)
| Hexane | 110-54-3 | 0.0269 |  | 0.030702 | (b) | 0.078351 | (f) | 0.030702 | (b) | 0.078351 | (f) | 0.030702 | (b) | 0.078351 | (f) | 0.030702 | (b) | 0.078351 | (f) | 0.024265 | (b) | 0.061923 | (f) | 0.024265 | (b) | 0.061923 | (f) | 0.024265 | (b) | 0.061923 | (f) | 0.033269 | (b) | 0.084901 | (f) | 0.033269 | (b) | 0.084901 | (f) | 0.037191 | (b) | 0.09491 | (f) | 0.039328 | (b) | 0.10036 | (f) | 0.039885 | (b) | 0.10178 | (f) | 0.039885 | (b) | 0.10178 | (f) | 0.039885 | (b) | 0.10178 | (f) | 0.039885 | (b) | 0.10178 | (f) | 0.039885 | (b) | 0.10178 | (f) | 0.039885 | (b) | 0.10178 | (f) | 0.006194 | (b) | 0.015807 | (f) | 0.006194 | (b) | 0.015807 | (f) | 0.01255 | (b) | 0.032028 | (f) | 0.0052473 | (b) | 0.013391 | (f)
| Propylene | 115-07-1 | 0.47 |  | 0.53643 | (b) | 1.369 | (f) | 0.53643 | (b) | 1.369 | (f) | 0.53643 | (b) | 1.369 | (f) | 0.53643 | (b) | 1.369 | (f) | 0.42396 | (b) | 1.0819 | (f) | 0.42396 | (b) | 1.0819 | (f) | 0.42396 | (b) | 1.0819 | (f) | 0.58128 | (b) | 1.4834 | (f) | 0.58128 | (b) | 1.4834 | (f) | 0.6498 | (b) | 1.6583 | (f) | 0.68714 | (b) | 1.7536 | (f) | 0.69687 | (b) | 1.7784 | (f) | 0.69687 | (b) | 1.7784 | (f) | 0.69687 | (b) | 1.7784 | (f) | 0.69687 | (b) | 1.7784 | (f) | 0.69687 | (b) | 1.7784 | (f) | 0.69687 | (b) | 1.7784 | (f) | 0.10822 | (b) | 0.27618 | (f) | 0.10822 | (b) | 0.27618 | (f) | 0.21928 | (b) | 0.55959 | (f) | 0.091681 | (b) | 0.23397 | (f)
| Toluene | 108-88-3 | 0.1054 |  | 0.1203 | (b) | 0.307 | (f) | 0.1203 | (b) | 0.307 | (f) | 0.1203 | (b) | 0.307 | (f) | 0.1203 | (b) | 0.307 | (f) | 0.095074 | (b) | 0.24263 | (f) | 0.095074 | (b) | 0.24263 | (f) | 0.095074 | (b) | 0.24263 | (f) | 0.13036 | (b) | 0.33266 | (f) | 0.13036 | (b) | 0.33266 | (f) | 0.14572 | (b) | 0.37188 | (f) | 0.15409 | (b) | 0.39324 | (f) | 0.15628 | (b) | 0.39882 | (f) | 0.15628 | (b) | 0.39882 | (f) | 0.15628 | (b) | 0.39882 | (f) | 0.15628 | (b) | 0.39882 | (f) | 0.15628 | (b) | 0.39882 | (f) | 0.15628 | (b) | 0.39882 | (f) | 0.024269 | (b) | 0.061935 | (f) | 0.024269 | (b) | 0.061935 | (f) | 0.049175 | (b) | 0.12549 | (f) | 0.02056 | (b) | 0.052469 | (f)
| Xylene (mixed isomers) | 1330-20-7 | 0.0424 |  | 0.048393 | (b) | 0.1235 | (f) | 0.048393 | (b) | 0.1235 | (f) | 0.048393 | (b) | 0.1235 | (f) | 0.048393 | (b) | 0.1235 | (f) | 0.038246 | (b) | 0.097603 | (f) | 0.038246 | (b) | 0.097603 | (f) | 0.038246 | (b) | 0.097603 | (f) | 0.052439 | (b) | 0.13382 | (f) | 0.052439 | (b) | 0.13382 | (f) | 0.058621 | (b) | 0.1496 | (f) | 0.061989 | (b) | 0.15819 | (f) | 0.062867 | (b) | 0.16043 | (f) | 0.062867 | (b) | 0.16043 | (f) | 0.062867 | (b) | 0.16043 | (f) | 0.062867 | (b) | 0.16043 | (f) | 0.062867 | (b) | 0.16043 | (f) | 0.062867 | (b) | 0.16043 | (f) | 0.009763 | (b) | 0.024915 | (f) | 0.009763 | (b) | 0.024915 | (f) | 0.019782 | (b) | 0.050482 | (f) | 0.0082708 | (b) | 0.021107 | (f)
INORGANIC COMPOUNDS
| Ammonia | 7664-41-7 | 0.8 |  | 0.91307 | (b) | 2.3301 | (f) | 0.91307 | (b) | 2.3301 | (f) | 0.91307 | (b) | 2.3301 | (f) | 0.91307 | (b) | 2.3301 | (f) | 0.72163 | (b) | 1.8416 | (f) | 0.72163 | (b) | 1.8416 | (f) | 0.72163 | (b) | 1.8416 | (f) | 0.98941 | (b) | 2.5249 | (f) | 0.98941 | (b) | 2.5249 | (f) | 1.106 | (b) | 2.8226 | (f) | 1.1696 | (b) | 2.9848 | (f) | 1.1862 | (b) | 3.0271 | (f) | 1.1862 | (b) | 3.0271 | (f) | 1.1862 | (b) | 3.0271 | (f) | 1.1862 | (b) | 3.0271 | (f) | 1.1862 | (b) | 3.0271 | (f) | 1.1862 | (b) | 3.0271 | (f) | 0.18421 | (b) | 0.47009 | (f) | 0.18421 | (b) | 0.47009 | (f) | 0.37324 | (b) | 0.9525 | (f) | 0.15605 | (b) | 0.39824 | (f)
| Hydrochloric Acid | 7647-01-0 | 0.1863 |  | 0.21263 | (b) | 0.54263 | (f) | 0.21263 | (b) | 0.54263 | (f) | 0.21263 | (b) | 0.54263 | (f) | 0.21263 | (b) | 0.54263 | (f) | 0.16805 | (b) | 0.42885 | (f) | 0.16805 | (b) | 0.42885 | (f) | 0.16805 | (b) | 0.42885 | (f) | 0.23041 | (b) | 0.588 | (f) | 0.23041 | (b) | 0.588 | (f) | 0.25757 | (b) | 0.65731 | (f) | 0.27237 | (b) | 0.69508 | (f) | 0.27623 | (b) | 0.70493 | (f) | 0.27623 | (b) | 0.70493 | (f) | 0.27623 | (b) | 0.70493 | (f) | 0.27623 | (b) | 0.70493 | (f) | 0.27623 | (b) | 0.70493 | (f) | 0.27623 | (b) | 0.70493 | (f) | 0.042897 | (b) | 0.10947 | (f) | 0.042897 | (b) | 0.10947 | (f) | 0.086919 | (b) | 0.22181 | (f) | 0.036341 | (b) | 0.092741 | (f)
POLYCYCLIC AROMATIC HYDROCARBONS (PAH)
| Benzo[a]pyrene | 50-32-8 | 3.52e-05 |  | 4.0175e-05 | (b) | 0.00010253 | (f) | 4.0175e-05 | (b) | 0.00010253 | (f) | 4.0175e-05 | (b) | 0.00010253 | (f) | 4.0175e-05 | (b) | 0.00010253 | (f) | 3.1752e-05 | (b) | 8.1029e-05 | (f) | 3.1752e-05 | (b) | 8.1029e-05 | (f) | 3.1752e-05 | (b) | 8.1029e-05 | (f) | 4.3534e-05 | (b) | 0.0001111 | (f) | 4.3534e-05 | (b) | 0.0001111 | (f) | 4.8666e-05 | (b) | 0.00012419 | (f) | 5.1462e-05 | (b) | 0.00013133 | (f) | 5.2191e-05 | (b) | 0.00013319 | (f) | 5.2191e-05 | (b) | 0.00013319 | (f) | 5.2191e-05 | (b) | 0.00013319 | (f) | 5.2191e-05 | (b) | 0.00013319 | (f) | 5.2191e-05 | (b) | 0.00013319 | (f) | 5.2191e-05 | (b) | 0.00013319 | (f) | 8.1051e-06 | (b) | 2.0684e-05 | (f) | 8.1051e-06 | (b) | 2.0684e-05 | (f) | 1.6423e-05 | (b) | 4.191e-05 | (f) | 6.8664e-06 | (b) | 1.7523e-05 | (f)
| Naphthalene | 91-20-3 | 0.0197 |  | 0.022484 | (b) | 0.05738 | (f) | 0.022484 | (b) | 0.05738 | (f) | 0.022484 | (b) | 0.05738 | (f) | 0.022484 | (b) | 0.05738 | (f) | 0.01777 | (b) | 0.045349 | (f) | 0.01777 | (b) | 0.045349 | (f) | 0.01777 | (b) | 0.045349 | (f) | 0.024364 | (b) | 0.062177 | (f) | 0.024364 | (b) | 0.062177 | (f) | 0.027236 | (b) | 0.069507 | (f) | 0.028801 | (b) | 0.0735 | (f) | 0.029209 | (b) | 0.074541 | (f) | 0.029209 | (b) | 0.074541 | (f) | 0.029209 | (b) | 0.074541 | (f) | 0.029209 | (b) | 0.074541 | (f) | 0.029209 | (b) | 0.074541 | (f) | 0.029209 | (b) | 0.074541 | (f) | 0.0045361 | (b) | 0.011576 | (f) | 0.0045361 | (b) | 0.011576 | (f) | 0.0091911 | (b) | 0.023455 | (f) | 0.0038428 | (b) | 0.0098067 | (f)
| PAH | 401 | 0.0362 |  | 0.041317 | (b) | 0.10544 | (f) | 0.041317 | (b) | 0.10544 | (f) | 0.041317 | (b) | 0.10544 | (f) | 0.041317 | (b) | 0.10544 | (f) | 0.032654 | (b) | 0.083331 | (f) | 0.032654 | (b) | 0.083331 | (f) | 0.032654 | (b) | 0.083331 | (f) | 0.044771 | (b) | 0.11425 | (f) | 0.044771 | (b) | 0.11425 | (f) | 0.050049 | (b) | 0.12772 | (f) | 0.052924 | (b) | 0.13506 | (f) | 0.053674 | (b) | 0.13697 | (f) | 0.053674 | (b) | 0.13697 | (f) | 0.053674 | (b) | 0.13697 | (f) | 0.053674 | (b) | 0.13697 | (f) | 0.053674 | (b) | 0.13697 | (f) | 0.053674 | (b) | 0.13697 | (f) | 0.0083354 | (b) | 0.021272 | (f) | 0.0083354 | (b) | 0.021272 | (f) | 0.016889 | (b) | 0.043101 | (f) | 0.0070614 | (b) | 0.018021 | (f)
DIESEL PARTICULATE MATTER (DPM)
| DPM | 200 | 33.5 |  | 38.235 | (b) | 97.5743 | (f) | 38.235 | (b) | 97.5743 | (f) | 38.235 | (b) | 97.5743 | (f) | 38.235 | (b) | 97.5743 | (f) | 30.2181 | (b) | 77.1156 | (f) | 30.2181 | (b) | 77.1156 | (f) | 30.2181 | (b) | 77.1156 | (f) | 41.4316 | (b) | 105.732 | (f) | 41.4316 | (b) | 105.732 | (f) | 46.3158 | (b) | 118.1964 | (f) | 48.9769 | (b) | 124.9873 | (f) | 49.6708 | (b) | 126.7581 | (f) | 49.6708 | (b) | 126.7581 | (f) | 49.6708 | (b) | 126.7581 | (f) | 49.6708 | (b) | 126.7581 | (f) | 49.6708 | (b) | 126.7581 | (f) | 49.6708 | (b) | 126.7581 | (f) | 7.7137 | (b) | 19.6851 | (f) | 7.7137 | (b) | 19.6851 | (f) | 15.6295 | (b) | 39.8859 | (f) | 6.5347 | (b) | 16.6764 | (f)
Notes
DPF = Diesel Particulate Filter; HAP = Hazardous Air Pollutant; Mgal = 1,000 gallons; TAC = Toxic Air Contaminant.
(a) | Daily emissions estimate (lb/day) = ([emission factor {lb/Mgal}] x [fuel consumption {gal/hr}] x [daily hours of operation {hrs/day}] x [Mgal/1,000 gal]
(b) | Daily emissions estimate (lb/day) = (emission factor [lb/Mgal]) x (fuel consumption [gal/hr]) x (daily hours of operation [hrs/day]) x (Mgal/1,000 gal) | [14 empty] | (c), (d)
| + (cold start emissions [lb/minute]) x (number of cold starts per day) - (emissions per minute, normal operation [lb/minute]) x (number of cold starts per day) | [14 empty] | (3)
|  | Cold start adjustment factor = | 4.3 | (4)
|  | Cold start adjustment factor (formaldehyde) = | 4.8 | (4)
|  | Number of cold starts per day = | 1 | (5)
(c) | Cold start emissions (lb/minute) = (emission factor [lb/Mgal]) x [Mgal/1,000 gal] x (cold start adjustment factor) x (hourly fuel consumption [gal/hr]) / 60
(d) | Emissions per minute, normal operation (lb/minute) = (emission factor [lb/Mgal]) x (hourly fuel consumption [gal/hr]) / 60
(e) | Annual emissions estimate (lb/yr) = ([emission factor {lb/Mgal}] x [fuel consumption {gal/hr}] x [annual hours of operation {hrs/yr}] x [Mgal/1,000 gal]
(f) | Annual emissions estimate (lb/yr) = (emission factor [lb/Mgal]) x (fuel consumption [gal/hr]) x (annual hours of operation [hrs/yr]) x (Mgal/1,000 gal) | [14 empty] | (c), (d)
| + (cold start emissions [lb/minute]) x (number of cold starts per year) - (emissions per minute, normal operation [lb/minute]) x (number of cold starts per year) | [14 empty] | (3)
|  | Cold start adjustment factor = | 4.3 | (4)
|  | Cold start adjustment factor (formaldehyde) = | 4.8 | (4)
|  | Number of cold starts per year = | 12 | (5)
References
(1) | See Table 1, Input Emergency Generator Rates and Parameters
(2) | Emission Factors from the Oregon Department of Environmental Quality, AQ104B, diesel internal combustion, pre-2006, less than
750 hp. Ammonia emission factor assumes value for no SNCR or SCR control. DEQ reference CAO Diesel RICE (a).
(3) | Time allotted for cold stats was omitted from the daily/annual operating capacity in emission calculations. Cold start adjustments are not required for metals.
(4) | Cold start adjustment factors provided by the Oregon Department of Environmental Quality. All applicable pollutants, except
formaldehyde, share the same adjustment factor. Cold start adjustments are not required for metals.
(5) | Information provided by Intel based on one cold start per month per engine.

## EGENnoDPF_b_RONLER
Table 5
Emergency Generator—No DPF, Post 2006, > 750 hp TAC Emission Estimates—Ronler Acres
Intel Corporation
Emission Unit ID |  |  |  |  | RP1-GEN-2 |  |  |  | D1D-GEN-7 |  |  |  | RS6-GEN-2 |  |  |  | D1X-GEN-1A |  |  |  | D1X-GEN-1B |  |  |  | D1X-GEN-1C |  |  |  | D1X-GEN-2A |  |  |  | D1X-GEN-2B |  |  |  | D1X-GEN-2C |  |  |  | D1X-GEN-3A |  |  |  | D1X-GEN-3B |  |  |  | D1X-GEN-3C |  |  |  | D1X-GEN-4A |  |  |  | D1X-GEN-4B |  |  |  | D1X-GEN-5C
Fuel Consumption (gal/hr) |  |  |  | (1) | 145.4 |  |  |  | 147.5 |  |  |  | 147.5 |  |  |  | 176 |  |  |  | 172.1 |  |  |  | 176 |  |  |  | 176 |  |  |  | 176 |  |  |  | 176 |  |  |  | 172.1 |  |  |  | 176 |  |  |  | 172.1 |  |  |  | 172.1 |  |  |  | 172.1 |  |  |  | 172.1
Daily Hours of Operation (hrs/day) |  |  |  | (1) | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10
Annual Hours of Operation (hrs/yr) |  |  |  | (1) | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25
Pollutant |  | CAS | Emission Factor (2) (lb/Mgal) |  | Emissions Estimate
[5 empty] | RP1-GEN-2 |  |  |  | D1D-GEN-7 |  |  |  | RS6-GEN-2 |  |  |  | D1X-GEN-1A |  |  |  | D1X-GEN-1B |  |  |  | D1X-GEN-1C |  |  |  | D1X-GEN-2A |  |  |  | D1X-GEN-2B |  |  |  | D1X-GEN-2C |  |  |  | D1X-GEN-3A |  |  |  | D1X-GEN-3B |  |  |  | D1X-GEN-3C |  |  |  | D1X-GEN-4A |  |  |  | D1X-GEN-4B |  |  |  | D1X-GEN-5C
[5 empty] | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr)
METALS
| Antimony and Compounds | 7440-36-0 | 0.00031819 |  | 0.00046264 | (a) | 0.0011566 | (e) | 0.00046933 | (a) | 0.0011733 | (e) | 0.00046933 | (a) | 0.0011733 | (e) | 0.00056001 | (a) | 0.0014 | (e) | 0.0005476 | (a) | 0.001369 | (e) | 0.00056001 | (a) | 0.0014 | (e) | 0.00056001 | (a) | 0.0014 | (e) | 0.00056001 | (a) | 0.0014 | (e) | 0.00056001 | (a) | 0.0014 | (e) | 0.0005476 | (a) | 0.001369 | (e) | 0.00056001 | (a) | 0.0014 | (e) | 0.0005476 | (a) | 0.001369 | (e) | 0.0005476 | (a) | 0.001369 | (e) | 0.0005476 | (a) | 0.001369 | (e) | 0.0005476 | (a) | 0.001369 | (e)
| Arsenic and Compounds | 7440-38-2 | 0.00027685 |  | 0.00040254 | (a) | 0.0010064 | (e) | 0.00040836 | (a) | 0.0010209 | (e) | 0.00040836 | (a) | 0.0010209 | (e) | 0.00048726 | (a) | 0.0012182 | (e) | 0.00047646 | (a) | 0.0011912 | (e) | 0.00048726 | (a) | 0.0012182 | (e) | 0.00048726 | (a) | 0.0012182 | (e) | 0.00048726 | (a) | 0.0012182 | (e) | 0.00048726 | (a) | 0.0012182 | (e) | 0.00047646 | (a) | 0.0011912 | (e) | 0.00048726 | (a) | 0.0012182 | (e) | 0.00047646 | (a) | 0.0011912 | (e) | 0.00047646 | (a) | 0.0011912 | (e) | 0.00047646 | (a) | 0.0011912 | (e) | 0.00047646 | (a) | 0.0011912 | (e)
| Barium and Compounds | 7440-39-3 | 0.00037389 |  | 0.00054364 | (a) | 0.0013591 | (e) | 0.00055149 | (a) | 0.0013787 | (e) | 0.00055149 | (a) | 0.0013787 | (e) | 0.00065805 | (a) | 0.0016451 | (e) | 0.00064347 | (a) | 0.0016087 | (e) | 0.00065805 | (a) | 0.0016451 | (e) | 0.00065805 | (a) | 0.0016451 | (e) | 0.00065805 | (a) | 0.0016451 | (e) | 0.00065805 | (a) | 0.0016451 | (e) | 0.00064347 | (a) | 0.0016087 | (e) | 0.00065805 | (a) | 0.0016451 | (e) | 0.00064347 | (a) | 0.0016087 | (e) | 0.00064347 | (a) | 0.0016087 | (e) | 0.00064347 | (a) | 0.0016087 | (e) | 0.00064347 | (a) | 0.0016087 | (e)
| Beryllium and compounds | 7440-41-7 | 4.7708e-06 |  | 6.9368e-06 | (a) | 1.7342e-05 | (e) | 7.037e-06 | (a) | 1.7592e-05 | (e) | 7.037e-06 | (a) | 1.7592e-05 | (e) | 8.3967e-06 | (a) | 2.0992e-05 | (e) | 8.2106e-06 | (a) | 2.0527e-05 | (e) | 8.3967e-06 | (a) | 2.0992e-05 | (e) | 8.3967e-06 | (a) | 2.0992e-05 | (e) | 8.3967e-06 | (a) | 2.0992e-05 | (e) | 8.3967e-06 | (a) | 2.0992e-05 | (e) | 8.2106e-06 | (a) | 2.0527e-05 | (e) | 8.3967e-06 | (a) | 2.0992e-05 | (e) | 8.2106e-06 | (a) | 2.0527e-05 | (e) | 8.2106e-06 | (a) | 2.0527e-05 | (e) | 8.2106e-06 | (a) | 2.0527e-05 | (e) | 8.2106e-06 | (a) | 2.0527e-05 | (e)
| Cadmium and Compounds | 7440-43-9 | 8.0778e-05 |  | 0.00011745 | (a) | 0.00029363 | (e) | 0.00011915 | (a) | 0.00029787 | (e) | 0.00011915 | (a) | 0.00029787 | (e) | 0.00014217 | (a) | 0.00035542 | (e) | 0.00013902 | (a) | 0.00034755 | (e) | 0.00014217 | (a) | 0.00035542 | (e) | 0.00014217 | (a) | 0.00035542 | (e) | 0.00014217 | (a) | 0.00035542 | (e) | 0.00014217 | (a) | 0.00035542 | (e) | 0.00013902 | (a) | 0.00034755 | (e) | 0.00014217 | (a) | 0.00035542 | (e) | 0.00013902 | (a) | 0.00034755 | (e) | 0.00013902 | (a) | 0.00034755 | (e) | 0.00013902 | (a) | 0.00034755 | (e) | 0.00013902 | (a) | 0.00034755 | (e)
| Chromium VI | 18540-29-9 | 6.3144e-05 |  | 9.1812e-05 | (a) | 0.00022953 | (e) | 9.3138e-05 | (a) | 0.00023285 | (e) | 9.3138e-05 | (a) | 0.00023285 | (e) | 0.00011113 | (a) | 0.00027784 | (e) | 0.00010867 | (a) | 0.00027168 | (e) | 0.00011113 | (a) | 0.00027784 | (e) | 0.00011113 | (a) | 0.00027784 | (e) | 0.00011113 | (a) | 0.00027784 | (e) | 0.00011113 | (a) | 0.00027784 | (e) | 0.00010867 | (a) | 0.00027168 | (e) | 0.00011113 | (a) | 0.00027784 | (e) | 0.00010867 | (a) | 0.00027168 | (e) | 0.00010867 | (a) | 0.00027168 | (e) | 0.00010867 | (a) | 0.00027168 | (e) | 0.00010867 | (a) | 0.00027168 | (e)
| Copper and Compounds | 7440-50-8 | 0.00050214 |  | 0.0007301 | (a) | 0.0018253 | (e) | 0.00074065 | (a) | 0.0018516 | (e) | 0.00074065 | (a) | 0.0018516 | (e) | 0.00088376 | (a) | 0.0022094 | (e) | 0.00086417 | (a) | 0.0021604 | (e) | 0.00088376 | (a) | 0.0022094 | (e) | 0.00088376 | (a) | 0.0022094 | (e) | 0.00088376 | (a) | 0.0022094 | (e) | 0.00088376 | (a) | 0.0022094 | (e) | 0.00086417 | (a) | 0.0021604 | (e) | 0.00088376 | (a) | 0.0022094 | (e) | 0.00086417 | (a) | 0.0021604 | (e) | 0.00086417 | (a) | 0.0021604 | (e) | 0.00086417 | (a) | 0.0021604 | (e) | 0.00086417 | (a) | 0.0021604 | (e)
| Cobalt and compounds | 7440-48-4 | 1.5751e-05 |  | 2.2902e-05 | (a) | 5.7255e-05 | (e) | 2.3233e-05 | (a) | 5.8082e-05 | (e) | 2.3233e-05 | (a) | 5.8082e-05 | (e) | 2.7722e-05 | (a) | 6.9305e-05 | (e) | 2.7108e-05 | (a) | 6.7769e-05 | (e) | 2.7722e-05 | (a) | 6.9305e-05 | (e) | 2.7722e-05 | (a) | 6.9305e-05 | (e) | 2.7722e-05 | (a) | 6.9305e-05 | (e) | 2.7722e-05 | (a) | 6.9305e-05 | (e) | 2.7108e-05 | (a) | 6.7769e-05 | (e) | 2.7722e-05 | (a) | 6.9305e-05 | (e) | 2.7108e-05 | (a) | 6.7769e-05 | (e) | 2.7108e-05 | (a) | 6.7769e-05 | (e) | 2.7108e-05 | (a) | 6.7769e-05 | (e) | 2.7108e-05 | (a) | 6.7769e-05 | (e)
| Lead and Compounds | 7439-92-1 | 0.00036367 |  | 0.00052878 | (a) | 0.0013219 | (e) | 0.00053642 | (a) | 0.001341 | (e) | 0.00053642 | (a) | 0.001341 | (e) | 0.00064006 | (a) | 0.0016002 | (e) | 0.00062588 | (a) | 0.0015647 | (e) | 0.00064006 | (a) | 0.0016002 | (e) | 0.00064006 | (a) | 0.0016002 | (e) | 0.00064006 | (a) | 0.0016002 | (e) | 0.00064006 | (a) | 0.0016002 | (e) | 0.00062588 | (a) | 0.0015647 | (e) | 0.00064006 | (a) | 0.0016002 | (e) | 0.00062588 | (a) | 0.0015647 | (e) | 0.00062588 | (a) | 0.0015647 | (e) | 0.00062588 | (a) | 0.0015647 | (e) | 0.00062588 | (a) | 0.0015647 | (e)
| Manganese and Compounds | 7439-96-5 | 0.00041991 |  | 0.00061055 | (a) | 0.0015264 | (e) | 0.00061937 | (a) | 0.0015484 | (e) | 0.00061937 | (a) | 0.0015484 | (e) | 0.00073905 | (a) | 0.0018476 | (e) | 0.00072267 | (a) | 0.0018067 | (e) | 0.00073905 | (a) | 0.0018476 | (e) | 0.00073905 | (a) | 0.0018476 | (e) | 0.00073905 | (a) | 0.0018476 | (e) | 0.00073905 | (a) | 0.0018476 | (e) | 0.00072267 | (a) | 0.0018067 | (e) | 0.00073905 | (a) | 0.0018476 | (e) | 0.00072267 | (a) | 0.0018067 | (e) | 0.00072267 | (a) | 0.0018067 | (e) | 0.00072267 | (a) | 0.0018067 | (e) | 0.00072267 | (a) | 0.0018067 | (e)
| Mercury and Compounds | 7439-97-6 | 1.5107e-05 |  | 2.1966e-05 | (a) | 5.4915e-05 | (e) | 2.2283e-05 | (a) | 5.5708e-05 | (e) | 2.2283e-05 | (a) | 5.5708e-05 | (e) | 2.6589e-05 | (a) | 6.6472e-05 | (e) | 2.6e-05 | (a) | 6.4999e-05 | (e) | 2.6589e-05 | (a) | 6.6472e-05 | (e) | 2.6589e-05 | (a) | 6.6472e-05 | (e) | 2.6589e-05 | (a) | 6.6472e-05 | (e) | 2.6589e-05 | (a) | 6.6472e-05 | (e) | 2.6e-05 | (a) | 6.4999e-05 | (e) | 2.6589e-05 | (a) | 6.6472e-05 | (e) | 2.6e-05 | (a) | 6.4999e-05 | (e) | 2.6e-05 | (a) | 6.4999e-05 | (e) | 2.6e-05 | (a) | 6.4999e-05 | (e) | 2.6e-05 | (a) | 6.4999e-05 | (e)
| Nickel and Compounds | 7440-02-0 | 0.00018223 |  | 0.00026496 | (a) | 0.0006624 | (e) | 0.00026879 | (a) | 0.00067197 | (e) | 0.00026879 | (a) | 0.00067197 | (e) | 0.00032072 | (a) | 0.00080181 | (e) | 0.00031362 | (a) | 0.00078404 | (e) | 0.00032072 | (a) | 0.00080181 | (e) | 0.00032072 | (a) | 0.00080181 | (e) | 0.00032072 | (a) | 0.00080181 | (e) | 0.00032072 | (a) | 0.00080181 | (e) | 0.00031362 | (a) | 0.00078404 | (e) | 0.00032072 | (a) | 0.00080181 | (e) | 0.00031362 | (a) | 0.00078404 | (e) | 0.00031362 | (a) | 0.00078404 | (e) | 0.00031362 | (a) | 0.00078404 | (e) | 0.00031362 | (a) | 0.00078404 | (e)
| Phosphorus and compounds | 504 | 0.008404 |  | 0.012219 | (a) | 0.030548 | (e) | 0.012396 | (a) | 0.03099 | (e) | 0.012396 | (a) | 0.03099 | (e) | 0.014791 | (a) | 0.036978 | (e) | 0.014463 | (a) | 0.036158 | (e) | 0.014791 | (a) | 0.036978 | (e) | 0.014791 | (a) | 0.036978 | (e) | 0.014791 | (a) | 0.036978 | (e) | 0.014791 | (a) | 0.036978 | (e) | 0.014463 | (a) | 0.036158 | (e) | 0.014791 | (a) | 0.036978 | (e) | 0.014463 | (a) | 0.036158 | (e) | 0.014463 | (a) | 0.036158 | (e) | 0.014463 | (a) | 0.036158 | (e) | 0.014463 | (a) | 0.036158 | (e)
| Selenium and Compounds | 7782-49-2 | 0.00037638 |  | 0.00054726 | (a) | 0.0013682 | (e) | 0.00055516 | (a) | 0.0013879 | (e) | 0.00055516 | (a) | 0.0013879 | (e) | 0.00066243 | (a) | 0.0016561 | (e) | 0.00064775 | (a) | 0.0016194 | (e) | 0.00066243 | (a) | 0.0016561 | (e) | 0.00066243 | (a) | 0.0016561 | (e) | 0.00066243 | (a) | 0.0016561 | (e) | 0.00066243 | (a) | 0.0016561 | (e) | 0.00064775 | (a) | 0.0016194 | (e) | 0.00066243 | (a) | 0.0016561 | (e) | 0.00064775 | (a) | 0.0016194 | (e) | 0.00064775 | (a) | 0.0016194 | (e) | 0.00064775 | (a) | 0.0016194 | (e) | 0.00064775 | (a) | 0.0016194 | (e)
| Silver and compounds | 7440-22-4 | 4.8013e-05 |  | 6.9811e-05 | (a) | 0.00017453 | (e) | 7.0819e-05 | (a) | 0.00017705 | (e) | 7.0819e-05 | (a) | 0.00017705 | (e) | 8.4503e-05 | (a) | 0.00021126 | (e) | 8.263e-05 | (a) | 0.00020658 | (e) | 8.4503e-05 | (a) | 0.00021126 | (e) | 8.4503e-05 | (a) | 0.00021126 | (e) | 8.4503e-05 | (a) | 0.00021126 | (e) | 8.4503e-05 | (a) | 0.00021126 | (e) | 8.263e-05 | (a) | 0.00020658 | (e) | 8.4503e-05 | (a) | 0.00021126 | (e) | 8.263e-05 | (a) | 0.00020658 | (e) | 8.263e-05 | (a) | 0.00020658 | (e) | 8.263e-05 | (a) | 0.00020658 | (e) | 8.263e-05 | (a) | 0.00020658 | (e)
| Thallium and compounds | 7440-28-0 | 0.00024009 |  | 0.0003491 | (a) | 0.00087274 | (e) | 0.00035414 | (a) | 0.00088535 | (e) | 0.00035414 | (a) | 0.00088535 | (e) | 0.00042256 | (a) | 0.0010564 | (e) | 0.0004132 | (a) | 0.001033 | (e) | 0.00042256 | (a) | 0.0010564 | (e) | 0.00042256 | (a) | 0.0010564 | (e) | 0.00042256 | (a) | 0.0010564 | (e) | 0.00042256 | (a) | 0.0010564 | (e) | 0.0004132 | (a) | 0.001033 | (e) | 0.00042256 | (a) | 0.0010564 | (e) | 0.0004132 | (a) | 0.001033 | (e) | 0.0004132 | (a) | 0.001033 | (e) | 0.0004132 | (a) | 0.001033 | (e) | 0.0004132 | (a) | 0.001033 | (e)
| Zinc and compounds | 7440-66-6 | 0.0052262 |  | 0.0075989 | (a) | 0.018997 | (e) | 0.0077086 | (a) | 0.019272 | (e) | 0.0077086 | (a) | 0.019272 | (e) | 0.0091981 | (a) | 0.022995 | (e) | 0.0089943 | (a) | 0.022486 | (e) | 0.0091981 | (a) | 0.022995 | (e) | 0.0091981 | (a) | 0.022995 | (e) | 0.0091981 | (a) | 0.022995 | (e) | 0.0091981 | (a) | 0.022995 | (e) | 0.0089943 | (a) | 0.022486 | (e) | 0.0091981 | (a) | 0.022995 | (e) | 0.0089943 | (a) | 0.022486 | (e) | 0.0089943 | (a) | 0.022486 | (e) | 0.0089943 | (a) | 0.022486 | (e) | 0.0089943 | (a) | 0.022486 | (e)
ORGANIC COMPOUNDS
| 1,3-Butadiene | 106-99-0 | 0.2174 |  | 0.31784 | (b) | 0.81111 | (f) | 0.32243 | (b) | 0.82283 | (f) | 0.32243 | (b) | 0.82283 | (f) | 0.38473 | (b) | 0.98181 | (f) | 0.3762 | (b) | 0.96006 | (f) | 0.38473 | (b) | 0.98181 | (f) | 0.38473 | (b) | 0.98181 | (f) | 0.38473 | (b) | 0.98181 | (f) | 0.38473 | (b) | 0.98181 | (f) | 0.3762 | (b) | 0.96006 | (f) | 0.38473 | (b) | 0.98181 | (f) | 0.3762 | (b) | 0.96006 | (f) | 0.3762 | (b) | 0.96006 | (f) | 0.3762 | (b) | 0.96006 | (f) | 0.3762 | (b) | 0.96006 | (f)
| 2-Methyl naphthalene | 91-57-6 | 0.012298 |  | 0.01798 | (b) | 0.045883 | (f) | 0.018239 | (b) | 0.046546 | (f) | 0.018239 | (b) | 0.046546 | (f) | 0.021763 | (b) | 0.055539 | (f) | 0.021281 | (b) | 0.054309 | (f) | 0.021763 | (b) | 0.055539 | (f) | 0.021763 | (b) | 0.055539 | (f) | 0.021763 | (b) | 0.055539 | (f) | 0.021763 | (b) | 0.055539 | (f) | 0.021281 | (b) | 0.054309 | (f) | 0.021763 | (b) | 0.055539 | (f) | 0.021281 | (b) | 0.054309 | (f) | 0.021281 | (b) | 0.054309 | (f) | 0.021281 | (b) | 0.054309 | (f) | 0.021281 | (b) | 0.054309 | (f)
| Acenaphthene | 83-32-9 | 0.00073461 |  | 0.001074 | (b) | 0.0027408 | (f) | 0.0010895 | (b) | 0.0027804 | (f) | 0.0010895 | (b) | 0.0027804 | (f) | 0.0013 | (b) | 0.0033176 | (f) | 0.0012712 | (b) | 0.0032441 | (f) | 0.0013 | (b) | 0.0033176 | (f) | 0.0013 | (b) | 0.0033176 | (f) | 0.0013 | (b) | 0.0033176 | (f) | 0.0013 | (b) | 0.0033176 | (f) | 0.0012712 | (b) | 0.0032441 | (f) | 0.0013 | (b) | 0.0033176 | (f) | 0.0012712 | (b) | 0.0032441 | (f) | 0.0012712 | (b) | 0.0032441 | (f) | 0.0012712 | (b) | 0.0032441 | (f) | 0.0012712 | (b) | 0.0032441 | (f)
| Acenaphthylene | 208-96-8 | 0.00080982 |  | 0.0011839 | (b) | 0.0030214 | (f) | 0.001201 | (b) | 0.003065 | (f) | 0.001201 | (b) | 0.003065 | (f) | 0.0014331 | (b) | 0.0036573 | (f) | 0.0014014 | (b) | 0.0035762 | (f) | 0.0014331 | (b) | 0.0036573 | (f) | 0.0014331 | (b) | 0.0036573 | (f) | 0.0014331 | (b) | 0.0036573 | (f) | 0.0014331 | (b) | 0.0036573 | (f) | 0.0014014 | (b) | 0.0035762 | (f) | 0.0014331 | (b) | 0.0036573 | (f) | 0.0014014 | (b) | 0.0035762 | (f) | 0.0014014 | (b) | 0.0035762 | (f) | 0.0014014 | (b) | 0.0035762 | (f) | 0.0014014 | (b) | 0.0035762 | (f)
| Acetaldehyde | 75-07-0 | 0.7833 |  | 1.1452 | (b) | 2.9225 | (f) | 1.1617 | (b) | 2.9647 | (f) | 1.1617 | (b) | 2.9647 | (f) | 1.3862 | (b) | 3.5375 | (f) | 1.3555 | (b) | 3.4591 | (f) | 1.3862 | (b) | 3.5375 | (f) | 1.3862 | (b) | 3.5375 | (f) | 1.3862 | (b) | 3.5375 | (f) | 1.3862 | (b) | 3.5375 | (f) | 1.3555 | (b) | 3.4591 | (f) | 1.3862 | (b) | 3.5375 | (f) | 1.3555 | (b) | 3.4591 | (f) | 1.3555 | (b) | 3.4591 | (f) | 1.3555 | (b) | 3.4591 | (f) | 1.3555 | (b) | 3.4591 | (f)
| Acrolein | 107-02-8 | 0.0339 |  | 0.049562 | (b) | 0.12648 | (f) | 0.050278 | (b) | 0.12831 | (f) | 0.050278 | (b) | 0.12831 | (f) | 0.059992 | (b) | 0.1531 | (f) | 0.058663 | (b) | 0.14971 | (f) | 0.059992 | (b) | 0.1531 | (f) | 0.059992 | (b) | 0.1531 | (f) | 0.059992 | (b) | 0.1531 | (f) | 0.059992 | (b) | 0.1531 | (f) | 0.058663 | (b) | 0.14971 | (f) | 0.059992 | (b) | 0.1531 | (f) | 0.058663 | (b) | 0.14971 | (f) | 0.058663 | (b) | 0.14971 | (f) | 0.058663 | (b) | 0.14971 | (f) | 0.058663 | (b) | 0.14971 | (f)
| Anthracene | 120-12-7 | 0.00045209 |  | 0.00066095 | (b) | 0.0016867 | (f) | 0.0006705 | (b) | 0.0017111 | (f) | 0.0006705 | (b) | 0.0017111 | (f) | 0.00080005 | (b) | 0.0020417 | (f) | 0.00078233 | (b) | 0.0019965 | (f) | 0.00080005 | (b) | 0.0020417 | (f) | 0.00080005 | (b) | 0.0020417 | (f) | 0.00080005 | (b) | 0.0020417 | (f) | 0.00080005 | (b) | 0.0020417 | (f) | 0.00078233 | (b) | 0.0019965 | (f) | 0.00080005 | (b) | 0.0020417 | (f) | 0.00078233 | (b) | 0.0019965 | (f) | 0.00078233 | (b) | 0.0019965 | (f) | 0.00078233 | (b) | 0.0019965 | (f) | 0.00078233 | (b) | 0.0019965 | (f)
| Benzene | 71-43-2 | 0.1863 |  | 0.27237 | (b) | 0.69508 | (f) | 0.2763 | (b) | 0.70512 | (f) | 0.2763 | (b) | 0.70512 | (f) | 0.32969 | (b) | 0.84136 | (f) | 0.32239 | (b) | 0.82272 | (f) | 0.32969 | (b) | 0.84136 | (f) | 0.32969 | (b) | 0.84136 | (f) | 0.32969 | (b) | 0.84136 | (f) | 0.32969 | (b) | 0.84136 | (f) | 0.32239 | (b) | 0.82272 | (f) | 0.32969 | (b) | 0.84136 | (f) | 0.32239 | (b) | 0.82272 | (f) | 0.32239 | (b) | 0.82272 | (f) | 0.32239 | (b) | 0.82272 | (f) | 0.32239 | (b) | 0.82272 | (f)
| Chlorobenzene | 108-90-7 | 0.0002 |  | 0.0002924 | (b) | 0.00074619 | (f) | 0.00029662 | (b) | 0.00075697 | (f) | 0.00029662 | (b) | 0.00075697 | (f) | 0.00035394 | (b) | 0.00090323 | (f) | 0.00034609 | (b) | 0.00088322 | (f) | 0.00035394 | (b) | 0.00090323 | (f) | 0.00035394 | (b) | 0.00090323 | (f) | 0.00035394 | (b) | 0.00090323 | (f) | 0.00035394 | (b) | 0.00090323 | (f) | 0.00034609 | (b) | 0.00088322 | (f) | 0.00035394 | (b) | 0.00090323 | (f) | 0.00034609 | (b) | 0.00088322 | (f) | 0.00034609 | (b) | 0.00088322 | (f) | 0.00034609 | (b) | 0.00088322 | (f) | 0.00034609 | (b) | 0.00088322 | (f)
| Ethylbenzene | 100-41-4 | 0.0109 |  | 0.015936 | (b) | 0.040668 | (f) | 0.016166 | (b) | 0.041255 | (f) | 0.016166 | (b) | 0.041255 | (f) | 0.01929 | (b) | 0.049226 | (f) | 0.018862 | (b) | 0.048135 | (f) | 0.01929 | (b) | 0.049226 | (f) | 0.01929 | (b) | 0.049226 | (f) | 0.01929 | (b) | 0.049226 | (f) | 0.01929 | (b) | 0.049226 | (f) | 0.018862 | (b) | 0.048135 | (f) | 0.01929 | (b) | 0.049226 | (f) | 0.018862 | (b) | 0.048135 | (f) | 0.018862 | (b) | 0.048135 | (f) | 0.018862 | (b) | 0.048135 | (f) | 0.018862 | (b) | 0.048135 | (f)
| Formaldehyde | 50-00-0 | 2.7131 |  | 3.9698 | (b) | 10.1618 | (f) | 4.0271 | (b) | 10.3086 | (f) | 4.0271 | (b) | 10.3086 | (f) | 4.8052 | (b) | 12.3004 | (f) | 4.6988 | (b) | 12.0278 | (f) | 4.8052 | (b) | 12.3004 | (f) | 4.8052 | (b) | 12.3004 | (f) | 4.8052 | (b) | 12.3004 | (f) | 4.8052 | (b) | 12.3004 | (f) | 4.6988 | (b) | 12.0278 | (f) | 4.8052 | (b) | 12.3004 | (f) | 4.6988 | (b) | 12.0278 | (f) | 4.6988 | (b) | 12.0278 | (f) | 4.6988 | (b) | 12.0278 | (f) | 4.6988 | (b) | 12.0278 | (f)
| Hexane | 110-54-3 | 0.0269 |  | 0.039328 | (b) | 0.10036 | (f) | 0.039896 | (b) | 0.10181 | (f) | 0.039896 | (b) | 0.10181 | (f) | 0.047604 | (b) | 0.12148 | (f) | 0.04655 | (b) | 0.11879 | (f) | 0.047604 | (b) | 0.12148 | (f) | 0.047604 | (b) | 0.12148 | (f) | 0.047604 | (b) | 0.12148 | (f) | 0.047604 | (b) | 0.12148 | (f) | 0.04655 | (b) | 0.11879 | (f) | 0.047604 | (b) | 0.12148 | (f) | 0.04655 | (b) | 0.11879 | (f) | 0.04655 | (b) | 0.11879 | (f) | 0.04655 | (b) | 0.11879 | (f) | 0.04655 | (b) | 0.11879 | (f)
| Propylene | 115-07-1 | 0.47 |  | 0.68714 | (b) | 1.7536 | (f) | 0.69706 | (b) | 1.7789 | (f) | 0.69706 | (b) | 1.7789 | (f) | 0.83175 | (b) | 2.1226 | (f) | 0.81332 | (b) | 2.0756 | (f) | 0.83175 | (b) | 2.1226 | (f) | 0.83175 | (b) | 2.1226 | (f) | 0.83175 | (b) | 2.1226 | (f) | 0.83175 | (b) | 2.1226 | (f) | 0.81332 | (b) | 2.0756 | (f) | 0.83175 | (b) | 2.1226 | (f) | 0.81332 | (b) | 2.0756 | (f) | 0.81332 | (b) | 2.0756 | (f) | 0.81332 | (b) | 2.0756 | (f) | 0.81332 | (b) | 2.0756 | (f)
| Toluene | 108-88-3 | 0.1054 |  | 0.15409 | (b) | 0.39324 | (f) | 0.15632 | (b) | 0.39892 | (f) | 0.15632 | (b) | 0.39892 | (f) | 0.18652 | (b) | 0.476 | (f) | 0.18239 | (b) | 0.46546 | (f) | 0.18652 | (b) | 0.476 | (f) | 0.18652 | (b) | 0.476 | (f) | 0.18652 | (b) | 0.476 | (f) | 0.18652 | (b) | 0.476 | (f) | 0.18239 | (b) | 0.46546 | (f) | 0.18652 | (b) | 0.476 | (f) | 0.18239 | (b) | 0.46546 | (f) | 0.18239 | (b) | 0.46546 | (f) | 0.18239 | (b) | 0.46546 | (f) | 0.18239 | (b) | 0.46546 | (f)
| Xylene (mixed isomers) | 1330-20-7 | 0.0424 |  | 0.061989 | (b) | 0.15819 | (f) | 0.062884 | (b) | 0.16048 | (f) | 0.062884 | (b) | 0.16048 | (f) | 0.075034 | (b) | 0.19149 | (f) | 0.073372 | (b) | 0.18724 | (f) | 0.075034 | (b) | 0.19149 | (f) | 0.075034 | (b) | 0.19149 | (f) | 0.075034 | (b) | 0.19149 | (f) | 0.075034 | (b) | 0.19149 | (f) | 0.073372 | (b) | 0.18724 | (f) | 0.075034 | (b) | 0.19149 | (f) | 0.073372 | (b) | 0.18724 | (f) | 0.073372 | (b) | 0.18724 | (f) | 0.073372 | (b) | 0.18724 | (f) | 0.073372 | (b) | 0.18724 | (f)
INORGANIC COMPOUNDS
| Ammonia | 7664-41-7 | 0.8 |  | 1.1696 | (b) | 2.9848 | (f) | 1.1865 | (b) | 3.0279 | (f) | 1.1865 | (b) | 3.0279 | (f) | 1.4157 | (b) | 3.6129 | (f) | 1.3844 | (b) | 3.5329 | (f) | 1.4157 | (b) | 3.6129 | (f) | 1.4157 | (b) | 3.6129 | (f) | 1.4157 | (b) | 3.6129 | (f) | 1.4157 | (b) | 3.6129 | (f) | 1.3844 | (b) | 3.5329 | (f) | 1.4157 | (b) | 3.6129 | (f) | 1.3844 | (b) | 3.5329 | (f) | 1.3844 | (b) | 3.5329 | (f) | 1.3844 | (b) | 3.5329 | (f) | 1.3844 | (b) | 3.5329 | (f)
| Hydrochloric Acid | 7647-01-0 | 0.1863 |  | 0.27237 | (b) | 0.69508 | (f) | 0.2763 | (b) | 0.70512 | (f) | 0.2763 | (b) | 0.70512 | (f) | 0.32969 | (b) | 0.84136 | (f) | 0.32239 | (b) | 0.82272 | (f) | 0.32969 | (b) | 0.84136 | (f) | 0.32969 | (b) | 0.84136 | (f) | 0.32969 | (b) | 0.84136 | (f) | 0.32969 | (b) | 0.84136 | (f) | 0.32239 | (b) | 0.82272 | (f) | 0.32969 | (b) | 0.84136 | (f) | 0.32239 | (b) | 0.82272 | (f) | 0.32239 | (b) | 0.82272 | (f) | 0.32239 | (b) | 0.82272 | (f) | 0.32239 | (b) | 0.82272 | (f)
POLYCYCLIC AROMATIC HYDROCARBONS (PAH)
| Benz[a]anthracene | 56-55-3 | 4.8541e-05 |  | 7.0967e-05 | (b) | 0.00018111 | (f) | 7.1992e-05 | (b) | 0.00018372 | (f) | 7.1992e-05 | (b) | 0.00018372 | (f) | 8.5903e-05 | (b) | 0.00021922 | (f) | 8.3999e-05 | (b) | 0.00021436 | (f) | 8.5903e-05 | (b) | 0.00021922 | (f) | 8.5903e-05 | (b) | 0.00021922 | (f) | 8.5903e-05 | (b) | 0.00021922 | (f) | 8.5903e-05 | (b) | 0.00021922 | (f) | 8.3999e-05 | (b) | 0.00021436 | (f) | 8.5903e-05 | (b) | 0.00021922 | (f) | 8.3999e-05 | (b) | 0.00021436 | (f) | 8.3999e-05 | (b) | 0.00021436 | (f) | 8.3999e-05 | (b) | 0.00021436 | (f) | 8.3999e-05 | (b) | 0.00021436 | (f)
| Benzo[a]pyrene | 50-32-8 | 1.4385e-05 |  | 2.1031e-05 | (b) | 5.3671e-05 | (f) | 2.1335e-05 | (b) | 5.4446e-05 | (f) | 2.1335e-05 | (b) | 5.4446e-05 | (f) | 2.5457e-05 | (b) | 6.4966e-05 | (f) | 2.4893e-05 | (b) | 6.3526e-05 | (f) | 2.5457e-05 | (b) | 6.4966e-05 | (f) | 2.5457e-05 | (b) | 6.4966e-05 | (f) | 2.5457e-05 | (b) | 6.4966e-05 | (f) | 2.5457e-05 | (b) | 6.4966e-05 | (f) | 2.4893e-05 | (b) | 6.3526e-05 | (f) | 2.5457e-05 | (b) | 6.4966e-05 | (f) | 2.4893e-05 | (b) | 6.3526e-05 | (f) | 2.4893e-05 | (b) | 6.3526e-05 | (f) | 2.4893e-05 | (b) | 6.3526e-05 | (f) | 2.4893e-05 | (b) | 6.3526e-05 | (f)
| Benzo[b]fluoranthene | 205-99-2 | 4.4354e-05 |  | 6.4845e-05 | (b) | 0.00016548 | (f) | 6.5781e-05 | (b) | 0.00016787 | (f) | 6.5781e-05 | (b) | 0.00016787 | (f) | 7.8492e-05 | (b) | 0.00020031 | (f) | 7.6752e-05 | (b) | 0.00019587 | (f) | 7.8492e-05 | (b) | 0.00020031 | (f) | 7.8492e-05 | (b) | 0.00020031 | (f) | 7.8492e-05 | (b) | 0.00020031 | (f) | 7.8492e-05 | (b) | 0.00020031 | (f) | 7.6752e-05 | (b) | 0.00019587 | (f) | 7.8492e-05 | (b) | 0.00020031 | (f) | 7.6752e-05 | (b) | 0.00019587 | (f) | 7.6752e-05 | (b) | 0.00019587 | (f) | 7.6752e-05 | (b) | 0.00019587 | (f) | 7.6752e-05 | (b) | 0.00019587 | (f)
| Benzo[e]pyrene | 192-97-2 | 3.2868e-05 |  | 4.8053e-05 | (b) | 0.00012263 | (f) | 4.8747e-05 | (b) | 0.0001244 | (f) | 4.8747e-05 | (b) | 0.0001244 | (f) | 5.8166e-05 | (b) | 0.00014844 | (f) | 5.6877e-05 | (b) | 0.00014515 | (f) | 5.8166e-05 | (b) | 0.00014844 | (f) | 5.8166e-05 | (b) | 0.00014844 | (f) | 5.8166e-05 | (b) | 0.00014844 | (f) | 5.8166e-05 | (b) | 0.00014844 | (f) | 5.6877e-05 | (b) | 0.00014515 | (f) | 5.8166e-05 | (b) | 0.00014844 | (f) | 5.6877e-05 | (b) | 0.00014515 | (f) | 5.6877e-05 | (b) | 0.00014515 | (f) | 5.6877e-05 | (b) | 0.00014515 | (f) | 5.6877e-05 | (b) | 0.00014515 | (f)
| Benzo[g,h,i]perylene | 191-24-2 | 2.1874e-05 |  | 3.198e-05 | (b) | 8.1612e-05 | (f) | 3.2442e-05 | (b) | 8.2791e-05 | (f) | 3.2442e-05 | (b) | 8.2791e-05 | (f) | 3.8711e-05 | (b) | 9.8788e-05 | (f) | 3.7853e-05 | (b) | 9.6599e-05 | (f) | 3.8711e-05 | (b) | 9.8788e-05 | (f) | 3.8711e-05 | (b) | 9.8788e-05 | (f) | 3.8711e-05 | (b) | 9.8788e-05 | (f) | 3.8711e-05 | (b) | 9.8788e-05 | (f) | 3.7853e-05 | (b) | 9.6599e-05 | (f) | 3.8711e-05 | (b) | 9.8788e-05 | (f) | 3.7853e-05 | (b) | 9.6599e-05 | (f) | 3.7853e-05 | (b) | 9.6599e-05 | (f) | 3.7853e-05 | (b) | 9.6599e-05 | (f) | 3.7853e-05 | (b) | 9.6599e-05 | (f)
| Benzo[k]fluoranthene | 207-08-9 | 1.3054e-05 |  | 1.9085e-05 | (b) | 4.8705e-05 | (f) | 1.9361e-05 | (b) | 4.9409e-05 | (f) | 1.9361e-05 | (b) | 4.9409e-05 | (f) | 2.3102e-05 | (b) | 5.8956e-05 | (f) | 2.259e-05 | (b) | 5.7649e-05 | (f) | 2.3102e-05 | (b) | 5.8956e-05 | (f) | 2.3102e-05 | (b) | 5.8956e-05 | (f) | 2.3102e-05 | (b) | 5.8956e-05 | (f) | 2.3102e-05 | (b) | 5.8956e-05 | (f) | 2.259e-05 | (b) | 5.7649e-05 | (f) | 2.3102e-05 | (b) | 5.8956e-05 | (f) | 2.259e-05 | (b) | 5.7649e-05 | (f) | 2.259e-05 | (b) | 5.7649e-05 | (f) | 2.259e-05 | (b) | 5.7649e-05 | (f) | 2.259e-05 | (b) | 5.7649e-05 | (f)
| Chrysene | 218-01-9 | 6.7e-05 |  | 9.7954e-05 | (b) | 0.00024997 | (f) | 9.9368e-05 | (b) | 0.00025358 | (f) | 9.9368e-05 | (b) | 0.00025358 | (f) | 0.00011857 | (b) | 0.00030258 | (f) | 0.00011594 | (b) | 0.00029588 | (f) | 0.00011857 | (b) | 0.00030258 | (f) | 0.00011857 | (b) | 0.00030258 | (f) | 0.00011857 | (b) | 0.00030258 | (f) | 0.00011857 | (b) | 0.00030258 | (f) | 0.00011594 | (b) | 0.00029588 | (f) | 0.00011857 | (b) | 0.00030258 | (f) | 0.00011594 | (b) | 0.00029588 | (f) | 0.00011594 | (b) | 0.00029588 | (f) | 0.00011594 | (b) | 0.00029588 | (f) | 0.00011594 | (b) | 0.00029588 | (f)
| Dibenz[a,h]anthracene | 53-70-3 | 1.037e-06 |  | 1.5161e-06 | (b) | 3.869e-06 | (f) | 1.538e-06 | (b) | 3.9248e-06 | (f) | 1.538e-06 | (b) | 3.9248e-06 | (f) | 1.8351e-06 | (b) | 4.6832e-06 | (f) | 1.7945e-06 | (b) | 4.5794e-06 | (f) | 1.8351e-06 | (b) | 4.6832e-06 | (f) | 1.8351e-06 | (b) | 4.6832e-06 | (f) | 1.8351e-06 | (b) | 4.6832e-06 | (f) | 1.8351e-06 | (b) | 4.6832e-06 | (f) | 1.7945e-06 | (b) | 4.5794e-06 | (f) | 1.8351e-06 | (b) | 4.6832e-06 | (f) | 1.7945e-06 | (b) | 4.5794e-06 | (f) | 1.7945e-06 | (b) | 4.5794e-06 | (f) | 1.7945e-06 | (b) | 4.5794e-06 | (f) | 1.7945e-06 | (b) | 4.5794e-06 | (f)
| Fluoranthene | 206-44-0 | 0.00036995 |  | 0.00054087 | (b) | 0.0013803 | (f) | 0.00054868 | (b) | 0.0014002 | (f) | 0.00054868 | (b) | 0.0014002 | (f) | 0.0006547 | (b) | 0.0016708 | (f) | 0.00064019 | (b) | 0.0016337 | (f) | 0.0006547 | (b) | 0.0016708 | (f) | 0.0006547 | (b) | 0.0016708 | (f) | 0.0006547 | (b) | 0.0016708 | (f) | 0.0006547 | (b) | 0.0016708 | (f) | 0.00064019 | (b) | 0.0016337 | (f) | 0.0006547 | (b) | 0.0016708 | (f) | 0.00064019 | (b) | 0.0016337 | (f) | 0.00064019 | (b) | 0.0016337 | (f) | 0.00064019 | (b) | 0.0016337 | (f) | 0.00064019 | (b) | 0.0016337 | (f)
| Fluorene | 86-73-7 | 0.0021844 |  | 0.0031936 | (b) | 0.0081499 | (f) | 0.0032397 | (b) | 0.0082676 | (f) | 0.0032397 | (b) | 0.0082676 | (f) | 0.0038657 | (b) | 0.0098651 | (f) | 0.00378 | (b) | 0.0096465 | (f) | 0.0038657 | (b) | 0.0098651 | (f) | 0.0038657 | (b) | 0.0098651 | (f) | 0.0038657 | (b) | 0.0098651 | (f) | 0.0038657 | (b) | 0.0098651 | (f) | 0.00378 | (b) | 0.0096465 | (f) | 0.0038657 | (b) | 0.0098651 | (f) | 0.00378 | (b) | 0.0096465 | (f) | 0.00378 | (b) | 0.0096465 | (f) | 0.00378 | (b) | 0.0096465 | (f) | 0.00378 | (b) | 0.0096465 | (f)
| Indeno[1,2,3-cd]pyrene | 193-39-5 | 1.0711e-05 |  | 1.5659e-05 | (b) | 3.9962e-05 | (f) | 1.5886e-05 | (b) | 4.0539e-05 | (f) | 1.5886e-05 | (b) | 4.0539e-05 | (f) | 1.8955e-05 | (b) | 4.8372e-05 | (f) | 1.8535e-05 | (b) | 4.7301e-05 | (f) | 1.8955e-05 | (b) | 4.8372e-05 | (f) | 1.8955e-05 | (b) | 4.8372e-05 | (f) | 1.8955e-05 | (b) | 4.8372e-05 | (f) | 1.8955e-05 | (b) | 4.8372e-05 | (f) | 1.8535e-05 | (b) | 4.7301e-05 | (f) | 1.8955e-05 | (b) | 4.8372e-05 | (f) | 1.8535e-05 | (b) | 4.7301e-05 | (f) | 1.8535e-05 | (b) | 4.7301e-05 | (f) | 1.8535e-05 | (b) | 4.7301e-05 | (f) | 1.8535e-05 | (b) | 4.7301e-05 | (f)
| Naphthalene | 91-20-3 | 0.026352 |  | 0.038527 | (b) | 0.09832 | (f) | 0.039084 | (b) | 0.09974 | (f) | 0.039084 | (b) | 0.09974 | (f) | 0.046635 | (b) | 0.11901 | (f) | 0.045602 | (b) | 0.11637 | (f) | 0.046635 | (b) | 0.11901 | (f) | 0.046635 | (b) | 0.11901 | (f) | 0.046635 | (b) | 0.11901 | (f) | 0.046635 | (b) | 0.11901 | (f) | 0.045602 | (b) | 0.11637 | (f) | 0.046635 | (b) | 0.11901 | (f) | 0.045602 | (b) | 0.11637 | (f) | 0.045602 | (b) | 0.11637 | (f) | 0.045602 | (b) | 0.11637 | (f) | 0.045602 | (b) | 0.11637 | (f)
| Perylene | 198-55-0 | 1.1782e-06 |  | 1.7226e-06 | (b) | 4.396e-06 | (f) | 1.7475e-06 | (b) | 4.4595e-06 | (f) | 1.7475e-06 | (b) | 4.4595e-06 | (f) | 2.0851e-06 | (b) | 5.3211e-06 | (f) | 2.0389e-06 | (b) | 5.2032e-06 | (f) | 2.0851e-06 | (b) | 5.3211e-06 | (f) | 2.0851e-06 | (b) | 5.3211e-06 | (f) | 2.0851e-06 | (b) | 5.3211e-06 | (f) | 2.0851e-06 | (b) | 5.3211e-06 | (f) | 2.0389e-06 | (b) | 5.2032e-06 | (f) | 2.0851e-06 | (b) | 5.3211e-06 | (f) | 2.0389e-06 | (b) | 5.2032e-06 | (f) | 2.0389e-06 | (b) | 5.2032e-06 | (f) | 2.0389e-06 | (b) | 5.2032e-06 | (f) | 2.0389e-06 | (b) | 5.2032e-06 | (f)
| Phenanthrene | 85-01-8 | 0.0045419 |  | 0.0066403 | (b) | 0.016946 | (f) | 0.0067362 | (b) | 0.017191 | (f) | 0.0067362 | (b) | 0.017191 | (f) | 0.0080378 | (b) | 0.020512 | (f) | 0.0078597 | (b) | 0.020058 | (f) | 0.0080378 | (b) | 0.020512 | (f) | 0.0080378 | (b) | 0.020512 | (f) | 0.0080378 | (b) | 0.020512 | (f) | 0.0080378 | (b) | 0.020512 | (f) | 0.0078597 | (b) | 0.020058 | (f) | 0.0080378 | (b) | 0.020512 | (f) | 0.0078597 | (b) | 0.020058 | (f) | 0.0078597 | (b) | 0.020058 | (f) | 0.0078597 | (b) | 0.020058 | (f) | 0.0078597 | (b) | 0.020058 | (f)
| Pyrene | 129-00-0 | 0.00125 |  | 0.0018275 | (b) | 0.0046637 | (f) | 0.0018539 | (b) | 0.0047311 | (f) | 0.0018539 | (b) | 0.0047311 | (f) | 0.0022121 | (b) | 0.0056452 | (f) | 0.0021631 | (b) | 0.0055201 | (f) | 0.0022121 | (b) | 0.0056452 | (f) | 0.0022121 | (b) | 0.0056452 | (f) | 0.0022121 | (b) | 0.0056452 | (f) | 0.0022121 | (b) | 0.0056452 | (f) | 0.0021631 | (b) | 0.0055201 | (f) | 0.0022121 | (b) | 0.0056452 | (f) | 0.0021631 | (b) | 0.0055201 | (f) | 0.0021631 | (b) | 0.0055201 | (f) | 0.0021631 | (b) | 0.0055201 | (f) | 0.0021631 | (b) | 0.0055201 | (f)
DIESEL PARTICULATE MATTER (DPM)
| DPM | 200 | 16.9752 |  | 24.8178 | (b) | 63.334 | (f) | 25.1762 | (b) | 64.2488 | (f) | 25.1762 | (b) | 64.2488 | (f) | 30.0408 | (b) | 76.6629 | (f) | 29.3751 | (b) | 74.9641 | (f) | 30.0408 | (b) | 76.6629 | (f) | 30.0408 | (b) | 76.6629 | (f) | 30.0408 | (b) | 76.6629 | (f) | 30.0408 | (b) | 76.6629 | (f) | 29.3751 | (b) | 74.9641 | (f) | 30.0408 | (b) | 76.6629 | (f) | 29.3751 | (b) | 74.9641 | (f) | 29.3751 | (b) | 74.9641 | (f) | 29.3751 | (b) | 74.9641 | (f) | 29.3751 | (b) | 74.9641 | (f)
Notes
DPF = Diesel Particulate Filter; HAP = Hazardous Air Pollutant; Mgal = 1,000 gallons; TAC = Toxic Air Contaminant.
(a) | Daily emissions estimate (lb/day) = ([emission factor {lb/Mgal}] x [fuel consumption {gal/hr}] x [daily hours of operation {hrs/day}] x [Mgal/1,000 gal]
(b) | Daily emissions estimate (lb/day) = (emission factor [lb/Mgal]) x (fuel consumption [gal/hr]) x (daily hours of operation [hrs/day]) x (Mgal/1,000 gal) | [14 empty] | (c), (d)
| + (cold start emissions [lb/minute]) x (number of cold starts per day) - (emissions per minute, normal operation [lb/minute]) x (number of cold starts per day) | [14 empty] | (3)
|  | Cold start adjustment factor = | 4.3 | (4)
|  | Cold start adjustment factor (formaldehyde) = | 4.8 | (4)
|  | Number of cold starts per day = | 1 | (5)
(c) | Cold start emissions (lb/minute) = (emission factor [lb/Mgal]) x [Mgal/1,000 gal] x (cold start adjustment factor) x (hourly fuel consumption [gal/hr]) / 60
(d) | Emissions per minute, normal operation (lb/minute) = (emission factor [lb/Mgal]) x (hourly fuel consumption [gal/hr]) / 60
(e) | Annual emissions estimate (lb/yr) = ([emission factor {lb/Mgal}] x [fuel consumption {gal/hr}] x [annual hours of operation {hrs/yr}] x [Mgal/1,000 gal]
(f) | Annual emissions estimate (lb/yr) = (emission factor [lb/Mgal]) x (fuel consumption [gal/hr]) x (annual hours of operation [hrs/yr]) x (Mgal/1,000 gal) | [14 empty] | (c), (d)
| + (cold start emissions [lb/minute]) x (number of cold starts per year) - (emissions per minute, normal operation [lb/minute]) x (number of cold starts per year) | [14 empty] | (3)
|  | Cold start adjustment factor = | 4.3 | (4)
|  | Cold start adjustment factor (formaldehyde) = | 4.8 | (4)
|  | Number of cold starts per year = | 12 | (5)
References
(1) | See Table 1, Input Emergency Generator Rates and Parameters
(2) | Emission Factors from the Oregon Department of Environmental Quality, AQ104B, diesel internal combustion, greater
than 750 hp. Ammonia emission factor assumes value for no SNCR or SCR control. DEQ reference CAO Diesel RICE (b).
(3) | Time allotted for cold stats was omitted from the daily/annual operating capacity in emission calculations. Cold start adjustments are not required for metals.
(4) | Cold start adjustment factors provided by the Oregon Department of Environmental Quality. All applicable pollutants, except
formaldehyde, share the same adjustment factor. Cold start adjustments are not required for metals.
(5) | Information provided by Intel based on one cold start per month per engine.

## FirePump_RONLER
Table 6
Fire Pumps TAC Emission Estimates—Ronler Acres
Intel Corporation
Emission Unit ID |  |  |  |  | PH #1 |  |  |  | PH #2 |  |  |  | PH #3 |  |  |  | PH #4
Fuel Consumption (gal/hr) |  |  |  | (1) | 10.4 |  |  |  | 11.3 |  |  |  | 6.6 |  |  |  | 6.1
Daily Hours of Operation (hrs/day) |  |  |  | (1) | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10
Annual Hours of Operation (hrs/yr) |  |  |  | (1) | 50 |  |  |  | 50 |  |  |  | 50 |  |  |  | 50
Pollutant |  | CAS | Emission Factor (2) (lb/Mgal) |  | Emissions Estimate (a)
[5 empty] | PH #1 |  |  |  | PH #2 |  |  |  | PH #3 |  |  |  | PH #4
[5 empty] | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr)
METALS
| Antimony and Compounds | 7440-36-0 | 0.00031819 |  | 3.3091e-05 | (a) | 0.00016546 | (e) | 3.5955e-05 | (a) | 0.00017978 | (e) | 2.1e-05 | (a) | 0.000105 | (e) | 1.9409e-05 | (a) | 9.7047e-05 | (e)
| Arsenic and Compounds | 7440-38-2 | 0.0016 |  | 0.0001664 | (a) | 0.000832 | (e) | 0.0001808 | (a) | 0.000904 | (e) | 0.0001056 | (a) | 0.000528 | (e) | 9.76e-05 | (a) | 0.000488 | (e)
| Barium and Compounds | 7440-39-3 | 0.00037389 |  | 3.8885e-05 | (a) | 0.00019442 | (e) | 4.225e-05 | (a) | 0.00021125 | (e) | 2.4677e-05 | (a) | 0.00012338 | (e) | 2.2807e-05 | (a) | 0.00011404 | (e)
| Beryllium and compounds | 7440-41-7 | 4.7708e-06 |  | 4.9617e-07 | (a) | 2.4808e-06 | (e) | 5.3911e-07 | (a) | 2.6955e-06 | (e) | 3.1488e-07 | (a) | 1.5744e-06 | (e) | 2.9102e-07 | (a) | 1.4551e-06 | (e)
| Cadmium and Compounds | 7440-43-9 | 0.0015 |  | 0.000156 | (a) | 0.00078 | (e) | 0.0001695 | (a) | 0.0008475 | (e) | 9.9e-05 | (a) | 0.000495 | (e) | 9.15e-05 | (a) | 0.0004575 | (e)
| Chromium VI | 18540-29-9 | 0.0001 |  | 1.04e-05 | (a) | 5.2e-05 | (e) | 1.13e-05 | (a) | 5.65e-05 | (e) | 6.6e-06 | (a) | 3.3e-05 | (e) | 6.1e-06 | (a) | 3.05e-05 | (e)
| Copper and Compounds | 7440-50-8 | 0.0041 |  | 0.0004264 | (a) | 0.002132 | (e) | 0.0004633 | (a) | 0.0023165 | (e) | 0.0002706 | (a) | 0.001353 | (e) | 0.0002501 | (a) | 0.0012505 | (e)
| Cobalt and compounds | 7440-48-4 | 1.5751e-05 |  | 1.6381e-06 | (a) | 8.1906e-06 | (e) | 1.7799e-06 | (a) | 8.8994e-06 | (e) | 1.0396e-06 | (a) | 5.1979e-06 | (e) | 9.6082e-07 | (a) | 4.8041e-06 | (e)
| Lead and Compounds | 7439-92-1 | 0.0083 |  | 0.0008632 | (a) | 0.004316 | (e) | 0.0009379 | (a) | 0.0046895 | (e) | 0.0005478 | (a) | 0.002739 | (e) | 0.0005063 | (a) | 0.0025315 | (e)
| Manganese and Compounds | 7439-96-5 | 0.0031 |  | 0.0003224 | (a) | 0.001612 | (e) | 0.0003503 | (a) | 0.0017515 | (e) | 0.0002046 | (a) | 0.001023 | (e) | 0.0001891 | (a) | 0.0009455 | (e)
| Mercury and Compounds | 7439-97-6 | 0.002 |  | 0.000208 | (a) | 0.00104 | (e) | 0.000226 | (a) | 0.00113 | (e) | 0.000132 | (a) | 0.00066 | (e) | 0.000122 | (a) | 0.00061 | (e)
| Nickel and Compounds | 7440-02-0 | 0.0039 |  | 0.0004056 | (a) | 0.002028 | (e) | 0.0004407 | (a) | 0.0022035 | (e) | 0.0002574 | (a) | 0.001287 | (e) | 0.0002379 | (a) | 0.0011895 | (e)
| Phosphorus and compounds | 504 | 0.008404 |  | 0.00087401 | (a) | 0.0043701 | (e) | 0.00094965 | (a) | 0.0047483 | (e) | 0.00055466 | (a) | 0.0027733 | (e) | 0.00051264 | (a) | 0.0025632 | (e)
| Selenium and Compounds | 7782-49-2 | 0.0022 |  | 0.0002288 | (a) | 0.001144 | (e) | 0.0002486 | (a) | 0.001243 | (e) | 0.0001452 | (a) | 0.000726 | (e) | 0.0001342 | (a) | 0.000671 | (e)
| Silver and compounds | 7440-22-4 | 4.8013e-05 |  | 4.9934e-06 | (a) | 2.4967e-05 | (e) | 5.4255e-06 | (a) | 2.7127e-05 | (e) | 3.1689e-06 | (a) | 1.5844e-05 | (e) | 2.9288e-06 | (a) | 1.4644e-05 | (e)
| Thallium and compounds | 7440-28-0 | 0.00024009 |  | 2.497e-05 | (a) | 0.00012485 | (e) | 2.7131e-05 | (a) | 0.00013565 | (e) | 1.5846e-05 | (a) | 7.9231e-05 | (e) | 1.4646e-05 | (a) | 7.3229e-05 | (e)
| Zinc and compounds | 7440-66-6 | 0.0052262 |  | 0.00054352 | (a) | 0.0027176 | (e) | 0.00059056 | (a) | 0.0029528 | (e) | 0.00034493 | (a) | 0.0017246 | (e) | 0.0003188 | (a) | 0.001594 | (e)
ORGANIC COMPOUNDS
| 1,3-Butadiene | 106-99-0 | 0.2174 |  | 0.022734 | (b) | 0.11951 | (f) | 0.024701 | (b) | 0.12986 | (f) | 0.014427 | (b) | 0.075846 | (f) | 0.013334 | (b) | 0.0701 | (f)
| Acetaldehyde | 75-07-0 | 0.7833 |  | 0.081911 | (b) | 0.43061 | (f) | 0.089 | (b) | 0.46788 | (f) | 0.051982 | (b) | 0.27327 | (f) | 0.048044 | (b) | 0.25257 | (f)
| Acrolein | 107-02-8 | 0.0339 |  | 0.003545 | (b) | 0.018636 | (f) | 0.0038518 | (b) | 0.020249 | (f) | 0.0022497 | (b) | 0.011827 | (f) | 0.0020793 | (b) | 0.010931 | (f)
| Benzene | 71-43-2 | 0.1863 |  | 0.019482 | (b) | 0.10242 | (f) | 0.021168 | (b) | 0.11128 | (f) | 0.012363 | (b) | 0.064996 | (f) | 0.011427 | (b) | 0.060072 | (f)
| Chlorobenzene | 108-90-7 | 0.0002 |  | 2.0914e-05 | (b) | 0.00010995 | (f) | 2.2724e-05 | (b) | 0.00011946 | (f) | 1.3273e-05 | (b) | 6.9775e-05 | (f) | 1.2267e-05 | (b) | 6.4489e-05 | (f)
| Ethylbenzene | 100-41-4 | 0.0109 |  | 0.0011398 | (b) | 0.0059922 | (f) | 0.0012385 | (b) | 0.0065108 | (f) | 0.00072336 | (b) | 0.0038027 | (f) | 0.00066856 | (b) | 0.0035147 | (f)
| Formaldehyde | 50-00-0 | 1.7261 |  | 0.18065 | (b) | 0.95669 | (f) | 0.19628 | (b) | 1.0395 | (f) | 0.11464 | (b) | 0.60713 | (f) | 0.10596 | (b) | 0.56114 | (f)
| Hexane | 110-54-3 | 0.0269 |  | 0.002813 | (b) | 0.014788 | (f) | 0.0030564 | (b) | 0.016068 | (f) | 0.0017852 | (b) | 0.0093848 | (f) | 0.0016499 | (b) | 0.0086738 | (f)
| Propylene | 115-07-1 | 0.47 |  | 0.049149 | (b) | 0.25838 | (f) | 0.053402 | (b) | 0.28074 | (f) | 0.031191 | (b) | 0.16397 | (f) | 0.028828 | (b) | 0.15155 | (f)
| Toluene | 108-88-3 | 0.1054 |  | 0.011022 | (b) | 0.057943 | (f) | 0.011976 | (b) | 0.062957 | (f) | 0.0069947 | (b) | 0.036772 | (f) | 0.0064648 | (b) | 0.033986 | (f)
| Xylene (mixed isomers) | 1330-20-7 | 0.0424 |  | 0.0044339 | (b) | 0.023309 | (f) | 0.0048176 | (b) | 0.025326 | (f) | 0.0028138 | (b) | 0.014792 | (f) | 0.0026006 | (b) | 0.013672 | (f)
INORGANIC COMPOUNDS
| Ammonia | 7664-41-7 | 0.8 |  | 0.083658 | (b) | 0.4398 | (f) | 0.090897 | (b) | 0.47785 | (f) | 0.05309 | (b) | 0.2791 | (f) | 0.049068 | (b) | 0.25796 | (f)
| Hydrochloric Acid | 7647-01-0 | 0.1863 |  | 0.019482 | (b) | 0.10242 | (f) | 0.021168 | (b) | 0.11128 | (f) | 0.012363 | (b) | 0.064996 | (f) | 0.011427 | (b) | 0.060072 | (f)
POLYCYCLIC AROMATIC HYDROCARBONS (PAH)
| Benzo[a]pyrene | 50-32-8 | 3.52e-05 |  | 3.6809e-06 | (b) | 1.9351e-05 | (f) | 3.9995e-06 | (b) | 2.1026e-05 | (f) | 2.336e-06 | (b) | 1.228e-05 | (f) | 2.159e-06 | (b) | 1.135e-05 | (f)
| Naphthalene | 91-20-3 | 0.0197 |  | 0.0020601 | (b) | 0.01083 | (f) | 0.0022383 | (b) | 0.011767 | (f) | 0.0013074 | (b) | 0.0068729 | (f) | 0.0012083 | (b) | 0.0063522 | (f)
| PAH | 401 | 0.0362 |  | 0.0037855 | (b) | 0.019901 | (f) | 0.0041131 | (b) | 0.021623 | (f) | 0.0024023 | (b) | 0.012629 | (f) | 0.0022203 | (b) | 0.011673 | (f)
DIESEL PARTICULATE MATTER (DPM)
| DPM | 200 | 33.5 |  | 3.5032 | (b) | 18.4164 | (f) | 3.8063 | (b) | 20.0102 | (f) | 2.2232 | (b) | 11.6873 | (f) | 2.0547 | (b) | 10.8019 | (f)
Notes
HAP = Hazardous Air Pollutant; Mgal = 1,000 gallons; TAC = Toxic Air Contaminant.
(a) | Daily emissions estimate (lb/day) = ([emission factor {lb/Mgal}] x [fuel consumption {gal/hr}] x [daily hours of operation {hrs/day}] x [Mgal/1,000 gal]
(b) | Daily emissions estimate (lb/day) = (emission factor [lb/Mgal]) x (fuel consumption [gal/hr]) x (daily hours of operation [hrs/day]) x (Mgal/1,000 gal) | [14 empty] | (c), (d)
| + (cold start emissions [lb/minute]) x (number of cold starts per day) - (emissions per minute, normal operation [lb/minute]) x (number of cold starts per day) | [14 empty] | (3)
|  | Cold start adjustment factor = | 4.3 | (4)
|  | Cold start adjustment factor (formaldehyde) = | 4.8 | (4)
|  | Number of cold starts per day = | 1 | (5)
(c) | Cold start emissions (lb/minute) = (emission factor [lb/Mgal]) x [Mgal/1,000 gal] x (cold start adjustment factor) x (hourly fuel consumption [gal/hr]) / 60
(d) | Emissions per minute, normal operation (lb/minute) = (emission factor [lb/Mgal]) x (hourly fuel consumption [gal/hr]) / 60
(e) | Annual emissions estimate (lb/yr) = ([emission factor {lb/Mgal}] x [fuel consumption {gal/hr}] x [annual hours of operation {hrs/yr}] x [Mgal/1,000 gal]
(f) | Annual emissions estimate (lb/yr) = (emission factor [lb/Mgal]) x (fuel consumption [gal/hr]) x (annual hours of operation [hrs/yr]) x (Mgal/1,000 gal) | [14 empty] | (c), (d)
| + (cold start emissions [lb/minute]) x (number of cold starts per year) - (emissions per minute, normal operation [lb/minute]) x (number of cold starts per year) | [14 empty] | (3)
|  | Cold start adjustment factor = | 4.3 | (4)
|  | Cold start adjustment factor (formaldehyde) = | 4.8 | (4)
|  | Number of cold starts per year = | 52 | (5)
References
(1) | See Table 1, Input Emergency Generator Rates and Parameters
(2) | Emission Factors from the Oregon Department of Environmental Quality, AQ104B, diesel internal combustion, less than
750 hp. Ammonia emission factor assumes value for no SNCR or SCR control. DEQ reference CAO Diesel RICE (a).
(3) | Time allotted for cold stats was omitted from the daily/annual operating capacity in emission calculations. Cold start adjustments are not required for metals.
(4) | Cold start adjustment factors provided by the Oregon Department of Environmental Quality. All applicable pollutants, except
formaldehyde, share the same adjustment factor. Cold start adjustments are not required for metals.
(5) | Information provided by Intel based on one cold start per week per engine.

## EGEN_ALOHA
Table 7
Emergency Generator TAC Emission Estimates—Aloha Campus
Intel Corporation
Emission Unit ID |  |  |  |  | F15-EG01 |  |  |  | F15-EG02 |  |  |  | F15-EG03 |  |  |  | F15.5-EG01 |  |  |  | F15.5-EG02
Fuel Consumption (gal/hr) |  |  |  | (1) | 107.8 |  |  |  | 107.8 |  |  |  | 107.8 |  |  |  | 107.86 |  |  |  | 107.28
Daily Hours of Operation (hrs/day) |  |  |  | (1) | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10 |  |  |  | 10
Annual Hours of Operation (hrs/yr) |  |  |  | (1) | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25 |  |  |  | 25
Pollutant |  | CAS | Emission Factor (2) (lb/Mgal) |  | Emissions Estimate (a)
[5 empty] | F15-EG01 |  |  |  | F15-EG02 |  |  |  | F15-EG03 |  |  |  | F15.5-EG01 |  |  |  | F15.5-EG02
[5 empty] | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr) |  | Daily (lb/day) |  | Annual (lb/yr)
METALS
| Antimony and Compounds | 7440-36-0 | 0.00031819 |  | 0.00034301 | (a) | 0.00085751 | (e) | 0.00034301 | (a) | 0.00085751 | (e) | 0.00034301 | (a) | 0.00085751 | (e) | 0.0003432 | (a) | 0.00085799 | (e) | 0.00034135 | (a) | 0.00085338 | (e)
| Arsenic and Compounds | 7440-38-2 | 0.0016 |  | 0.0017248 | (a) | 0.004312 | (e) | 0.0017248 | (a) | 0.004312 | (e) | 0.0017248 | (a) | 0.004312 | (e) | 0.0017258 | (a) | 0.0043144 | (e) | 0.0017165 | (a) | 0.0042912 | (e)
| Barium and Compounds | 7440-39-3 | 0.00037389 |  | 0.00040306 | (a) | 0.0010076 | (e) | 0.00040306 | (a) | 0.0010076 | (e) | 0.00040306 | (a) | 0.0010076 | (e) | 0.00040328 | (a) | 0.0010082 | (e) | 0.00040111 | (a) | 0.0010028 | (e)
| Beryllium and compounds | 7440-41-7 | 4.7708e-06 |  | 5.143e-06 | (a) | 1.2857e-05 | (e) | 5.143e-06 | (a) | 1.2857e-05 | (e) | 5.143e-06 | (a) | 1.2857e-05 | (e) | 5.1458e-06 | (a) | 1.2865e-05 | (e) | 5.1182e-06 | (a) | 1.2795e-05 | (e)
| Cadmium and Compounds | 7440-43-9 | 0.0015 |  | 0.001617 | (a) | 0.0040425 | (e) | 0.001617 | (a) | 0.0040425 | (e) | 0.001617 | (a) | 0.0040425 | (e) | 0.0016179 | (a) | 0.0040447 | (e) | 0.0016092 | (a) | 0.004023 | (e)
| Chromium VI | 18540-29-9 | 0.0001 |  | 0.0001078 | (a) | 0.0002695 | (e) | 0.0001078 | (a) | 0.0002695 | (e) | 0.0001078 | (a) | 0.0002695 | (e) | 0.00010786 | (a) | 0.00026965 | (e) | 0.00010728 | (a) | 0.0002682 | (e)
| Copper and Compounds | 7440-50-8 | 0.0041 |  | 0.0044198 | (a) | 0.01105 | (e) | 0.0044198 | (a) | 0.01105 | (e) | 0.0044198 | (a) | 0.01105 | (e) | 0.0044223 | (a) | 0.011056 | (e) | 0.0043985 | (a) | 0.010996 | (e)
| Cobalt and compounds | 7440-48-4 | 1.5751e-05 |  | 1.698e-05 | (a) | 4.2449e-05 | (e) | 1.698e-05 | (a) | 4.2449e-05 | (e) | 1.698e-05 | (a) | 4.2449e-05 | (e) | 1.6989e-05 | (a) | 4.2473e-05 | (e) | 1.6898e-05 | (a) | 4.2245e-05 | (e)
| Lead and Compounds | 7439-92-1 | 0.0083 |  | 0.0089474 | (a) | 0.022368 | (e) | 0.0089474 | (a) | 0.022368 | (e) | 0.0089474 | (a) | 0.022368 | (e) | 0.0089524 | (a) | 0.022381 | (e) | 0.0089042 | (a) | 0.022261 | (e)
| Manganese and Compounds | 7439-96-5 | 0.0031 |  | 0.0033418 | (a) | 0.0083545 | (e) | 0.0033418 | (a) | 0.0083545 | (e) | 0.0033418 | (a) | 0.0083545 | (e) | 0.0033437 | (a) | 0.0083591 | (e) | 0.0033257 | (a) | 0.0083142 | (e)
| Mercury and Compounds | 7439-97-6 | 0.002 |  | 0.002156 | (a) | 0.00539 | (e) | 0.002156 | (a) | 0.00539 | (e) | 0.002156 | (a) | 0.00539 | (e) | 0.0021572 | (a) | 0.005393 | (e) | 0.0021456 | (a) | 0.005364 | (e)
| Nickel and Compounds | 7440-02-0 | 0.0039 |  | 0.0042042 | (a) | 0.01051 | (e) | 0.0042042 | (a) | 0.01051 | (e) | 0.0042042 | (a) | 0.01051 | (e) | 0.0042065 | (a) | 0.010516 | (e) | 0.0041839 | (a) | 0.01046 | (e)
| Phosphorus and compounds | 504 | 0.008404 |  | 0.0090595 | (a) | 0.022649 | (e) | 0.0090595 | (a) | 0.022649 | (e) | 0.0090595 | (a) | 0.022649 | (e) | 0.0090645 | (a) | 0.022661 | (e) | 0.0090158 | (a) | 0.022539 | (e)
| Selenium and Compounds | 7782-49-2 | 0.0022 |  | 0.0023716 | (a) | 0.005929 | (e) | 0.0023716 | (a) | 0.005929 | (e) | 0.0023716 | (a) | 0.005929 | (e) | 0.0023729 | (a) | 0.0059323 | (e) | 0.0023602 | (a) | 0.0059004 | (e)
| Silver and compounds | 7440-22-4 | 4.8013e-05 |  | 5.1758e-05 | (a) | 0.0001294 | (e) | 5.1758e-05 | (a) | 0.0001294 | (e) | 5.1758e-05 | (a) | 0.0001294 | (e) | 5.1787e-05 | (a) | 0.00012947 | (e) | 5.1508e-05 | (a) | 0.00012877 | (e)
| Thallium and compounds | 7440-28-0 | 0.00024009 |  | 0.00025882 | (a) | 0.00064705 | (e) | 0.00025882 | (a) | 0.00064705 | (e) | 0.00025882 | (a) | 0.00064705 | (e) | 0.00025897 | (a) | 0.00064741 | (e) | 0.00025757 | (a) | 0.00064393 | (e)
| Zinc and compounds | 7440-66-6 | 0.0052262 |  | 0.0056338 | (a) | 0.014085 | (e) | 0.0056338 | (a) | 0.014085 | (e) | 0.0056338 | (a) | 0.014085 | (e) | 0.005637 | (a) | 0.014092 | (e) | 0.0056066 | (a) | 0.014017 | (e)
ORGANIC COMPOUNDS
| 1,3-Butadiene | 106-99-0 | 0.2174 |  | 0.23565 | (b) | 0.60136 | (f) | 0.23565 | (b) | 0.60136 | (f) | 0.23565 | (b) | 0.60136 | (f) | 0.23578 | (b) | 0.6017 | (f) | 0.23451 | (b) | 0.59846 | (f)
| Acetaldehyde | 75-07-0 | 0.7833 |  | 0.84904 | (b) | 2.1667 | (f) | 0.84904 | (b) | 2.1667 | (f) | 0.84904 | (b) | 2.1667 | (f) | 0.84951 | (b) | 2.1679 | (f) | 0.84495 | (b) | 2.1563 | (f)
| Acrolein | 107-02-8 | 0.0339 |  | 0.036745 | (b) | 0.093772 | (f) | 0.036745 | (b) | 0.093772 | (f) | 0.036745 | (b) | 0.093772 | (f) | 0.036766 | (b) | 0.093825 | (f) | 0.036568 | (b) | 0.09332 | (f)
| Benzene | 71-43-2 | 0.1863 |  | 0.20194 | (b) | 0.51533 | (f) | 0.20194 | (b) | 0.51533 | (f) | 0.20194 | (b) | 0.51533 | (f) | 0.20205 | (b) | 0.51562 | (f) | 0.20096 | (b) | 0.51285 | (f)
| Chlorobenzene | 108-90-7 | 0.0002 |  | 0.00021679 | (b) | 0.00055323 | (f) | 0.00021679 | (b) | 0.00055323 | (f) | 0.00021679 | (b) | 0.00055323 | (f) | 0.00021691 | (b) | 0.00055354 | (f) | 0.00021574 | (b) | 0.00055056 | (f)
| Ethylbenzene | 100-41-4 | 0.0109 |  | 0.011815 | (b) | 0.030151 | (f) | 0.011815 | (b) | 0.030151 | (f) | 0.011815 | (b) | 0.030151 | (f) | 0.011821 | (b) | 0.030168 | (f) | 0.011758 | (b) | 0.030006 | (f)
| Formaldehyde | 50-00-0 | 1.7261 |  | 1.8725 | (b) | 4.7933 | (f) | 1.8725 | (b) | 4.7933 | (f) | 1.8725 | (b) | 4.7933 | (f) | 1.8736 | (b) | 4.7959 | (f) | 1.8635 | (b) | 4.7701 | (f)
| Hexane | 110-54-3 | 0.0269 |  | 0.029158 | (b) | 0.074409 | (f) | 0.029158 | (b) | 0.074409 | (f) | 0.029158 | (b) | 0.074409 | (f) | 0.029174 | (b) | 0.074451 | (f) | 0.029017 | (b) | 0.07405 | (f)
| Propylene | 115-07-1 | 0.47 |  | 0.50945 | (b) | 1.3001 | (f) | 0.50945 | (b) | 1.3001 | (f) | 0.50945 | (b) | 1.3001 | (f) | 0.50973 | (b) | 1.3008 | (f) | 0.50699 | (b) | 1.2938 | (f)
| Toluene | 108-88-3 | 0.1054 |  | 0.11425 | (b) | 0.29155 | (f) | 0.11425 | (b) | 0.29155 | (f) | 0.11425 | (b) | 0.29155 | (f) | 0.11431 | (b) | 0.29171 | (f) | 0.1137 | (b) | 0.29015 | (f)
| Xylene (mixed isomers) | 1330-20-7 | 0.0424 |  | 0.045959 | (b) | 0.11728 | (f) | 0.045959 | (b) | 0.11728 | (f) | 0.045959 | (b) | 0.11728 | (f) | 0.045984 | (b) | 0.11735 | (f) | 0.045737 | (b) | 0.11672 | (f)
INORGANIC COMPOUNDS
| Ammonia | 7664-41-7 | 0.8 |  | 0.86714 | (b) | 2.2129 | (f) | 0.86714 | (b) | 2.2129 | (f) | 0.86714 | (b) | 2.2129 | (f) | 0.86763 | (b) | 2.2142 | (f) | 0.86296 | (b) | 2.2022 | (f)
| Hydrochloric Acid | 7647-01-0 | 0.1863 |  | 0.20194 | (b) | 0.51533 | (f) | 0.20194 | (b) | 0.51533 | (f) | 0.20194 | (b) | 0.51533 | (f) | 0.20205 | (b) | 0.51562 | (f) | 0.20096 | (b) | 0.51285 | (f)
POLYCYCLIC AROMATIC HYDROCARBONS (PAH)
| Benzo[a]pyrene | 50-32-8 | 3.52e-05 |  | 3.8154e-05 | (b) | 9.7368e-05 | (f) | 3.8154e-05 | (b) | 9.7368e-05 | (f) | 3.8154e-05 | (b) | 9.7368e-05 | (f) | 3.8176e-05 | (b) | 9.7423e-05 | (f) | 3.797e-05 | (b) | 9.6899e-05 | (f)
| Naphthalene | 91-20-3 | 0.0197 |  | 0.021353 | (b) | 0.054493 | (f) | 0.021353 | (b) | 0.054493 | (f) | 0.021353 | (b) | 0.054493 | (f) | 0.021365 | (b) | 0.054523 | (f) | 0.02125 | (b) | 0.05423 | (f)
| PAH | 401 | 0.0362 |  | 0.039238 | (b) | 0.10013 | (f) | 0.039238 | (b) | 0.10013 | (f) | 0.039238 | (b) | 0.10013 | (f) | 0.03926 | (b) | 0.10019 | (f) | 0.039049 | (b) | 0.099652 | (f)
DIESEL PARTICULATE MATTER (DPM)
| DPM | 200 | 33.5 |  | 36.3116 | (b) | 92.666 | (f) | 36.3116 |  | 92.666 | (f) | 36.3116 |  | 92.666 | (f) | 36.3318 |  | 92.7175 | (f) | 36.1365 |  | 92.219 | (f)
Notes
HAP = Hazardous Air Pollutant; Mgal = 1,000 gallons; TAC = Toxic Air Contaminant.
(a) | Daily emissions estimate (lb/day) = ([emission factor {lb/Mgal}] x [fuel consumption {gal/hr}] x [daily hours of operation {hrs/day}] x [Mgal/1,000 gal]
(b) | Daily emissions estimate (lb/day) = (emission factor [lb/Mgal]) x (fuel consumption [gal/hr]) x (daily hours of operation [hrs/day]) x (Mgal/1,000 gal) | [14 empty] | (c), (d)
| + (cold start emissions [lb/minute]) x (number of cold starts per day) - (emissions per minute, normal operation [lb/minute]) x (number of cold starts per day) | [14 empty] | (3)
|  | Cold start adjustment factor = | 4.3 | (4)
|  | Cold start adjustment factor (formaldehyde) = | 4.8 | (4)
|  | Number of cold starts per day = | 1 | (5)
(c) | Cold start emissions (lb/minute) = (emission factor [lb/Mgal]) x [Mgal/1,000 gal] x (cold start adjustment factor) x (hourly fuel consumption [gal/hr]) / 60
(d) | Emissions per minute, normal operation (lb/minute) = (emission factor [lb/Mgal]) x (hourly fuel consumption [gal/hr]) / 60
(e) | Annual emissions estimate (lb/yr) = ([emission factor {lb/Mgal}] x [fuel consumption {gal/hr}] x [annual hours of operation {hrs/yr}] x [Mgal/1,000 gal]
(f) | Annual emissions estimate (lb/yr) = (emission factor [lb/Mgal]) x (fuel consumption [gal/hr]) x (annual hours of operation [hrs/yr]) x (Mgal/1,000 gal) | [14 empty] | (c), (d)
| + (cold start emissions [lb/minute]) x (number of cold starts per year) - (emissions per minute, normal operation [lb/minute]) x (number of cold starts per year) | [14 empty] | (3)
|  | Cold start adjustment factor = | 4.3 | (4)
|  | Cold start adjustment factor (formaldehyde) = | 4.8 | (4)
|  | Number of cold starts per year = | 12 | (5)
References
(1) | See Table 1, Input Emergency Generator Rates and Parameters
(2) | Emission Factors from the Oregon Department of Environmental Quality, AQ104B, diesel internal combustion, less than
750 hp. Ammonia emission factor assumes value for no SNCR or SCR control. DEQ reference CAO Diesel RICE (a).
(3) | Time allotted for cold stats was omitted from the daily/annual operating capacity in emission calculations. Cold start adjustments are not required for metals.
(4) | Cold start adjustment factors provided by the Oregon Department of Environmental Quality. All applicable pollutants, except
formaldehyde, share the same adjustment factor. Cold start adjustments are not required for metals.
(5) | Information provided by Intel based on one cold start per month per engine.

## DAY TAC SumEGEN
Table 8
Daily TAC Emission Estimate Summary—Emergency Generators
Intel Corporation
Pollutant |  | CAS | Regulatory Category |  | Daily Emissions Estimate (lb/day) | [89 empty] | Total Emissions Estimate (Emergency Generators) (lb/day)
[5 empty] | Ronler | [84 empty] | Aloha
[5 empty] | DPF | [44 empty] | No DPF | [35 empty] | Fire Pumps |  |  |  | Aloha
|  |  | TAC | RBC? | N2-GEN-1A | H2-GEN-1 | D1X-GEN-5A | D1X-GEN-5B | D1X-GEN-4C | D1X-GEN-6A | D1X-GEN-6B | D1X-GEN-6C | D1X-GEN-7A | D1X-GEN-7B | D1X-GEN-7C | D1X2-GEN-6A | D1X2-GEN-6B | D1X2-GEN-6C | D1X2-GEN-7A | D1X2-GEN-7B | D1X2-GEN-7C | D1X2-GEN-1A | D1X2-GEN-1B | D1X2-GEN-1C | D1X2-GEN-2A | D1X2-GEN-2B | D1X2-GEN-2C | D1X2-GEN-3A | D1X2-GEN-3B | D1X2-GEN-3C | D1X2-GEN-4A | D1X2-GEN-4B | D1X2-GEN-4C | D1X2-GEN-5A | D1X2-GEN-5B | D1X2-GEN-5C | F20-EPS-1 | F20-EPS-2 | IWW-GEN-1 | IWW-GEN-2 | IWW-PS-1 | D1A-GEN-1 | D1A-GEN-2 | D1A-GEN-3 | D1A-GEN-4 | D1A-GEN-5 | D1A-GEN-6 | D1A-GEN-7 | D1A-GEN-8 | RA1-ELEC-CPS-GEN01 | RA1-ELEC-CPS-GEN02 | RA1-ELEC-CPS-GEN03 | RA1-ELEC-CPS-GEN04 | D1C-CPS-GEN01 | D1C-CPS-GEN02 | D1C-CPS-GEN03 | D1C-EPS-GEN01 | D1C-EPS-GEN02 | RB1-EPS-GEN01 | RP1-EPS-GEN01 | EPS-GEN01 | EPS-GEN02 | EPS-GEN03 | EPS-GEN04 | EPS-GEN05 | EPS-GEN06 | RS4-ELEC-EG-4-1 | RS6-ELEC-EG-6-1 | F20-CPS-1 | MAX-EGEN | RP1-GEN-2 | D1D-GEN-7 | RS6-GEN-2 | D1X-GEN-1A | D1X-GEN-1B | D1X-GEN-1C | D1X-GEN-2A | D1X-GEN-2B | D1X-GEN-2C | D1X-GEN-3A | D1X-GEN-3B | D1X-GEN-3C | D1X-GEN-4A | D1X-GEN-4B | D1X-GEN-5C | PH #1 | PH #2 | PH #3 | PH #4 | F15-EG01 | F15-EG02 | F15-EG03 | F15.5-EG01 | F15.5-EG02
Stack ID |  |  |  |  | EGN2_01 | EGH2_01 | EGE1_14 | EGE1_15 | EGE1_13 | EGE1_16 | EGE1_17 | EGE1_18 | EGE1_19 | EGE1_20 | EGE1_21 | EGC5_16 | EGC5_17 | EGC5_18 | EGC5_19 | EGC5_20 | EGC5_21 | EGC5_01 | EGC5_02 | EGC5_03 | EGC5_04 | EGC5_05 | EGC5_06 | EGC5_07 | EGC5_08 | EGC5_09 | EGC5_10 | EGC5_11 | EGC5_12 | EGC5_13 | EGC5_14 | EGC5_15 | EGDB_01 | EGDB_02 | EGIW_02 | EGIW_01 | EGIW_03 | EGDA_01 | EGDA_02 | EGDA_03 | EGDA_04 | EGDA_05 | EGDA_06 | EGDA_07 | EGDA_08 | EGR1_01 | EGR1_02 | EGR1_03 | EGR1_04 | EGDC_01 | EGDC_02 | EGDC_03 | EGDC_04 | EGDC_05 | EGRB1_01 | EGRP1_01 | EGDD_01 | EGDD_02 | EGDD_03 | EGDD_04 | EGDD_05 | EGDD_06 | EGRS4_01 | EGRS6_01 | EGDB_03 | EGRS8_01 | EGRP1_02 | EGDD_07 | EGRS6_02 | EGE1_01 | EGE1_02 | EGE1_03 | EGE1_04 | EGE1_05 | EGE1_06 | EGE1_07 | EGE1_08 | EGE1_09 | EGE1_10 | EGE1_11 | EGE1_12 | FIPH1_01 | FIPH2_01 | FIRS4_01 | FIC5_01 | EGF15_01 | EGF15_02 | EGF15_03 | EGF5_01 | EGF5_02
METALS
| Antimony and Compounds | 7440-36-0 | Yes | Yes | 2.8732e-05 | 2.0428e-05 | 0.00019664 | 0.00019664 | 0.00019664 | 0.00019664 | 0.00019664 | 0.00019664 | 0.00016418 | 0.00016418 | 0.00016418 | 0.00022909 | 0.00022909 | 0.00022909 | 0.00022909 | 0.00022909 | 0.00022909 | 0.00022909 | 0.00022909 | 0.00022909 | 0.00022909 | 0.00022909 | 0.00022909 | 0.00022909 | 0.00022909 | 0.00022909 | 0.00022909 | 0.00022909 | 0.00022909 | 0.00022909 | 0.00022909 | 0.00022909 | 0.00019664 | 0.00019664 | 0.00019664 | 0.00019664 | 3.2837e-05 | 0.00022909 | 0.00022909 | 0.00022909 | 0.00022909 | 0.00022909 | 0.00022909 | 0.00022909 | 0.00022909 | 0.00036117 | 0.00036117 | 0.00036117 | 0.00036117 | 0.00028545 | 0.00028545 | 0.00028545 | 0.00039137 | 0.00039137 | 0.00043751 | 0.00046264 | 0.0004692 | 0.0004692 | 0.0004692 | 0.0004692 | 0.0004692 | 0.0004692 | 7.2865e-05 | 7.2865e-05 | 0.00014764 | 6.1728e-05 | 0.00046264 | 0.00046933 | 0.00046933 | 0.00056001 | 0.0005476 | 0.00056001 | 0.00056001 | 0.00056001 | 0.00056001 | 0.0005476 | 0.00056001 | 0.0005476 | 0.0005476 | 0.0005476 | 0.0005476 | 3.3091e-05 | 3.5955e-05 | 2.1e-05 | 1.9409e-05 | 0.00034301 | 0.00034301 | 0.00034301 | 0.0003432 | 0.00034135 | 0.026209
| Arsenic and compounds | 7440-38-2 | Yes | Yes | 0.00014448 | 0.00010272 | 0.00017109 | 0.00017109 | 0.00017109 | 0.00017109 | 0.00017109 | 0.00017109 | 0.00014286 | 0.00014286 | 0.00014286 | 0.00019933 | 0.00019933 | 0.00019933 | 0.00019933 | 0.00019933 | 0.00019933 | 0.00019933 | 0.00019933 | 0.00019933 | 0.00019933 | 0.00019933 | 0.00019933 | 0.00019933 | 0.00019933 | 0.00019933 | 0.00019933 | 0.00019933 | 0.00019933 | 0.00019933 | 0.00019933 | 0.00019933 | 0.00017109 | 0.00017109 | 0.00017109 | 0.00017109 | 2.8571e-05 | 0.00019933 | 0.00019933 | 0.00019933 | 0.00019933 | 0.00019933 | 0.00019933 | 0.00019933 | 0.00019933 | 0.0018162 | 0.0018162 | 0.0018162 | 0.0018162 | 0.0014354 | 0.0014354 | 0.0014354 | 0.001968 | 0.001968 | 0.0022 | 0.0023264 | 0.0023594 | 0.0023594 | 0.0023594 | 0.0023594 | 0.0023594 | 0.0023594 | 0.0003664 | 0.0003664 | 0.0007424 | 0.0003104 | 0.00040254 | 0.00040836 | 0.00040836 | 0.00048726 | 0.00047646 | 0.00048726 | 0.00048726 | 0.00048726 | 0.00048726 | 0.00047646 | 0.00048726 | 0.00047646 | 0.00047646 | 0.00047646 | 0.00047646 | 0.0001664 | 0.0001808 | 0.0001056 | 9.76e-05 | 0.0017248 | 0.0017248 | 0.0017248 | 0.0017258 | 0.0017165 | 0.060339
| Barium and Compounds | 7440-39-3 | Yes | -- | 6.1898e-06 | 4.4007e-06 | 4.2362e-05 | 4.2362e-05 | 4.2362e-05 | 4.2362e-05 | 4.2362e-05 | 4.2362e-05 | 3.537e-05 | 3.537e-05 | 3.537e-05 | 4.9354e-05 | 4.9354e-05 | 4.9354e-05 | 4.9354e-05 | 4.9354e-05 | 4.9354e-05 | 4.9354e-05 | 4.9354e-05 | 4.9354e-05 | 4.9354e-05 | 4.9354e-05 | 4.9354e-05 | 4.9354e-05 | 4.9354e-05 | 4.9354e-05 | 4.9354e-05 | 4.9354e-05 | 4.9354e-05 | 4.9354e-05 | 4.9354e-05 | 4.9354e-05 | 4.2362e-05 | 4.2362e-05 | 0.00023107 | 0.00023107 | 3.8586e-05 | 4.9354e-05 | 4.9354e-05 | 4.9354e-05 | 4.9354e-05 | 4.9354e-05 | 4.9354e-05 | 4.9354e-05 | 4.9354e-05 | 0.00042441 | 0.00042441 | 0.00042441 | 0.00042441 | 0.00033542 | 0.00033542 | 0.00033542 | 0.00045989 | 0.00045989 | 0.0005141 | 0.00054364 | 0.00055134 | 0.00055134 | 0.00055134 | 0.00055134 | 0.00055134 | 0.00055134 | 8.5622e-05 | 8.5622e-05 | 0.00017349 | 7.2535e-05 | 0.00054364 | 0.00055149 | 0.00055149 | 0.00065805 | 0.00064347 | 0.00065805 | 0.00065805 | 0.00065805 | 0.00065805 | 0.00064347 | 0.00065805 | 0.00064347 | 0.00064347 | 0.00064347 | 0.00064347 | 3.8885e-05 | 4.225e-05 | 2.4677e-05 | 2.2807e-05 | 0.00040306 | 0.00040306 | 0.00040306 | 0.00040328 | 0.00040111 | 0.022392
| Beryllium and Compounds | 7440-41-7 | Yes | Yes | 4.3081e-07 | 3.0629e-07 | 2.9484e-06 | 2.9484e-06 | 2.9484e-06 | 2.9484e-06 | 2.9484e-06 | 2.9484e-06 | 2.4618e-06 | 2.4618e-06 | 2.4618e-06 | 3.435e-06 | 3.435e-06 | 3.435e-06 | 3.435e-06 | 3.435e-06 | 3.435e-06 | 3.435e-06 | 3.435e-06 | 3.435e-06 | 3.435e-06 | 3.435e-06 | 3.435e-06 | 3.435e-06 | 3.435e-06 | 3.435e-06 | 3.435e-06 | 3.435e-06 | 3.435e-06 | 3.435e-06 | 3.435e-06 | 3.435e-06 | 2.9484e-06 | 2.9484e-06 | 2.9484e-06 | 2.9484e-06 | 4.9235e-07 | 3.435e-06 | 3.435e-06 | 3.435e-06 | 3.435e-06 | 3.435e-06 | 3.435e-06 | 3.435e-06 | 3.435e-06 | 5.4154e-06 | 5.4154e-06 | 5.4154e-06 | 5.4154e-06 | 4.2799e-06 | 4.2799e-06 | 4.2799e-06 | 5.8681e-06 | 5.8681e-06 | 6.5599e-06 | 6.9368e-06 | 7.0351e-06 | 7.0351e-06 | 7.0351e-06 | 7.0351e-06 | 7.0351e-06 | 7.0351e-06 | 1.0925e-06 | 1.0925e-06 | 2.2137e-06 | 9.2554e-07 | 6.9368e-06 | 7.037e-06 | 7.037e-06 | 8.3967e-06 | 8.2106e-06 | 8.3967e-06 | 8.3967e-06 | 8.3967e-06 | 8.3967e-06 | 8.2106e-06 | 8.3967e-06 | 8.2106e-06 | 8.2106e-06 | 8.2106e-06 | 8.2106e-06 | 4.9617e-07 | 5.3911e-07 | 3.1488e-07 | 2.9102e-07 | 5.143e-06 | 5.143e-06 | 5.143e-06 | 5.1458e-06 | 5.1182e-06 | 0.00039297
| Cadmium and Compounds | 7440-43-9 | Yes | Yes | 0.00013545 | 9.63e-05 | 4.9921e-05 | 4.9921e-05 | 4.9921e-05 | 4.9921e-05 | 4.9921e-05 | 4.9921e-05 | 4.1682e-05 | 4.1682e-05 | 4.1682e-05 | 5.816e-05 | 5.816e-05 | 5.816e-05 | 5.816e-05 | 5.816e-05 | 5.816e-05 | 5.816e-05 | 5.816e-05 | 5.816e-05 | 5.816e-05 | 5.816e-05 | 5.816e-05 | 5.816e-05 | 5.816e-05 | 5.816e-05 | 5.816e-05 | 5.816e-05 | 5.816e-05 | 5.816e-05 | 5.816e-05 | 5.816e-05 | 4.9921e-05 | 4.9921e-05 | 4.9921e-05 | 4.9921e-05 | 8.3363e-06 | 5.816e-05 | 5.816e-05 | 5.816e-05 | 5.816e-05 | 5.816e-05 | 5.816e-05 | 5.816e-05 | 5.816e-05 | 0.0017026 | 0.0017026 | 0.0017026 | 0.0017026 | 0.0013457 | 0.0013457 | 0.0013457 | 0.001845 | 0.001845 | 0.0020625 | 0.002181 | 0.0022119 | 0.0022119 | 0.0022119 | 0.0022119 | 0.0022119 | 0.0022119 | 0.0003435 | 0.0003435 | 0.000696 | 0.000291 | 0.00011745 | 0.00011915 | 0.00011915 | 0.00014217 | 0.00013902 | 0.00014217 | 0.00014217 | 0.00014217 | 0.00014217 | 0.00013902 | 0.00014217 | 0.00013902 | 0.00013902 | 0.00013902 | 0.00013902 | 0.000156 | 0.0001695 | 9.9e-05 | 9.15e-05 | 0.001617 | 0.001617 | 0.001617 | 0.0016179 | 0.0016092 | 0.046914
| Chromium VI | 18540-29-9 | Yes | Yes | 1.6555e-06 | 1.177e-06 | 7.1543e-06 | 7.1543e-06 | 7.1543e-06 | 7.1543e-06 | 7.1543e-06 | 7.1543e-06 | 5.9735e-06 | 5.9735e-06 | 5.9735e-06 | 8.3351e-06 | 8.3351e-06 | 8.3351e-06 | 8.3351e-06 | 8.3351e-06 | 8.3351e-06 | 8.3351e-06 | 8.3351e-06 | 8.3351e-06 | 8.3351e-06 | 8.3351e-06 | 8.3351e-06 | 8.3351e-06 | 8.3351e-06 | 8.3351e-06 | 8.3351e-06 | 8.3351e-06 | 8.3351e-06 | 8.3351e-06 | 8.3351e-06 | 8.3351e-06 | 7.1543e-06 | 7.1543e-06 | 3.9023e-05 | 3.9023e-05 | 6.5165e-06 | 8.3351e-06 | 8.3351e-06 | 8.3351e-06 | 8.3351e-06 | 8.3351e-06 | 8.3351e-06 | 8.3351e-06 | 8.3351e-06 | 0.00011351 | 0.00011351 | 0.00011351 | 0.00011351 | 8.971e-05 | 8.971e-05 | 8.971e-05 | 0.000123 | 0.000123 | 0.0001375 | 0.0001454 | 0.00014746 | 0.00014746 | 0.00014746 | 0.00014746 | 0.00014746 | 0.00014746 | 2.29e-05 | 2.29e-05 | 4.64e-05 | 1.94e-05 | 9.1812e-05 | 9.3138e-05 | 9.3138e-05 | 0.00011113 | 0.00010867 | 0.00011113 | 0.00011113 | 0.00011113 | 0.00011113 | 0.00010867 | 0.00011113 | 0.00010867 | 0.00010867 | 0.00010867 | 0.00010867 | 1.04e-05 | 1.13e-05 | 6.6e-06 | 6.1e-06 | 0.0001078 | 0.0001078 | 0.0001078 | 0.00010786 | 0.00010728 | 0.0048226
| Cobalt and Compounds | 7440-48-4 | Yes | Yes | 1.4223e-06 | 1.0112e-06 | 9.7342e-06 | 9.7342e-06 | 9.7342e-06 | 9.7342e-06 | 9.7342e-06 | 9.7342e-06 | 8.1276e-06 | 8.1276e-06 | 8.1276e-06 | 1.1341e-05 | 1.1341e-05 | 1.1341e-05 | 1.1341e-05 | 1.1341e-05 | 1.1341e-05 | 1.1341e-05 | 1.1341e-05 | 1.1341e-05 | 1.1341e-05 | 1.1341e-05 | 1.1341e-05 | 1.1341e-05 | 1.1341e-05 | 1.1341e-05 | 1.1341e-05 | 1.1341e-05 | 1.1341e-05 | 1.1341e-05 | 1.1341e-05 | 1.1341e-05 | 9.7342e-06 | 9.7342e-06 | 9.7342e-06 | 9.7342e-06 | 1.6255e-06 | 1.1341e-05 | 1.1341e-05 | 1.1341e-05 | 1.1341e-05 | 1.1341e-05 | 1.1341e-05 | 1.1341e-05 | 1.1341e-05 | 1.7879e-05 | 1.7879e-05 | 1.7879e-05 | 1.7879e-05 | 1.413e-05 | 1.413e-05 | 1.413e-05 | 1.9374e-05 | 1.9374e-05 | 2.1658e-05 | 2.2902e-05 | 2.3227e-05 | 2.3227e-05 | 2.3227e-05 | 2.3227e-05 | 2.3227e-05 | 2.3227e-05 | 3.607e-06 | 3.607e-06 | 7.3085e-06 | 3.0557e-06 | 2.2902e-05 | 2.3233e-05 | 2.3233e-05 | 2.7722e-05 | 2.7108e-05 | 2.7722e-05 | 2.7722e-05 | 2.7722e-05 | 2.7722e-05 | 2.7108e-05 | 2.7722e-05 | 2.7108e-05 | 2.7108e-05 | 2.7108e-05 | 2.7108e-05 | 1.6381e-06 | 1.7799e-06 | 1.0396e-06 | 9.6082e-07 | 1.698e-05 | 1.698e-05 | 1.698e-05 | 1.6989e-05 | 1.6898e-05 | 0.0012974
| Copper and Compounds | 7440-50-8 | Yes | Yes | 6.7876e-05 | 4.8257e-05 | 5.6892e-05 | 5.6892e-05 | 5.6892e-05 | 5.6892e-05 | 5.6892e-05 | 5.6892e-05 | 4.7502e-05 | 4.7502e-05 | 4.7502e-05 | 6.6282e-05 | 6.6282e-05 | 6.6282e-05 | 6.6282e-05 | 6.6282e-05 | 6.6282e-05 | 6.6282e-05 | 6.6282e-05 | 6.6282e-05 | 6.6282e-05 | 6.6282e-05 | 6.6282e-05 | 6.6282e-05 | 6.6282e-05 | 6.6282e-05 | 6.6282e-05 | 6.6282e-05 | 6.6282e-05 | 6.6282e-05 | 6.6282e-05 | 6.6282e-05 | 5.6892e-05 | 5.6892e-05 | 0.00031032 | 0.00031032 | 5.182e-05 | 6.6282e-05 | 6.6282e-05 | 6.6282e-05 | 6.6282e-05 | 6.6282e-05 | 6.6282e-05 | 6.6282e-05 | 6.6282e-05 | 0.0046539 | 0.0046539 | 0.0046539 | 0.0046539 | 0.0036781 | 0.0036781 | 0.0036781 | 0.005043 | 0.005043 | 0.0056375 | 0.0059614 | 0.0060459 | 0.0060459 | 0.0060459 | 0.0060459 | 0.0060459 | 0.0060459 | 0.0009389 | 0.0009389 | 0.0019024 | 0.0007954 | 0.0007301 | 0.00074065 | 0.00074065 | 0.00088376 | 0.00086417 | 0.00088376 | 0.00088376 | 0.00088376 | 0.00088376 | 0.00086417 | 0.00088376 | 0.00086417 | 0.00086417 | 0.00086417 | 0.00086417 | 0.0004264 | 0.0004633 | 0.0002706 | 0.0002501 | 0.0044198 | 0.0044198 | 0.0044198 | 0.0044223 | 0.0043985 | 0.13168
| Lead and Compounds | 7439-92-1 | Yes | Yes | 0.00074949 | 0.00053286 | 0.00022475 | 0.00022475 | 0.00022475 | 0.00022475 | 0.00022475 | 0.00022475 | 0.00018765 | 0.00018765 | 0.00018765 | 0.00026184 | 0.00026184 | 0.00026184 | 0.00026184 | 0.00026184 | 0.00026184 | 0.00026184 | 0.00026184 | 0.00026184 | 0.00026184 | 0.00026184 | 0.00026184 | 0.00026184 | 0.00026184 | 0.00026184 | 0.00026184 | 0.00026184 | 0.00026184 | 0.00026184 | 0.00026184 | 0.00026184 | 0.00022475 | 0.00022475 | 0.00022475 | 0.00022475 | 3.7531e-05 | 0.00026184 | 0.00026184 | 0.00026184 | 0.00026184 | 0.00026184 | 0.00026184 | 0.00026184 | 0.00026184 | 0.0094213 | 0.0094213 | 0.0094213 | 0.0094213 | 0.0074459 | 0.0074459 | 0.0074459 | 0.010209 | 0.010209 | 0.011413 | 0.012068 | 0.012239 | 0.012239 | 0.012239 | 0.012239 | 0.012239 | 0.012239 | 0.0019007 | 0.0019007 | 0.0038512 | 0.0016102 | 0.00052878 | 0.00053642 | 0.00053642 | 0.00064006 | 0.00062588 | 0.00064006 | 0.00064006 | 0.00064006 | 0.00064006 | 0.00062588 | 0.00064006 | 0.00062588 | 0.00062588 | 0.00062588 | 0.00062588 | 0.0008632 | 0.0009379 | 0.0005478 | 0.0005063 | 0.0089474 | 0.0089474 | 0.0089474 | 0.0089524 | 0.0089042 | 0.25509
| Manganese and Compounds | 7439-96-5 | Yes | Yes | 5.1321e-05 | 3.6487e-05 | 4.7576e-05 | 4.7576e-05 | 4.7576e-05 | 4.7576e-05 | 4.7576e-05 | 4.7576e-05 | 3.9724e-05 | 3.9724e-05 | 3.9724e-05 | 5.5428e-05 | 5.5428e-05 | 5.5428e-05 | 5.5428e-05 | 5.5428e-05 | 5.5428e-05 | 5.5428e-05 | 5.5428e-05 | 5.5428e-05 | 5.5428e-05 | 5.5428e-05 | 5.5428e-05 | 5.5428e-05 | 5.5428e-05 | 5.5428e-05 | 5.5428e-05 | 5.5428e-05 | 5.5428e-05 | 5.5428e-05 | 5.5428e-05 | 5.5428e-05 | 4.7576e-05 | 4.7576e-05 | 0.00025951 | 0.00025951 | 4.3335e-05 | 5.5428e-05 | 5.5428e-05 | 5.5428e-05 | 5.5428e-05 | 5.5428e-05 | 5.5428e-05 | 5.5428e-05 | 5.5428e-05 | 0.0035188 | 0.0035188 | 0.0035188 | 0.0035188 | 0.002781 | 0.002781 | 0.002781 | 0.003813 | 0.003813 | 0.0042625 | 0.0045074 | 0.0045713 | 0.0045713 | 0.0045713 | 0.0045713 | 0.0045713 | 0.0045713 | 0.0007099 | 0.0007099 | 0.0014384 | 0.0006014 | 0.00061055 | 0.00061937 | 0.00061937 | 0.00073905 | 0.00072267 | 0.00073905 | 0.00073905 | 0.00073905 | 0.00073905 | 0.00072267 | 0.00073905 | 0.00072267 | 0.00072267 | 0.00072267 | 0.00072267 | 0.0003224 | 0.0003503 | 0.0002046 | 0.0001891 | 0.0033418 | 0.0033418 | 0.0033418 | 0.0033437 | 0.0033257 | 0.10084
| Mercury and Compounds | 7439-97-6 | Yes | Yes | 0.0003612 | 0.0002568 | 1.8673e-05 | 1.8673e-05 | 1.8673e-05 | 1.8673e-05 | 1.8673e-05 | 1.8673e-05 | 1.5591e-05 | 1.5591e-05 | 1.5591e-05 | 2.1755e-05 | 2.1755e-05 | 2.1755e-05 | 2.1755e-05 | 2.1755e-05 | 2.1755e-05 | 2.1755e-05 | 2.1755e-05 | 2.1755e-05 | 2.1755e-05 | 2.1755e-05 | 2.1755e-05 | 2.1755e-05 | 2.1755e-05 | 2.1755e-05 | 2.1755e-05 | 2.1755e-05 | 2.1755e-05 | 2.1755e-05 | 2.1755e-05 | 2.1755e-05 | 1.8673e-05 | 1.8673e-05 | 9.3363e-06 | 9.3363e-06 | 1.5591e-06 | 2.1755e-05 | 2.1755e-05 | 2.1755e-05 | 2.1755e-05 | 2.1755e-05 | 2.1755e-05 | 2.1755e-05 | 2.1755e-05 | 0.0022702 | 0.0022702 | 0.0022702 | 0.0022702 | 0.0017942 | 0.0017942 | 0.0017942 | 0.00246 | 0.00246 | 0.00275 | 0.002908 | 0.0029492 | 0.0029492 | 0.0029492 | 0.0029492 | 0.0029492 | 0.0029492 | 0.000458 | 0.000458 | 0.000928 | 0.000388 | 2.1966e-05 | 2.2283e-05 | 2.2283e-05 | 2.6589e-05 | 2.6e-05 | 2.6589e-05 | 2.6589e-05 | 2.6589e-05 | 2.6589e-05 | 2.6e-05 | 2.6589e-05 | 2.6e-05 | 2.6e-05 | 2.6e-05 | 2.6e-05 | 0.000208 | 0.000226 | 0.000132 | 0.000122 | 0.002156 | 0.002156 | 0.002156 | 0.0021572 | 0.0021456 | 0.058275
| Nickel and Compounds | 7440-02-0 | Yes | Yes | 6.4565e-05 | 4.5903e-05 | 2.0647e-05 | 2.0647e-05 | 2.0647e-05 | 2.0647e-05 | 2.0647e-05 | 2.0647e-05 | 1.7239e-05 | 1.7239e-05 | 1.7239e-05 | 2.4054e-05 | 2.4054e-05 | 2.4054e-05 | 2.4054e-05 | 2.4054e-05 | 2.4054e-05 | 2.4054e-05 | 2.4054e-05 | 2.4054e-05 | 2.4054e-05 | 2.4054e-05 | 2.4054e-05 | 2.4054e-05 | 2.4054e-05 | 2.4054e-05 | 2.4054e-05 | 2.4054e-05 | 2.4054e-05 | 2.4054e-05 | 2.4054e-05 | 2.4054e-05 | 2.0647e-05 | 2.0647e-05 | 0.00011262 | 0.00011262 | 1.8806e-05 | 2.4054e-05 | 2.4054e-05 | 2.4054e-05 | 2.4054e-05 | 2.4054e-05 | 2.4054e-05 | 2.4054e-05 | 2.4054e-05 | 0.0044269 | 0.0044269 | 0.0044269 | 0.0044269 | 0.0034987 | 0.0034987 | 0.0034987 | 0.004797 | 0.004797 | 0.0053625 | 0.0056706 | 0.0057509 | 0.0057509 | 0.0057509 | 0.0057509 | 0.0057509 | 0.0057509 | 0.0008931 | 0.0008931 | 0.0018096 | 0.0007566 | 0.00026496 | 0.00026879 | 0.00026879 | 0.00032072 | 0.00031362 | 0.00032072 | 0.00032072 | 0.00032072 | 0.00032072 | 0.00031362 | 0.00032072 | 0.00031362 | 0.00031362 | 0.00031362 | 0.00031362 | 0.0004056 | 0.0004407 | 0.0002574 | 0.0002379 | 0.0042042 | 0.0042042 | 0.0042042 | 0.0042065 | 0.0041839 | 0.11591
| Phosphorus and compounds | 504 | Yes | -- | 0.00012648 | 8.9923e-05 | 0.00086561 | 0.00086561 | 0.00086561 | 0.00086561 | 0.00086561 | 0.00086561 | 0.00072274 | 0.00072274 | 0.00072274 | 0.0010085 | 0.0010085 | 0.0010085 | 0.0010085 | 0.0010085 | 0.0010085 | 0.0010085 | 0.0010085 | 0.0010085 | 0.0010085 | 0.0010085 | 0.0010085 | 0.0010085 | 0.0010085 | 0.0010085 | 0.0010085 | 0.0010085 | 0.0010085 | 0.0010085 | 0.0010085 | 0.0010085 | 0.00086561 | 0.00086561 | 0.0051937 | 0.0051937 | 0.00086729 | 0.0010085 | 0.0010085 | 0.0010085 | 0.0010085 | 0.0010085 | 0.0010085 | 0.0010085 | 0.0010085 | 0.0095394 | 0.0095394 | 0.0095394 | 0.0095394 | 0.0075392 | 0.0075392 | 0.0075392 | 0.010337 | 0.010337 | 0.011555 | 0.012219 | 0.012393 | 0.012393 | 0.012393 | 0.012393 | 0.012393 | 0.012393 | 0.0019245 | 0.0019245 | 0.0038994 | 0.0016304 | 0.012219 | 0.012396 | 0.012396 | 0.014791 | 0.014463 | 0.014791 | 0.014791 | 0.014791 | 0.014791 | 0.014463 | 0.014791 | 0.014463 | 0.014463 | 0.014463 | 0.014463 | 0.00087401 | 0.00094965 | 0.00055466 | 0.00051264 | 0.0090595 | 0.0090595 | 0.0090595 | 0.0090645 | 0.0090158 | 0.49945
| Selenium and Compounds | 7782-49-2 | Yes | Yes | 0.00019866 | 0.00014124 | 0.0002326 | 0.0002326 | 0.0002326 | 0.0002326 | 0.0002326 | 0.0002326 | 0.00019421 | 0.00019421 | 0.00019421 | 0.000271 | 0.000271 | 0.000271 | 0.000271 | 0.000271 | 0.000271 | 0.000271 | 0.000271 | 0.000271 | 0.000271 | 0.000271 | 0.000271 | 0.000271 | 0.000271 | 0.000271 | 0.000271 | 0.000271 | 0.000271 | 0.000271 | 0.000271 | 0.000271 | 0.0002326 | 0.0002326 | 0.0002326 | 0.0002326 | 3.8843e-05 | 0.000271 | 0.000271 | 0.000271 | 0.000271 | 0.000271 | 0.000271 | 0.000271 | 0.000271 | 0.0024972 | 0.0024972 | 0.0024972 | 0.0024972 | 0.0019736 | 0.0019736 | 0.0019736 | 0.002706 | 0.002706 | 0.003025 | 0.0031988 | 0.0032441 | 0.0032441 | 0.0032441 | 0.0032441 | 0.0032441 | 0.0032441 | 0.0005038 | 0.0005038 | 0.0010208 | 0.0004268 | 0.00054726 | 0.00055516 | 0.00055516 | 0.00066243 | 0.00064775 | 0.00066243 | 0.00066243 | 0.00066243 | 0.00066243 | 0.00064775 | 0.00066243 | 0.00064775 | 0.00064775 | 0.00064775 | 0.00064775 | 0.0002288 | 0.0002486 | 0.0001452 | 0.0001342 | 0.0023716 | 0.0023716 | 0.0023716 | 0.0023729 | 0.0023602 | 0.082735
| Silver and compounds | 7440-22-4 | Yes | -- | 4.3356e-06 | 3.0824e-06 | 2.9672e-05 | 2.9672e-05 | 2.9672e-05 | 2.9672e-05 | 2.9672e-05 | 2.9672e-05 | 2.4775e-05 | 2.4775e-05 | 2.4775e-05 | 3.4569e-05 | 3.4569e-05 | 3.4569e-05 | 3.4569e-05 | 3.4569e-05 | 3.4569e-05 | 3.4569e-05 | 3.4569e-05 | 3.4569e-05 | 3.4569e-05 | 3.4569e-05 | 3.4569e-05 | 3.4569e-05 | 3.4569e-05 | 3.4569e-05 | 3.4569e-05 | 3.4569e-05 | 3.4569e-05 | 3.4569e-05 | 3.4569e-05 | 3.4569e-05 | 2.9672e-05 | 2.9672e-05 | 2.9672e-05 | 2.9672e-05 | 4.9549e-06 | 3.4569e-05 | 3.4569e-05 | 3.4569e-05 | 3.4569e-05 | 3.4569e-05 | 3.4569e-05 | 3.4569e-05 | 3.4569e-05 | 5.45e-05 | 5.45e-05 | 5.45e-05 | 5.45e-05 | 4.3072e-05 | 4.3072e-05 | 4.3072e-05 | 5.9056e-05 | 5.9056e-05 | 6.6018e-05 | 6.9811e-05 | 7.08e-05 | 7.08e-05 | 7.08e-05 | 7.08e-05 | 7.08e-05 | 7.08e-05 | 1.0995e-05 | 1.0995e-05 | 2.2278e-05 | 9.3145e-06 | 6.9811e-05 | 7.0819e-05 | 7.0819e-05 | 8.4503e-05 | 8.263e-05 | 8.4503e-05 | 8.4503e-05 | 8.4503e-05 | 8.4503e-05 | 8.263e-05 | 8.4503e-05 | 8.263e-05 | 8.263e-05 | 8.263e-05 | 8.263e-05 | 4.9934e-06 | 5.4255e-06 | 3.1689e-06 | 2.9288e-06 | 5.1758e-05 | 5.1758e-05 | 5.1758e-05 | 5.1787e-05 | 5.1508e-05 | 0.0039548
| Thallium and compounds | 7440-28-0 | Yes | -- | 2.168e-05 | 1.5414e-05 | 0.00014838 | 0.00014838 | 0.00014838 | 0.00014838 | 0.00014838 | 0.00014838 | 0.00012389 | 0.00012389 | 0.00012389 | 0.00017287 | 0.00017287 | 0.00017287 | 0.00017287 | 0.00017287 | 0.00017287 | 0.00017287 | 0.00017287 | 0.00017287 | 0.00017287 | 0.00017287 | 0.00017287 | 0.00017287 | 0.00017287 | 0.00017287 | 0.00017287 | 0.00017287 | 0.00017287 | 0.00017287 | 0.00017287 | 0.00017287 | 0.00014838 | 0.00014838 | 0.00014838 | 0.00014838 | 2.4778e-05 | 0.00017287 | 0.00017287 | 0.00017287 | 0.00017287 | 0.00017287 | 0.00017287 | 0.00017287 | 0.00017287 | 0.00027253 | 0.00027253 | 0.00027253 | 0.00027253 | 0.00021539 | 0.00021539 | 0.00021539 | 0.00029532 | 0.00029532 | 0.00033013 | 0.0003491 | 0.00035404 | 0.00035404 | 0.00035404 | 0.00035404 | 0.00035404 | 0.00035404 | 5.4981e-05 | 5.4981e-05 | 0.0001114 | 4.6578e-05 | 0.0003491 | 0.00035414 | 0.00035414 | 0.00042256 | 0.0004132 | 0.00042256 | 0.00042256 | 0.00042256 | 0.00042256 | 0.0004132 | 0.00042256 | 0.0004132 | 0.0004132 | 0.0004132 | 0.0004132 | 2.497e-05 | 2.7131e-05 | 1.5846e-05 | 1.4646e-05 | 0.00025882 | 0.00025882 | 0.00025882 | 0.00025897 | 0.00025757 | 0.019776
| Zinc and Compounds | 7440-66-6 | Yes | -- | 0.00047192 | 0.00033552 | 0.0032298 | 0.0032298 | 0.0032298 | 0.0032298 | 0.0032298 | 0.0032298 | 0.0026967 | 0.0026967 | 0.0026967 | 0.0037628 | 0.0037628 | 0.0037628 | 0.0037628 | 0.0037628 | 0.0037628 | 0.0037628 | 0.0037628 | 0.0037628 | 0.0037628 | 0.0037628 | 0.0037628 | 0.0037628 | 0.0037628 | 0.0037628 | 0.0037628 | 0.0037628 | 0.0037628 | 0.0037628 | 0.0037628 | 0.0037628 | 0.0032298 | 0.0032298 | 0.0032298 | 0.0032298 | 0.00053934 | 0.0037628 | 0.0037628 | 0.0037628 | 0.0037628 | 0.0037628 | 0.0037628 | 0.0037628 | 0.0037628 | 0.0059322 | 0.0059322 | 0.0059322 | 0.0059322 | 0.0046884 | 0.0046884 | 0.0046884 | 0.0064282 | 0.0064282 | 0.007186 | 0.0075989 | 0.0077065 | 0.0077065 | 0.0077065 | 0.0077065 | 0.0077065 | 0.0077065 | 0.0011968 | 0.0011968 | 0.0024249 | 0.0010139 | 0.0075989 | 0.0077086 | 0.0077086 | 0.0091981 | 0.0089943 | 0.0091981 | 0.0091981 | 0.0091981 | 0.0091981 | 0.0089943 | 0.0091981 | 0.0089943 | 0.0089943 | 0.0089943 | 0.0089943 | 0.00054352 | 0.00059056 | 0.00034493 | 0.0003188 | 0.0056338 | 0.0056338 | 0.0056338 | 0.005637 | 0.0056066 | 0.43048
ORGANIC COMPOUNDS
| 1,3-Butadiene | 106-99-0 | Yes | Yes | 0.019739 | 0.014034 | 0.13509 | 0.13509 | 0.13509 | 0.13509 | 0.13509 | 0.13509 | 0.1128 | 0.1128 | 0.1128 | 0.15739 | 0.15739 | 0.15739 | 0.15739 | 0.15739 | 0.15739 | 0.15739 | 0.15739 | 0.15739 | 0.15739 | 0.15739 | 0.15739 | 0.15739 | 0.15739 | 0.15739 | 0.15739 | 0.15739 | 0.15739 | 0.15739 | 0.15739 | 0.15739 | 0.13509 | 0.13509 | 0.1441 | 0.1441 | 0.024063 | 0.15739 | 0.15739 | 0.15739 | 0.15739 | 0.15739 | 0.15739 | 0.15739 | 0.15739 | 0.24813 | 0.24813 | 0.24813 | 0.24813 | 0.1961 | 0.1961 | 0.1961 | 0.26887 | 0.26887 | 0.30057 | 0.31784 | 0.32234 | 0.32234 | 0.32234 | 0.32234 | 0.32234 | 0.32234 | 0.050058 | 0.050058 | 0.10143 | 0.042408 | 0.31784 | 0.32243 | 0.32243 | 0.38473 | 0.3762 | 0.38473 | 0.38473 | 0.38473 | 0.38473 | 0.3762 | 0.38473 | 0.3762 | 0.3762 | 0.3762 | 0.3762 | 0.022734 | 0.024701 | 0.014427 | 0.013334 | 0.23565 | 0.23565 | 0.23565 | 0.23578 | 0.23451 | 18.0251
| 2-Methyl naphthalene | 91-57-6 | Yes | -- | -- | -- | 0.0089156 | 0.0089156 | 0.0089156 | 0.0089156 | 0.0089156 | 0.0089156 | 0.0074441 | 0.0074441 | 0.0074441 | 0.010387 | 0.010387 | 0.010387 | 0.010387 | 0.010387 | 0.010387 | 0.010387 | 0.010387 | 0.010387 | 0.010387 | 0.010387 | 0.010387 | 0.010387 | 0.010387 | 0.010387 | 0.010387 | 0.010387 | 0.010387 | 0.010387 | 0.010387 | 0.010387 | 0.0089156 | 0.0089156 | 0.009425 | 0.009425 | 0.0015739 | 0.010387 | 0.010387 | 0.010387 | 0.010387 | 0.010387 | 0.010387 | 0.010387 | 0.010387 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.01798 | 0.018239 | 0.018239 | 0.021763 | 0.021281 | 0.021763 | 0.021763 | 0.021763 | 0.021763 | 0.021281 | 0.021763 | 0.021281 | 0.021281 | 0.021281 | 0.021281 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.72803
| Acenaphthene | 83-32-9 | Yes | -- | -- | -- | 0.00051735 | 0.00051735 | 0.00051735 | 0.00051735 | 0.00051735 | 0.00051735 | 0.00043197 | 0.00043197 | 0.00043197 | 0.00060274 | 0.00060274 | 0.00060274 | 0.00060274 | 0.00060274 | 0.00060274 | 0.00060274 | 0.00060274 | 0.00060274 | 0.00060274 | 0.00060274 | 0.00060274 | 0.00060274 | 0.00060274 | 0.00060274 | 0.00060274 | 0.00060274 | 0.00060274 | 0.00060274 | 0.00060274 | 0.00060274 | 0.00051735 | 0.00051735 | 0.000563 | 0.000563 | 9.4016e-05 | 0.00060274 | 0.00060274 | 0.00060274 | 0.00060274 | 0.00060274 | 0.00060274 | 0.00060274 | 0.00060274 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.001074 | 0.0010895 | 0.0010895 | 0.0013 | 0.0012712 | 0.0013 | 0.0013 | 0.0013 | 0.0013 | 0.0012712 | 0.0013 | 0.0012712 | 0.0012712 | 0.0012712 | 0.0012712 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.042815
| Acenaphthylene | 208-96-8 | Yes | -- | -- | -- | 0.00062064 | 0.00062064 | 0.00062064 | 0.00062064 | 0.00062064 | 0.00062064 | 0.0005182 | 0.0005182 | 0.0005182 | 0.00072307 | 0.00072307 | 0.00072307 | 0.00072307 | 0.00072307 | 0.00072307 | 0.00072307 | 0.00072307 | 0.00072307 | 0.00072307 | 0.00072307 | 0.00072307 | 0.00072307 | 0.00072307 | 0.00072307 | 0.00072307 | 0.00072307 | 0.00072307 | 0.00072307 | 0.00072307 | 0.00072307 | 0.00062064 | 0.00062064 | 0.00062064 | 0.00062064 | 0.00010364 | 0.00072307 | 0.00072307 | 0.00072307 | 0.00072307 | 0.00072307 | 0.00072307 | 0.00072307 | 0.00072307 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.0011839 | 0.001201 | 0.001201 | 0.0014331 | 0.0014014 | 0.0014331 | 0.0014331 | 0.0014331 | 0.0014331 | 0.0014014 | 0.0014331 | 0.0014014 | 0.0014014 | 0.0014014 | 0.0014014 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.049427
| Acetaldehyde | 75-07-0 | Yes | Yes | 0.087716 | 0.062363 | 0.60031 | 0.60031 | 0.60031 | 0.60031 | 0.60031 | 0.60031 | 0.50123 | 0.50123 | 0.50123 | 0.6994 | 0.6994 | 0.6994 | 0.6994 | 0.6994 | 0.6994 | 0.6994 | 0.6994 | 0.6994 | 0.6994 | 0.6994 | 0.6994 | 0.6994 | 0.6994 | 0.6994 | 0.6994 | 0.6994 | 0.6994 | 0.6994 | 0.6994 | 0.6994 | 0.60031 | 0.60031 | 0.66521 | 0.66521 | 0.11108 | 0.6994 | 0.6994 | 0.6994 | 0.6994 | 0.6994 | 0.6994 | 0.6994 | 0.6994 | 0.89401 | 0.89401 | 0.89401 | 0.89401 | 0.70656 | 0.70656 | 0.70656 | 0.96876 | 0.96876 | 1.083 | 1.1452 | 1.1614 | 1.1614 | 1.1614 | 1.1614 | 1.1614 | 1.1614 | 0.18036 | 0.18036 | 0.36545 | 0.1528 | 1.1452 | 1.1617 | 1.1617 | 1.3862 | 1.3555 | 1.3862 | 1.3862 | 1.3862 | 1.3862 | 1.3555 | 1.3862 | 1.3555 | 1.3555 | 1.3555 | 1.3555 | 0.081911 | 0.089 | 0.051982 | 0.048044 | 0.84904 | 0.84904 | 0.84904 | 0.84951 | 0.84495 | 70.3202
| Acrolein | 107-02-8 | Yes | Yes | 0.003078 | 0.0021884 | 0.021065 | 0.021065 | 0.021065 | 0.021065 | 0.021065 | 0.021065 | 0.017589 | 0.017589 | 0.017589 | 0.024542 | 0.024542 | 0.024542 | 0.024542 | 0.024542 | 0.024542 | 0.024542 | 0.024542 | 0.024542 | 0.024542 | 0.024542 | 0.024542 | 0.024542 | 0.024542 | 0.024542 | 0.024542 | 0.024542 | 0.024542 | 0.024542 | 0.024542 | 0.024542 | 0.021065 | 0.021065 | 0.023874 | 0.023874 | 0.0039868 | 0.024542 | 0.024542 | 0.024542 | 0.024542 | 0.024542 | 0.024542 | 0.024542 | 0.024542 | 0.038692 | 0.038692 | 0.038692 | 0.038692 | 0.030579 | 0.030579 | 0.030579 | 0.041926 | 0.041926 | 0.046869 | 0.049562 | 0.050264 | 0.050264 | 0.050264 | 0.050264 | 0.050264 | 0.050264 | 0.0078058 | 0.0078058 | 0.015816 | 0.0066128 | 0.049562 | 0.050278 | 0.050278 | 0.059992 | 0.058663 | 0.059992 | 0.059992 | 0.059992 | 0.059992 | 0.058663 | 0.059992 | 0.058663 | 0.058663 | 0.058663 | 0.058663 | 0.003545 | 0.0038518 | 0.0022497 | 0.0020793 | 0.036745 | 0.036745 | 0.036745 | 0.036766 | 0.036568 | 2.8138
| Anthracene | 120-12-7 | Yes | -- | -- | -- | 0.00042139 | 0.00042139 | 0.00042139 | 0.00042139 | 0.00042139 | 0.00042139 | 0.00035184 | 0.00035184 | 0.00035184 | 0.00049094 | 0.00049094 | 0.00049094 | 0.00049094 | 0.00049094 | 0.00049094 | 0.00049094 | 0.00049094 | 0.00049094 | 0.00049094 | 0.00049094 | 0.00049094 | 0.00049094 | 0.00049094 | 0.00049094 | 0.00049094 | 0.00049094 | 0.00049094 | 0.00049094 | 0.00049094 | 0.00049094 | 0.00042139 | 0.00042139 | 0.00034648 | 0.00034648 | 5.7858e-05 | 0.00049094 | 0.00049094 | 0.00049094 | 0.00049094 | 0.00049094 | 0.00049094 | 0.00049094 | 0.00049094 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.00066095 | 0.0006705 | 0.0006705 | 0.00080005 | 0.00078233 | 0.00080005 | 0.00080005 | 0.00080005 | 0.00080005 | 0.00078233 | 0.00080005 | 0.00078233 | 0.00078233 | 0.00078233 | 0.00078233 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.030911
| Benzene | 71-43-2 | Yes | Yes | 0.019735 | 0.014031 | 0.13506 | 0.13506 | 0.13506 | 0.13506 | 0.13506 | 0.13506 | 0.11277 | 0.11277 | 0.11277 | 0.15735 | 0.15735 | 0.15735 | 0.15735 | 0.15735 | 0.15735 | 0.15735 | 0.15735 | 0.15735 | 0.15735 | 0.15735 | 0.15735 | 0.15735 | 0.15735 | 0.15735 | 0.15735 | 0.15735 | 0.15735 | 0.15735 | 0.15735 | 0.15735 | 0.13506 | 0.13506 | 0.14278 | 0.14278 | 0.023843 | 0.15735 | 0.15735 | 0.15735 | 0.15735 | 0.15735 | 0.15735 | 0.15735 | 0.15735 | 0.21263 | 0.21263 | 0.21263 | 0.21263 | 0.16805 | 0.16805 | 0.16805 | 0.23041 | 0.23041 | 0.25757 | 0.27237 | 0.27623 | 0.27623 | 0.27623 | 0.27623 | 0.27623 | 0.27623 | 0.042897 | 0.042897 | 0.086919 | 0.036341 | 0.27237 | 0.2763 | 0.2763 | 0.32969 | 0.32239 | 0.32969 | 0.32969 | 0.32969 | 0.32969 | 0.32239 | 0.32969 | 0.32239 | 0.32239 | 0.32239 | 0.32239 | 0.019482 | 0.021168 | 0.012363 | 0.011427 | 0.20194 | 0.20194 | 0.20194 | 0.20205 | 0.20096 | 16.3478
| Chlorobenzene | 108-90-7 | Yes | Yes | 2.2397e-05 | 1.5923e-05 | 0.00015328 | 0.00015328 | 0.00015328 | 0.00015328 | 0.00015328 | 0.00015328 | 0.00012798 | 0.00012798 | 0.00012798 | 0.00017858 | 0.00017858 | 0.00017858 | 0.00017858 | 0.00017858 | 0.00017858 | 0.00017858 | 0.00017858 | 0.00017858 | 0.00017858 | 0.00017858 | 0.00017858 | 0.00017858 | 0.00017858 | 0.00017858 | 0.00017858 | 0.00017858 | 0.00017858 | 0.00017858 | 0.00017858 | 0.00017858 | 0.00015328 | 0.00015328 | 0.00015328 | 0.00015328 | 2.5596e-05 | 0.00017858 | 0.00017858 | 0.00017858 | 0.00017858 | 0.00017858 | 0.00017858 | 0.00017858 | 0.00017858 | 0.00022827 | 0.00022827 | 0.00022827 | 0.00022827 | 0.00018041 | 0.00018041 | 0.00018041 | 0.00024735 | 0.00024735 | 0.00027651 | 0.0002924 | 0.00029654 | 0.00029654 | 0.00029654 | 0.00029654 | 0.00029654 | 0.00029654 | 4.6052e-05 | 4.6052e-05 | 9.331e-05 | 3.9013e-05 | 0.0002924 | 0.00029662 | 0.00029662 | 0.00035394 | 0.00034609 | 0.00035394 | 0.00035394 | 0.00035394 | 0.00035394 | 0.00034609 | 0.00035394 | 0.00034609 | 0.00034609 | 0.00034609 | 0.00034609 | 2.0914e-05 | 2.2724e-05 | 1.3273e-05 | 1.2267e-05 | 0.00021679 | 0.00021679 | 0.00021679 | 0.00021691 | 0.00021574 | 0.017919
| Ethylbenzene | 100-41-4 | Yes | Yes | 0.0010887 | 0.00077399 | 0.0074506 | 0.0074506 | 0.0074506 | 0.0074506 | 0.0074506 | 0.0074506 | 0.0062209 | 0.0062209 | 0.0062209 | 0.0086803 | 0.0086803 | 0.0086803 | 0.0086803 | 0.0086803 | 0.0086803 | 0.0086803 | 0.0086803 | 0.0086803 | 0.0086803 | 0.0086803 | 0.0086803 | 0.0086803 | 0.0086803 | 0.0086803 | 0.0086803 | 0.0086803 | 0.0086803 | 0.0086803 | 0.0086803 | 0.0086803 | 0.0074506 | 0.0074506 | 0.0083537 | 0.0083537 | 0.001395 | 0.0086803 | 0.0086803 | 0.0086803 | 0.0086803 | 0.0086803 | 0.0086803 | 0.0086803 | 0.0086803 | 0.012441 | 0.012441 | 0.012441 | 0.012441 | 0.0098322 | 0.0098322 | 0.0098322 | 0.013481 | 0.013481 | 0.01507 | 0.015936 | 0.016162 | 0.016162 | 0.016162 | 0.016162 | 0.016162 | 0.016162 | 0.0025098 | 0.0025098 | 0.0050854 | 0.0021262 | 0.015936 | 0.016166 | 0.016166 | 0.01929 | 0.018862 | 0.01929 | 0.01929 | 0.01929 | 0.01929 | 0.018862 | 0.01929 | 0.018862 | 0.018862 | 0.018862 | 0.018862 | 0.0011398 | 0.0012385 | 0.00072336 | 0.00066856 | 0.011815 | 0.011815 | 0.011815 | 0.011821 | 0.011758 | 0.93636
| Formaldehyde | 50-00-0 | Yes | Yes | 0.183 | 0.1301 | 1.9685 | 1.9685 | 1.9685 | 1.9685 | 1.9685 | 1.9685 | 1.6436 | 1.6436 | 1.6436 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 1.9685 | 1.9685 | 2.306 | 2.306 | 0.38507 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 2.2934 | 1.9717 | 1.9717 | 1.9717 | 1.9717 | 1.5583 | 1.5583 | 1.5583 | 2.1365 | 2.1365 | 2.3884 | 2.5256 | 2.5614 | 2.5614 | 2.5614 | 2.5614 | 2.5614 | 2.5614 | 0.39778 | 0.39778 | 0.80598 | 0.33698 | 3.9698 | 4.0271 | 4.0271 | 4.8052 | 4.6988 | 4.8052 | 4.8052 | 4.8052 | 4.8052 | 4.6988 | 4.8052 | 4.6988 | 4.6988 | 4.6988 | 4.6988 | 0.18065 | 0.19628 | 0.11464 | 0.10596 | 1.8725 | 1.8725 | 1.8725 | 1.8736 | 1.8635 | 210.5538
| Hexane | 110-54-3 | Yes | Yes | 0.0032566 | 0.0023153 | 0.022288 | 0.022288 | 0.022288 | 0.022288 | 0.022288 | 0.022288 | 0.018609 | 0.018609 | 0.018609 | 0.025966 | 0.025966 | 0.025966 | 0.025966 | 0.025966 | 0.025966 | 0.025966 | 0.025966 | 0.025966 | 0.025966 | 0.025966 | 0.025966 | 0.025966 | 0.025966 | 0.025966 | 0.025966 | 0.025966 | 0.025966 | 0.025966 | 0.025966 | 0.025966 | 0.022288 | 0.022288 | 0.025073 | 0.025073 | 0.004187 | 0.025966 | 0.025966 | 0.025966 | 0.025966 | 0.025966 | 0.025966 | 0.025966 | 0.025966 | 0.030702 | 0.030702 | 0.030702 | 0.030702 | 0.024265 | 0.024265 | 0.024265 | 0.033269 | 0.033269 | 0.037191 | 0.039328 | 0.039885 | 0.039885 | 0.039885 | 0.039885 | 0.039885 | 0.039885 | 0.006194 | 0.006194 | 0.01255 | 0.0052473 | 0.039328 | 0.039896 | 0.039896 | 0.047604 | 0.04655 | 0.047604 | 0.047604 | 0.047604 | 0.047604 | 0.04655 | 0.047604 | 0.04655 | 0.04655 | 0.04655 | 0.04655 | 0.002813 | 0.0030564 | 0.0017852 | 0.0016499 | 0.029158 | 0.029158 | 0.029158 | 0.029174 | 0.029017 | 2.4942
| Propylene | 115-07-1 | Yes | Yes | 0.052632 | 0.037419 | 0.3602 | 0.3602 | 0.3602 | 0.3602 | 0.3602 | 0.3602 | 0.30075 | 0.30075 | 0.30075 | 0.41966 | 0.41966 | 0.41966 | 0.41966 | 0.41966 | 0.41966 | 0.41966 | 0.41966 | 0.41966 | 0.41966 | 0.41966 | 0.41966 | 0.41966 | 0.41966 | 0.41966 | 0.41966 | 0.41966 | 0.41966 | 0.41966 | 0.41966 | 0.41966 | 0.3602 | 0.3602 | 0.3602 | 0.3602 | 0.060151 | 0.41966 | 0.41966 | 0.41966 | 0.41966 | 0.41966 | 0.41966 | 0.41966 | 0.41966 | 0.53643 | 0.53643 | 0.53643 | 0.53643 | 0.42396 | 0.42396 | 0.42396 | 0.58128 | 0.58128 | 0.6498 | 0.68714 | 0.69687 | 0.69687 | 0.69687 | 0.69687 | 0.69687 | 0.69687 | 0.10822 | 0.10822 | 0.21928 | 0.091681 | 0.68714 | 0.69706 | 0.69706 | 0.83175 | 0.81332 | 0.83175 | 0.83175 | 0.83175 | 0.83175 | 0.81332 | 0.83175 | 0.81332 | 0.81332 | 0.81332 | 0.81332 | 0.049149 | 0.053402 | 0.031191 | 0.028828 | 0.50945 | 0.50945 | 0.50945 | 0.50973 | 0.50699 | 42.1096
| Toluene | 108-88-3 | Yes | Yes | 0.008613 | 0.0061235 | 0.058946 | 0.058946 | 0.058946 | 0.058946 | 0.058946 | 0.058946 | 0.049217 | 0.049217 | 0.049217 | 0.068675 | 0.068675 | 0.068675 | 0.068675 | 0.068675 | 0.068675 | 0.068675 | 0.068675 | 0.068675 | 0.068675 | 0.068675 | 0.068675 | 0.068675 | 0.068675 | 0.068675 | 0.068675 | 0.068675 | 0.068675 | 0.068675 | 0.068675 | 0.068675 | 0.058946 | 0.058946 | 0.080778 | 0.080778 | 0.013489 | 0.068675 | 0.068675 | 0.068675 | 0.068675 | 0.068675 | 0.068675 | 0.068675 | 0.068675 | 0.1203 | 0.1203 | 0.1203 | 0.1203 | 0.095074 | 0.095074 | 0.095074 | 0.13036 | 0.13036 | 0.14572 | 0.15409 | 0.15628 | 0.15628 | 0.15628 | 0.15628 | 0.15628 | 0.15628 | 0.024269 | 0.024269 | 0.049175 | 0.02056 | 0.15409 | 0.15632 | 0.15632 | 0.18652 | 0.18239 | 0.18652 | 0.18652 | 0.18652 | 0.18652 | 0.18239 | 0.18652 | 0.18239 | 0.18239 | 0.18239 | 0.18239 | 0.011022 | 0.011976 | 0.0069947 | 0.0064648 | 0.11425 | 0.11425 | 0.11425 | 0.11431 | 0.1137 | 8.4709
| Xylene (mixed isomers) | 1330-20-7 | Yes | Yes | 0.0043631 | 0.003102 | 0.02986 | 0.02986 | 0.02986 | 0.02986 | 0.02986 | 0.02986 | 0.024932 | 0.024932 | 0.024932 | 0.034789 | 0.034789 | 0.034789 | 0.034789 | 0.034789 | 0.034789 | 0.034789 | 0.034789 | 0.034789 | 0.034789 | 0.034789 | 0.034789 | 0.034789 | 0.034789 | 0.034789 | 0.034789 | 0.034789 | 0.034789 | 0.034789 | 0.034789 | 0.034789 | 0.02986 | 0.02986 | 0.032495 | 0.032495 | 0.0054264 | 0.034789 | 0.034789 | 0.034789 | 0.034789 | 0.034789 | 0.034789 | 0.034789 | 0.034789 | 0.048393 | 0.048393 | 0.048393 | 0.048393 | 0.038246 | 0.038246 | 0.038246 | 0.052439 | 0.052439 | 0.058621 | 0.061989 | 0.062867 | 0.062867 | 0.062867 | 0.062867 | 0.062867 | 0.062867 | 0.009763 | 0.009763 | 0.019782 | 0.0082708 | 0.061989 | 0.062884 | 0.062884 | 0.075034 | 0.073372 | 0.075034 | 0.075034 | 0.075034 | 0.075034 | 0.073372 | 0.075034 | 0.073372 | 0.073372 | 0.073372 | 0.073372 | 0.0044339 | 0.0048176 | 0.0028138 | 0.0026006 | 0.045959 | 0.045959 | 0.045959 | 0.045984 | 0.045737 | 3.6815
INORGANIC COMPOUNDS
| Ammonia | 7664-41-7 | Yes | Yes | 0.24212 | 0.17214 | 1.6571 | 1.6571 | 1.6571 | 1.6571 | 1.6571 | 1.6571 | 1.3836 | 1.3836 | 1.3836 | 1.9306 | 1.9306 | 1.9306 | 1.9306 | 1.9306 | 1.9306 | 1.9306 | 1.9306 | 1.9306 | 1.9306 | 1.9306 | 1.9306 | 1.9306 | 1.9306 | 1.9306 | 1.9306 | 1.9306 | 1.9306 | 1.9306 | 1.9306 | 1.9306 | 1.6571 | 1.6571 | 1.6571 | 1.6571 | 0.27671 | 1.9306 | 1.9306 | 1.9306 | 1.9306 | 1.9306 | 1.9306 | 1.9306 | 1.9306 | 0.91307 | 0.91307 | 0.91307 | 0.91307 | 0.72163 | 0.72163 | 0.72163 | 0.98941 | 0.98941 | 1.106 | 1.1696 | 1.1862 | 1.1862 | 1.1862 | 1.1862 | 1.1862 | 1.1862 | 0.18421 | 0.18421 | 0.37324 | 0.15605 | 1.1696 | 1.1865 | 1.1865 | 1.4157 | 1.3844 | 1.4157 | 1.4157 | 1.4157 | 1.4157 | 1.3844 | 1.4157 | 1.3844 | 1.3844 | 1.3844 | 1.3844 | 0.083658 | 0.090897 | 0.05309 | 0.049068 | 0.86714 | 0.86714 | 0.86714 | 0.86763 | 0.86296 | 120.4369
| Hydrochloric Acid | 7647-01-0 | Yes | Yes | 0.056385 | 0.040087 | 0.38589 | 0.38589 | 0.38589 | 0.38589 | 0.38589 | 0.38589 | 0.3222 | 0.3222 | 0.3222 | 0.44958 | 0.44958 | 0.44958 | 0.44958 | 0.44958 | 0.44958 | 0.44958 | 0.44958 | 0.44958 | 0.44958 | 0.44958 | 0.44958 | 0.44958 | 0.44958 | 0.44958 | 0.44958 | 0.44958 | 0.44958 | 0.44958 | 0.44958 | 0.44958 | 0.38589 | 0.38589 | 0.11577 | 0.11577 | 0.019332 | 0.44958 | 0.44958 | 0.44958 | 0.44958 | 0.44958 | 0.44958 | 0.44958 | 0.44958 | 0.21263 | 0.21263 | 0.21263 | 0.21263 | 0.16805 | 0.16805 | 0.16805 | 0.23041 | 0.23041 | 0.25757 | 0.27237 | 0.27623 | 0.27623 | 0.27623 | 0.27623 | 0.27623 | 0.27623 | 0.042897 | 0.042897 | 0.086919 | 0.036341 | 0.27237 | 0.2763 | 0.2763 | 0.32969 | 0.32239 | 0.32969 | 0.32969 | 0.32969 | 0.32969 | 0.32239 | 0.32969 | 0.32239 | 0.32239 | 0.32239 | 0.32239 | 0.019482 | 0.021168 | 0.012363 | 0.011427 | 0.20194 | 0.20194 | 0.20194 | 0.20205 | 0.20096 | 27.4614
POLYCYCLIC AROMATIC HYDROCARBONS (PAH)
| Benz[a]anthracene | 56-55-3 | Yes | Yes | -- | -- | 3.7202e-05 | 3.7202e-05 | 3.7202e-05 | 3.7202e-05 | 3.7202e-05 | 3.7202e-05 | 3.1062e-05 | 3.1062e-05 | 3.1062e-05 | 4.3342e-05 | 4.3342e-05 | 4.3342e-05 | 4.3342e-05 | 4.3342e-05 | 4.3342e-05 | 4.3342e-05 | 4.3342e-05 | 4.3342e-05 | 4.3342e-05 | 4.3342e-05 | 4.3342e-05 | 4.3342e-05 | 4.3342e-05 | 4.3342e-05 | 4.3342e-05 | 4.3342e-05 | 4.3342e-05 | 4.3342e-05 | 4.3342e-05 | 4.3342e-05 | 3.7202e-05 | 3.7202e-05 | 3.7202e-05 | 3.7202e-05 | 6.2123e-06 | 4.3342e-05 | 4.3342e-05 | 4.3342e-05 | 4.3342e-05 | 4.3342e-05 | 4.3342e-05 | 4.3342e-05 | 4.3342e-05 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 7.0967e-05 | 7.1992e-05 | 7.1992e-05 | 8.5903e-05 | 8.3999e-05 | 8.5903e-05 | 8.5903e-05 | 8.5903e-05 | 8.5903e-05 | 8.3999e-05 | 8.5903e-05 | 8.3999e-05 | 8.3999e-05 | 8.3999e-05 | 8.3999e-05 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.0029627
| Benzo(a)pyrene | 50-32-8 | Yes | Yes | 3.7287e-06 | 2.651e-06 | 1.0429e-05 | 1.0429e-05 | 1.0429e-05 | 1.0429e-05 | 1.0429e-05 | 1.0429e-05 | 8.7075e-06 | 8.7075e-06 | 8.7075e-06 | 1.215e-05 | 1.215e-05 | 1.215e-05 | 1.215e-05 | 1.215e-05 | 1.215e-05 | 1.215e-05 | 1.215e-05 | 1.215e-05 | 1.215e-05 | 1.215e-05 | 1.215e-05 | 1.215e-05 | 1.215e-05 | 1.215e-05 | 1.215e-05 | 1.215e-05 | 1.215e-05 | 1.215e-05 | 1.215e-05 | 1.215e-05 | 1.0429e-05 | 1.0429e-05 | 1.1025e-05 | 1.1025e-05 | 1.841e-06 | 1.215e-05 | 1.215e-05 | 1.215e-05 | 1.215e-05 | 1.215e-05 | 1.215e-05 | 1.215e-05 | 1.215e-05 | 4.0175e-05 | 4.0175e-05 | 4.0175e-05 | 4.0175e-05 | 3.1752e-05 | 3.1752e-05 | 3.1752e-05 | 4.3534e-05 | 4.3534e-05 | 4.8666e-05 | 5.1462e-05 | 5.2191e-05 | 5.2191e-05 | 5.2191e-05 | 5.2191e-05 | 5.2191e-05 | 5.2191e-05 | 8.1051e-06 | 8.1051e-06 | 1.6423e-05 | 6.8664e-06 | 2.1031e-05 | 2.1335e-05 | 2.1335e-05 | 2.5457e-05 | 2.4893e-05 | 2.5457e-05 | 2.5457e-05 | 2.5457e-05 | 2.5457e-05 | 2.4893e-05 | 2.5457e-05 | 2.4893e-05 | 2.4893e-05 | 2.4893e-05 | 2.4893e-05 | 3.6809e-06 | 3.9995e-06 | 2.336e-06 | 2.159e-06 | 3.8154e-05 | 3.8154e-05 | 3.8154e-05 | 3.8176e-05 | 3.797e-05 | 0.0018566
| Benzo[b]fluoranthene | 205-99-2 | Yes | Yes | -- | -- | 3.3992e-05 | 3.3992e-05 | 3.3992e-05 | 3.3992e-05 | 3.3992e-05 | 3.3992e-05 | 2.8382e-05 | 2.8382e-05 | 2.8382e-05 | 3.9603e-05 | 3.9603e-05 | 3.9603e-05 | 3.9603e-05 | 3.9603e-05 | 3.9603e-05 | 3.9603e-05 | 3.9603e-05 | 3.9603e-05 | 3.9603e-05 | 3.9603e-05 | 3.9603e-05 | 3.9603e-05 | 3.9603e-05 | 3.9603e-05 | 3.9603e-05 | 3.9603e-05 | 3.9603e-05 | 3.9603e-05 | 3.9603e-05 | 3.9603e-05 | 3.3992e-05 | 3.3992e-05 | 3.3992e-05 | 3.3992e-05 | 5.6764e-06 | 3.9603e-05 | 3.9603e-05 | 3.9603e-05 | 3.9603e-05 | 3.9603e-05 | 3.9603e-05 | 3.9603e-05 | 3.9603e-05 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 6.4845e-05 | 6.5781e-05 | 6.5781e-05 | 7.8492e-05 | 7.6752e-05 | 7.8492e-05 | 7.8492e-05 | 7.8492e-05 | 7.8492e-05 | 7.6752e-05 | 7.8492e-05 | 7.6752e-05 | 7.6752e-05 | 7.6752e-05 | 7.6752e-05 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.0027071
| Benzo[e]pyrene | 192-97-2 | Yes | -- | -- | -- | 2.3828e-05 | 2.3828e-05 | 2.3828e-05 | 2.3828e-05 | 2.3828e-05 | 2.3828e-05 | 1.9896e-05 | 1.9896e-05 | 1.9896e-05 | 2.7761e-05 | 2.7761e-05 | 2.7761e-05 | 2.7761e-05 | 2.7761e-05 | 2.7761e-05 | 2.7761e-05 | 2.7761e-05 | 2.7761e-05 | 2.7761e-05 | 2.7761e-05 | 2.7761e-05 | 2.7761e-05 | 2.7761e-05 | 2.7761e-05 | 2.7761e-05 | 2.7761e-05 | 2.7761e-05 | 2.7761e-05 | 2.7761e-05 | 2.7761e-05 | 2.3828e-05 | 2.3828e-05 | 2.519e-05 | 2.519e-05 | 4.2065e-06 | 2.7761e-05 | 2.7761e-05 | 2.7761e-05 | 2.7761e-05 | 2.7761e-05 | 2.7761e-05 | 2.7761e-05 | 2.7761e-05 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 4.8053e-05 | 4.8747e-05 | 4.8747e-05 | 5.8166e-05 | 5.6877e-05 | 5.8166e-05 | 5.8166e-05 | 5.8166e-05 | 5.8166e-05 | 5.6877e-05 | 5.8166e-05 | 5.6877e-05 | 5.6877e-05 | 5.6877e-05 | 5.6877e-05 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.0019458
| Benzo[g,h,i]perylene | 191-24-2 | Yes | Yes | -- | -- | 1.6764e-05 | 1.6764e-05 | 1.6764e-05 | 1.6764e-05 | 1.6764e-05 | 1.6764e-05 | 1.3997e-05 | 1.3997e-05 | 1.3997e-05 | 1.9531e-05 | 1.9531e-05 | 1.9531e-05 | 1.9531e-05 | 1.9531e-05 | 1.9531e-05 | 1.9531e-05 | 1.9531e-05 | 1.9531e-05 | 1.9531e-05 | 1.9531e-05 | 1.9531e-05 | 1.9531e-05 | 1.9531e-05 | 1.9531e-05 | 1.9531e-05 | 1.9531e-05 | 1.9531e-05 | 1.9531e-05 | 1.9531e-05 | 1.9531e-05 | 1.6764e-05 | 1.6764e-05 | 1.6764e-05 | 1.6764e-05 | 2.7995e-06 | 1.9531e-05 | 1.9531e-05 | 1.9531e-05 | 1.9531e-05 | 1.9531e-05 | 1.9531e-05 | 1.9531e-05 | 1.9531e-05 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 3.198e-05 | 3.2442e-05 | 3.2442e-05 | 3.8711e-05 | 3.7853e-05 | 3.8711e-05 | 3.8711e-05 | 3.8711e-05 | 3.8711e-05 | 3.7853e-05 | 3.8711e-05 | 3.7853e-05 | 3.7853e-05 | 3.7853e-05 | 3.7853e-05 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.0013351
| Benzo[k]fluoranthene | 207-08-9 | Yes | Yes | -- | -- | 1.0005e-05 | 1.0005e-05 | 1.0005e-05 | 1.0005e-05 | 1.0005e-05 | 1.0005e-05 | 8.3535e-06 | 8.3535e-06 | 8.3535e-06 | 1.1656e-05 | 1.1656e-05 | 1.1656e-05 | 1.1656e-05 | 1.1656e-05 | 1.1656e-05 | 1.1656e-05 | 1.1656e-05 | 1.1656e-05 | 1.1656e-05 | 1.1656e-05 | 1.1656e-05 | 1.1656e-05 | 1.1656e-05 | 1.1656e-05 | 1.1656e-05 | 1.1656e-05 | 1.1656e-05 | 1.1656e-05 | 1.1656e-05 | 1.1656e-05 | 1.0005e-05 | 1.0005e-05 | 1.0005e-05 | 1.0005e-05 | 1.6707e-06 | 1.1656e-05 | 1.1656e-05 | 1.1656e-05 | 1.1656e-05 | 1.1656e-05 | 1.1656e-05 | 1.1656e-05 | 1.1656e-05 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 1.9085e-05 | 1.9361e-05 | 1.9361e-05 | 2.3102e-05 | 2.259e-05 | 2.3102e-05 | 2.3102e-05 | 2.3102e-05 | 2.3102e-05 | 2.259e-05 | 2.3102e-05 | 2.259e-05 | 2.259e-05 | 2.259e-05 | 2.259e-05 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.00079676
| Chrysene | 218-01-9 | Yes | Yes | -- | -- | 4.8573e-05 | 4.8573e-05 | 4.8573e-05 | 4.8573e-05 | 4.8573e-05 | 4.8573e-05 | 4.0556e-05 | 4.0556e-05 | 4.0556e-05 | 5.6589e-05 | 5.6589e-05 | 5.6589e-05 | 5.6589e-05 | 5.6589e-05 | 5.6589e-05 | 5.6589e-05 | 5.6589e-05 | 5.6589e-05 | 5.6589e-05 | 5.6589e-05 | 5.6589e-05 | 5.6589e-05 | 5.6589e-05 | 5.6589e-05 | 5.6589e-05 | 5.6589e-05 | 5.6589e-05 | 5.6589e-05 | 5.6589e-05 | 5.6589e-05 | 4.8573e-05 | 4.8573e-05 | 5.1348e-05 | 5.1348e-05 | 8.5747e-06 | 5.6589e-05 | 5.6589e-05 | 5.6589e-05 | 5.6589e-05 | 5.6589e-05 | 5.6589e-05 | 5.6589e-05 | 5.6589e-05 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 9.7954e-05 | 9.9368e-05 | 9.9368e-05 | 0.00011857 | 0.00011594 | 0.00011857 | 0.00011857 | 0.00011857 | 0.00011857 | 0.00011594 | 0.00011857 | 0.00011594 | 0.00011594 | 0.00011594 | 0.00011594 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.0039664
| Dibenz[a,h]anthracene | 53-70-3 | Yes | Yes | -- | -- | 7.5178e-07 | 7.5178e-07 | 7.5178e-07 | 7.5178e-07 | 7.5178e-07 | 7.5178e-07 | 6.277e-07 | 6.277e-07 | 6.277e-07 | 8.7586e-07 | 8.7586e-07 | 8.7586e-07 | 8.7586e-07 | 8.7586e-07 | 8.7586e-07 | 8.7586e-07 | 8.7586e-07 | 8.7586e-07 | 8.7586e-07 | 8.7586e-07 | 8.7586e-07 | 8.7586e-07 | 8.7586e-07 | 8.7586e-07 | 8.7586e-07 | 8.7586e-07 | 8.7586e-07 | 8.7586e-07 | 8.7586e-07 | 8.7586e-07 | 7.5178e-07 | 7.5178e-07 | 7.9474e-07 | 7.9474e-07 | 1.3271e-07 | 8.7586e-07 | 8.7586e-07 | 8.7586e-07 | 8.7586e-07 | 8.7586e-07 | 8.7586e-07 | 8.7586e-07 | 8.7586e-07 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 1.5161e-06 | 1.538e-06 | 1.538e-06 | 1.8351e-06 | 1.7945e-06 | 1.8351e-06 | 1.8351e-06 | 1.8351e-06 | 1.8351e-06 | 1.7945e-06 | 1.8351e-06 | 1.7945e-06 | 1.7945e-06 | 1.7945e-06 | 1.7945e-06 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 6.1389e-05
| Fluoranthene | 206-44-0 | Yes | Yes | -- | -- | 0.00024521 | 0.00024521 | 0.00024521 | 0.00024521 | 0.00024521 | 0.00024521 | 0.00020474 | 0.00020474 | 0.00020474 | 0.00028569 | 0.00028569 | 0.00028569 | 0.00028569 | 0.00028569 | 0.00028569 | 0.00028569 | 0.00028569 | 0.00028569 | 0.00028569 | 0.00028569 | 0.00028569 | 0.00028569 | 0.00028569 | 0.00028569 | 0.00028569 | 0.00028569 | 0.00028569 | 0.00028569 | 0.00028569 | 0.00028569 | 0.00024521 | 0.00024521 | 0.00028353 | 0.00028353 | 4.7347e-05 | 0.00028569 | 0.00028569 | 0.00028569 | 0.00028569 | 0.00028569 | 0.00028569 | 0.00028569 | 0.00028569 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.00054087 | 0.00054868 | 0.00054868 | 0.0006547 | 0.00064019 | 0.0006547 | 0.0006547 | 0.0006547 | 0.0006547 | 0.00064019 | 0.0006547 | 0.00064019 | 0.00064019 | 0.00064019 | 0.00064019 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.020883
| Fluorene | 86-73-7 | Yes | -- | -- | -- | 0.0014479 | 0.0014479 | 0.0014479 | 0.0014479 | 0.0014479 | 0.0014479 | 0.0012089 | 0.0012089 | 0.0012089 | 0.0016868 | 0.0016868 | 0.0016868 | 0.0016868 | 0.0016868 | 0.0016868 | 0.0016868 | 0.0016868 | 0.0016868 | 0.0016868 | 0.0016868 | 0.0016868 | 0.0016868 | 0.0016868 | 0.0016868 | 0.0016868 | 0.0016868 | 0.0016868 | 0.0016868 | 0.0016868 | 0.0016868 | 0.0014479 | 0.0014479 | 0.0016741 | 0.0016741 | 0.00027956 | 0.0016868 | 0.0016868 | 0.0016868 | 0.0016868 | 0.0016868 | 0.0016868 | 0.0016868 | 0.0016868 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.0031936 | 0.0032397 | 0.0032397 | 0.0038657 | 0.00378 | 0.0038657 | 0.0038657 | 0.0038657 | 0.0038657 | 0.00378 | 0.0038657 | 0.00378 | 0.00378 | 0.00378 | 0.00378 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.1233
| Indeno[1,2,3-cd]pyrene | 193-39-5 | Yes | Yes | -- | -- | 6.6558e-06 | 6.6558e-06 | 6.6558e-06 | 6.6558e-06 | 6.6558e-06 | 6.6558e-06 | 5.5573e-06 | 5.5573e-06 | 5.5573e-06 | 7.7543e-06 | 7.7543e-06 | 7.7543e-06 | 7.7543e-06 | 7.7543e-06 | 7.7543e-06 | 7.7543e-06 | 7.7543e-06 | 7.7543e-06 | 7.7543e-06 | 7.7543e-06 | 7.7543e-06 | 7.7543e-06 | 7.7543e-06 | 7.7543e-06 | 7.7543e-06 | 7.7543e-06 | 7.7543e-06 | 7.7543e-06 | 7.7543e-06 | 7.7543e-06 | 6.6558e-06 | 6.6558e-06 | 8.2088e-06 | 8.2088e-06 | 1.3708e-06 | 7.7543e-06 | 7.7543e-06 | 7.7543e-06 | 7.7543e-06 | 7.7543e-06 | 7.7543e-06 | 7.7543e-06 | 7.7543e-06 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 1.5659e-05 | 1.5886e-05 | 1.5886e-05 | 1.8955e-05 | 1.8535e-05 | 1.8955e-05 | 1.8955e-05 | 1.8955e-05 | 1.8955e-05 | 1.8535e-05 | 1.8955e-05 | 1.8535e-05 | 1.8535e-05 | 1.8535e-05 | 1.8535e-05 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.00058495
| Naphthalene | 91-20-3 | Yes | Yes | 0.0020868 | 0.0014836 | 0.019105 | 0.019105 | 0.019105 | 0.019105 | 0.019105 | 0.019105 | 0.015951 | 0.015951 | 0.015951 | 0.022258 | 0.022258 | 0.022258 | 0.022258 | 0.022258 | 0.022258 | 0.022258 | 0.022258 | 0.022258 | 0.022258 | 0.022258 | 0.022258 | 0.022258 | 0.022258 | 0.022258 | 0.022258 | 0.022258 | 0.022258 | 0.022258 | 0.022258 | 0.022258 | 0.019105 | 0.019105 | 0.020196 | 0.020196 | 0.0033726 | 0.022258 | 0.022258 | 0.022258 | 0.022258 | 0.022258 | 0.022258 | 0.022258 | 0.022258 | 0.022484 | 0.022484 | 0.022484 | 0.022484 | 0.01777 | 0.01777 | 0.01777 | 0.024364 | 0.024364 | 0.027236 | 0.028801 | 0.029209 | 0.029209 | 0.029209 | 0.029209 | 0.029209 | 0.029209 | 0.0045361 | 0.0045361 | 0.0091911 | 0.0038428 | 0.038527 | 0.039084 | 0.039084 | 0.046635 | 0.045602 | 0.046635 | 0.046635 | 0.046635 | 0.046635 | 0.045602 | 0.046635 | 0.045602 | 0.045602 | 0.045602 | 0.045602 | 0.0020601 | 0.0022383 | 0.0013074 | 0.0012083 | 0.021353 | 0.021353 | 0.021353 | 0.021365 | 0.02125 | 2.1225
| Perylene | 198-55-0 | Yes | -- | -- | -- | 9.03e-07 | 9.03e-07 | 9.03e-07 | 9.03e-07 | 9.03e-07 | 9.03e-07 | 7.5396e-07 | 7.5396e-07 | 7.5396e-07 | 1.052e-06 | 1.052e-06 | 1.052e-06 | 1.052e-06 | 1.052e-06 | 1.052e-06 | 1.052e-06 | 1.052e-06 | 1.052e-06 | 1.052e-06 | 1.052e-06 | 1.052e-06 | 1.052e-06 | 1.052e-06 | 1.052e-06 | 1.052e-06 | 1.052e-06 | 1.052e-06 | 1.052e-06 | 1.052e-06 | 1.052e-06 | 9.03e-07 | 9.03e-07 | 9.03e-07 | 9.03e-07 | 1.5079e-07 | 1.052e-06 | 1.052e-06 | 1.052e-06 | 1.052e-06 | 1.052e-06 | 1.052e-06 | 1.052e-06 | 1.052e-06 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 1.7226e-06 | 1.7475e-06 | 1.7475e-06 | 2.0851e-06 | 2.0389e-06 | 2.0851e-06 | 2.0851e-06 | 2.0851e-06 | 2.0851e-06 | 2.0389e-06 | 2.0851e-06 | 2.0389e-06 | 2.0389e-06 | 2.0389e-06 | 2.0389e-06 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 7.1913e-05
| Phenanthrene | 85-01-8 | Yes | -- | -- | -- | 0.0034809 | 0.0034809 | 0.0034809 | 0.0034809 | 0.0034809 | 0.0034809 | 0.0029064 | 0.0029064 | 0.0029064 | 0.0040554 | 0.0040554 | 0.0040554 | 0.0040554 | 0.0040554 | 0.0040554 | 0.0040554 | 0.0040554 | 0.0040554 | 0.0040554 | 0.0040554 | 0.0040554 | 0.0040554 | 0.0040554 | 0.0040554 | 0.0040554 | 0.0040554 | 0.0040554 | 0.0040554 | 0.0040554 | 0.0040554 | 0.0034809 | 0.0034809 | 0.0034809 | 0.0034809 | 0.00058128 | 0.0040554 | 0.0040554 | 0.0040554 | 0.0040554 | 0.0040554 | 0.0040554 | 0.0040554 | 0.0040554 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.0066403 | 0.0067362 | 0.0067362 | 0.0080378 | 0.0078597 | 0.0080378 | 0.0080378 | 0.0080378 | 0.0080378 | 0.0078597 | 0.0080378 | 0.0078597 | 0.0078597 | 0.0078597 | 0.0078597 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.27721
| Pyrene | 129-00-0 | Yes | -- | -- | -- | 0.00095799 | 0.00095799 | 0.00095799 | 0.00095799 | 0.00095799 | 0.00095799 | 0.00079988 | 0.00079988 | 0.00079988 | 0.0011161 | 0.0011161 | 0.0011161 | 0.0011161 | 0.0011161 | 0.0011161 | 0.0011161 | 0.0011161 | 0.0011161 | 0.0011161 | 0.0011161 | 0.0011161 | 0.0011161 | 0.0011161 | 0.0011161 | 0.0011161 | 0.0011161 | 0.0011161 | 0.0011161 | 0.0011161 | 0.0011161 | 0.00095799 | 0.00095799 | 0.00095799 | 0.00095799 | 0.00015998 | 0.0011161 | 0.0011161 | 0.0011161 | 0.0011161 | 0.0011161 | 0.0011161 | 0.0011161 | 0.0011161 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.0018275 | 0.0018539 | 0.0018539 | 0.0022121 | 0.0021631 | 0.0022121 | 0.0022121 | 0.0022121 | 0.0022121 | 0.0021631 | 0.0022121 | 0.0021631 | 0.0021631 | 0.0021631 | 0.0021631 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.076293
| PAH | 401 | Yes | Yes | 0.0040538 | 0.0028821 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.041317 | 0.041317 | 0.041317 | 0.041317 | 0.032654 | 0.032654 | 0.032654 | 0.044771 | 0.044771 | 0.050049 | 0.052924 | 0.053674 | 0.053674 | 0.053674 | 0.053674 | 0.053674 | 0.053674 | 0.0083354 | 0.0083354 | 0.016889 | 0.0070614 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.0037855 | 0.0041131 | 0.0024023 | 0.0022203 | 0.039238 | 0.039238 | 0.039238 | 0.03926 | 0.039049 | 1.0339
DIESEL PARTICULATE MATTER (DPM)
| DPM | 200 | Yes | Yes | 0.70973 | 0.50459 | 2.4613 | 2.4613 | 2.4613 | 2.4613 | 2.4613 | 2.4613 | 2.0551 | 2.0551 | 2.0551 | 2.8675 | 2.8675 | 2.8675 | 2.8675 | 2.8675 | 2.8675 | 2.8675 | 2.8675 | 2.8675 | 2.8675 | 2.8675 | 2.8675 | 2.8675 | 2.8675 | 2.8675 | 2.8675 | 2.8675 | 2.8675 | 2.8675 | 2.8675 | 2.8675 | 2.4613 | 2.4613 | 3.5161 | 3.5161 | 0.58716 | 2.8675 | 2.8675 | 2.8675 | 2.8675 | 2.8675 | 2.8675 | 2.8675 | 2.8675 | 38.235 | 38.235 | 38.235 | 38.235 | 30.2181 | 30.2181 | 30.2181 | 41.4316 | 41.4316 | 46.3158 | 48.9769 | 49.6708 | 49.6708 | 49.6708 | 49.6708 | 49.6708 | 49.6708 | 7.7137 | 7.7137 | 15.6295 | 6.5347 | 24.8178 | 25.1762 | 25.1762 | 30.0408 | 29.3751 | 30.0408 | 30.0408 | 30.0408 | 30.0408 | 29.3751 | 30.0408 | 29.3751 | 29.3751 | 29.3751 | 29.3751 | 3.5032 | 3.8063 | 2.2232 | 2.0547 | 36.3116 | 36.3116 | 36.3116 | 36.3318 | 36.1365 | 1499.87
Total TAC Emissions Estimate | [94 empty] | 2029.9215

## Annual TAC SumEGEN
Table 9
Annual TAC Emission Estimate Summary—Emergency Generators
Intel Corporation
Pollutant |  | CAS | Regulatory Category |  | Daily Emissions Estimate (lb/yr) | [89 empty] | Total Emissions Estimate (Emergency Generators) (lb/day)
[5 empty] | Ronler | [84 empty] | Aloha
[5 empty] | DPF | [44 empty] | No DPF | [35 empty] | Fire Pumps |  |  |  | Aloha
|  |  | TAC | RBC? | N2-GEN-1A | H2-GEN-1 | D1X-GEN-5A | D1X-GEN-5B | D1X-GEN-4C | D1X-GEN-6A | D1X-GEN-6B | D1X-GEN-6C | D1X-GEN-7A | D1X-GEN-7B | D1X-GEN-7C | D1X2-GEN-6A | D1X2-GEN-6B | D1X2-GEN-6C | D1X2-GEN-7A | D1X2-GEN-7B | D1X2-GEN-7C | D1X2-GEN-1A | D1X2-GEN-1B | D1X2-GEN-1C | D1X2-GEN-2A | D1X2-GEN-2B | D1X2-GEN-2C | D1X2-GEN-3A | D1X2-GEN-3B | D1X2-GEN-3C | D1X2-GEN-4A | D1X2-GEN-4B | D1X2-GEN-4C | D1X2-GEN-5A | D1X2-GEN-5B | D1X2-GEN-5C | F20-EPS-1 | F20-EPS-2 | IWW-GEN-1 | IWW-GEN-2 | IWW-PS-1 | D1A-GEN-1 | D1A-GEN-2 | D1A-GEN-3 | D1A-GEN-4 | D1A-GEN-5 | D1A-GEN-6 | D1A-GEN-7 | D1A-GEN-8 | RA1-ELEC-CPS-GEN01 | RA1-ELEC-CPS-GEN02 | RA1-ELEC-CPS-GEN03 | RA1-ELEC-CPS-GEN04 | D1C-CPS-GEN01 | D1C-CPS-GEN02 | D1C-CPS-GEN03 | D1C-EPS-GEN01 | D1C-EPS-GEN02 | RB1-EPS-GEN01 | RP1-EPS-GEN01 | EPS-GEN01 | EPS-GEN02 | EPS-GEN03 | EPS-GEN04 | EPS-GEN05 | EPS-GEN06 | RS4-ELEC-EG-4-1 | RS6-ELEC-EG-6-1 | F20-CPS-1 | MAX-EGEN | RP1-GEN-2 | D1D-GEN-7 | RS6-GEN-2 | D1X-GEN-1A | D1X-GEN-1B | D1X-GEN-1C | D1X-GEN-2A | D1X-GEN-2B | D1X-GEN-2C | D1X-GEN-3A | D1X-GEN-3B | D1X-GEN-3C | D1X-GEN-4A | D1X-GEN-4B | D1X-GEN-5C | PH #1 | PH #2 | PH #3 | PH #4 | F15-EG01 | F15-EG02 | F15-EG03 | F15.5-EG01 | F15.5-EG02
Stack ID |  |  |  |  | EGN2_01 | EGH2_01 | EGE1_14 | EGE1_15 | EGE1_13 | EGE1_16 | EGE1_17 | EGE1_18 | EGE1_19 | EGE1_20 | EGE1_21 | EGC5_16 | EGC5_17 | EGC5_18 | EGC5_19 | EGC5_20 | EGC5_21 | EGC5_01 | EGC5_02 | EGC5_03 | EGC5_04 | EGC5_05 | EGC5_06 | EGC5_07 | EGC5_08 | EGC5_09 | EGC5_10 | EGC5_11 | EGC5_12 | EGC5_13 | EGC5_14 | EGC5_15 | EGDB_01 | EGDB_02 | EGIW_02 | EGIW_01 | EGIW_03 | EGDA_01 | EGDA_02 | EGDA_03 | EGDA_04 | EGDA_05 | EGDA_06 | EGDA_07 | EGDA_08 | EGR1_01 | EGR1_02 | EGR1_03 | EGR1_04 | EGDC_01 | EGDC_02 | EGDC_03 | EGDC_04 | EGDC_05 | EGRB1_01 | EGRP1_01 | EGDD_01 | EGDD_02 | EGDD_03 | EGDD_04 | EGDD_05 | EGDD_06 | EGRS4_01 | EGRS6_01 | EGDB_03 | EGRS8_01 | EGRP1_02 | EGDD_07 | EGRS6_02 | EGE1_01 | EGE1_02 | EGE1_03 | EGE1_04 | EGE1_05 | EGE1_06 | EGE1_07 | EGE1_08 | EGE1_09 | EGE1_10 | EGE1_11 | EGE1_12 | FIPH1_01 | FIPH2_01 | FIRS4_01 | FIC5_01 | EGF15_01 | EGF15_02 | EGF15_03 | EGF5_01 | EGF5_02
METALS
| Antimony and Compounds | 7440-36-0 | Yes | Yes | 7.1831e-05 | 5.1069e-05 | 0.0004916 | 0.0004916 | 0.0004916 | 0.0004916 | 0.0004916 | 0.0004916 | 0.00041046 | 0.00041046 | 0.00041046 | 0.00057274 | 0.00057274 | 0.00057274 | 0.00057274 | 0.00057274 | 0.00057274 | 0.00057274 | 0.00057274 | 0.00057274 | 0.00057274 | 0.00057274 | 0.00057274 | 0.00057274 | 0.00057274 | 0.00057274 | 0.00057274 | 0.00057274 | 0.00057274 | 0.00057274 | 0.00057274 | 0.00057274 | 0.0004916 | 0.0004916 | 0.0004916 | 0.0004916 | 8.2092e-05 | 0.00057274 | 0.00057274 | 0.00057274 | 0.00057274 | 0.00057274 | 0.00057274 | 0.00057274 | 0.00057274 | 0.00090294 | 0.00090294 | 0.00090294 | 0.00090294 | 0.00071361 | 0.00071361 | 0.00071361 | 0.00097843 | 0.00097843 | 0.0010938 | 0.0011566 | 0.001173 | 0.001173 | 0.001173 | 0.001173 | 0.001173 | 0.001173 | 0.00018216 | 0.00018216 | 0.0003691 | 0.00015432 | 0.0011566 | 0.0011733 | 0.0011733 | 0.0014 | 0.001369 | 0.0014 | 0.0014 | 0.0014 | 0.0014 | 0.001369 | 0.0014 | 0.001369 | 0.001369 | 0.001369 | 0.001369 | 0.00016546 | 0.00017978 | 0.000105 | 9.7047e-05 | 0.00085751 | 0.00085751 | 0.00085751 | 0.00085799 | 0.00085338 | 0.065796
| Arsenic and compounds | 7440-38-2 | Yes | Yes | 0.0003612 | 0.0002568 | 0.00042774 | 0.00042774 | 0.00042774 | 0.00042774 | 0.00042774 | 0.00042774 | 0.00035714 | 0.00035714 | 0.00035714 | 0.00049833 | 0.00049833 | 0.00049833 | 0.00049833 | 0.00049833 | 0.00049833 | 0.00049833 | 0.00049833 | 0.00049833 | 0.00049833 | 0.00049833 | 0.00049833 | 0.00049833 | 0.00049833 | 0.00049833 | 0.00049833 | 0.00049833 | 0.00049833 | 0.00049833 | 0.00049833 | 0.00049833 | 0.00042774 | 0.00042774 | 0.00042774 | 0.00042774 | 7.1428e-05 | 0.00049833 | 0.00049833 | 0.00049833 | 0.00049833 | 0.00049833 | 0.00049833 | 0.00049833 | 0.00049833 | 0.0045404 | 0.0045404 | 0.0045404 | 0.0045404 | 0.0035884 | 0.0035884 | 0.0035884 | 0.00492 | 0.00492 | 0.0055 | 0.005816 | 0.0058984 | 0.0058984 | 0.0058984 | 0.0058984 | 0.0058984 | 0.0058984 | 0.000916 | 0.000916 | 0.001856 | 0.000776 | 0.0010064 | 0.0010209 | 0.0010209 | 0.0012182 | 0.0011912 | 0.0012182 | 0.0012182 | 0.0012182 | 0.0012182 | 0.0011912 | 0.0012182 | 0.0011912 | 0.0011912 | 0.0011912 | 0.0011912 | 0.000832 | 0.000904 | 0.000528 | 0.000488 | 0.004312 | 0.004312 | 0.004312 | 0.0043144 | 0.0042912 | 0.15222
| Barium and Compounds | 7440-39-3 | Yes | -- | 1.5475e-05 | 1.1002e-05 | 0.00010591 | 0.00010591 | 0.00010591 | 0.00010591 | 0.00010591 | 0.00010591 | 8.8426e-05 | 8.8426e-05 | 8.8426e-05 | 0.00012338 | 0.00012338 | 0.00012338 | 0.00012338 | 0.00012338 | 0.00012338 | 0.00012338 | 0.00012338 | 0.00012338 | 0.00012338 | 0.00012338 | 0.00012338 | 0.00012338 | 0.00012338 | 0.00012338 | 0.00012338 | 0.00012338 | 0.00012338 | 0.00012338 | 0.00012338 | 0.00012338 | 0.00010591 | 0.00010591 | 0.00057767 | 0.00057767 | 9.6464e-05 | 0.00012338 | 0.00012338 | 0.00012338 | 0.00012338 | 0.00012338 | 0.00012338 | 0.00012338 | 0.00012338 | 0.001061 | 0.001061 | 0.001061 | 0.001061 | 0.00083855 | 0.00083855 | 0.00083855 | 0.0011497 | 0.0011497 | 0.0012853 | 0.0013591 | 0.0013784 | 0.0013784 | 0.0013784 | 0.0013784 | 0.0013784 | 0.0013784 | 0.00021405 | 0.00021405 | 0.00043372 | 0.00018134 | 0.0013591 | 0.0013787 | 0.0013787 | 0.0016451 | 0.0016087 | 0.0016451 | 0.0016451 | 0.0016451 | 0.0016451 | 0.0016087 | 0.0016451 | 0.0016087 | 0.0016087 | 0.0016087 | 0.0016087 | 0.00019442 | 0.00021125 | 0.00012338 | 0.00011404 | 0.0010076 | 0.0010076 | 0.0010076 | 0.0010082 | 0.0010028 | 0.056302
| Beryllium and Compounds | 7440-41-7 | Yes | Yes | 1.077e-06 | 7.6572e-07 | 7.371e-06 | 7.371e-06 | 7.371e-06 | 7.371e-06 | 7.371e-06 | 7.371e-06 | 6.1544e-06 | 6.1544e-06 | 6.1544e-06 | 8.5875e-06 | 8.5875e-06 | 8.5875e-06 | 8.5875e-06 | 8.5875e-06 | 8.5875e-06 | 8.5875e-06 | 8.5875e-06 | 8.5875e-06 | 8.5875e-06 | 8.5875e-06 | 8.5875e-06 | 8.5875e-06 | 8.5875e-06 | 8.5875e-06 | 8.5875e-06 | 8.5875e-06 | 8.5875e-06 | 8.5875e-06 | 8.5875e-06 | 8.5875e-06 | 7.371e-06 | 7.371e-06 | 7.371e-06 | 7.371e-06 | 1.2309e-06 | 8.5875e-06 | 8.5875e-06 | 8.5875e-06 | 8.5875e-06 | 8.5875e-06 | 8.5875e-06 | 8.5875e-06 | 8.5875e-06 | 1.3538e-05 | 1.3538e-05 | 1.3538e-05 | 1.3538e-05 | 1.07e-05 | 1.07e-05 | 1.07e-05 | 1.467e-05 | 1.467e-05 | 1.64e-05 | 1.7342e-05 | 1.7588e-05 | 1.7588e-05 | 1.7588e-05 | 1.7588e-05 | 1.7588e-05 | 1.7588e-05 | 2.7313e-06 | 2.7313e-06 | 5.5342e-06 | 2.3139e-06 | 1.7342e-05 | 1.7592e-05 | 1.7592e-05 | 2.0992e-05 | 2.0527e-05 | 2.0992e-05 | 2.0992e-05 | 2.0992e-05 | 2.0992e-05 | 2.0527e-05 | 2.0992e-05 | 2.0527e-05 | 2.0527e-05 | 2.0527e-05 | 2.0527e-05 | 2.4808e-06 | 2.6955e-06 | 1.5744e-06 | 1.4551e-06 | 1.2857e-05 | 1.2857e-05 | 1.2857e-05 | 1.2865e-05 | 1.2795e-05 | 0.00098653
| Cadmium and Compounds | 7440-43-9 | Yes | Yes | 0.00033863 | 0.00024075 | 0.0001248 | 0.0001248 | 0.0001248 | 0.0001248 | 0.0001248 | 0.0001248 | 0.0001042 | 0.0001042 | 0.0001042 | 0.0001454 | 0.0001454 | 0.0001454 | 0.0001454 | 0.0001454 | 0.0001454 | 0.0001454 | 0.0001454 | 0.0001454 | 0.0001454 | 0.0001454 | 0.0001454 | 0.0001454 | 0.0001454 | 0.0001454 | 0.0001454 | 0.0001454 | 0.0001454 | 0.0001454 | 0.0001454 | 0.0001454 | 0.0001248 | 0.0001248 | 0.0001248 | 0.0001248 | 2.0841e-05 | 0.0001454 | 0.0001454 | 0.0001454 | 0.0001454 | 0.0001454 | 0.0001454 | 0.0001454 | 0.0001454 | 0.0042566 | 0.0042566 | 0.0042566 | 0.0042566 | 0.0033641 | 0.0033641 | 0.0033641 | 0.0046125 | 0.0046125 | 0.0051563 | 0.0054525 | 0.0055298 | 0.0055298 | 0.0055298 | 0.0055298 | 0.0055298 | 0.0055298 | 0.00085875 | 0.00085875 | 0.00174 | 0.0007275 | 0.00029363 | 0.00029787 | 0.00029787 | 0.00035542 | 0.00034755 | 0.00035542 | 0.00035542 | 0.00035542 | 0.00035542 | 0.00034755 | 0.00035542 | 0.00034755 | 0.00034755 | 0.00034755 | 0.00034755 | 0.00078 | 0.0008475 | 0.000495 | 0.0004575 | 0.0040425 | 0.0040425 | 0.0040425 | 0.0040447 | 0.004023 | 0.11858
| Chromium VI | 18540-29-9 | Yes | Yes | 4.1388e-06 | 2.9425e-06 | 1.7886e-05 | 1.7886e-05 | 1.7886e-05 | 1.7886e-05 | 1.7886e-05 | 1.7886e-05 | 1.4934e-05 | 1.4934e-05 | 1.4934e-05 | 2.0838e-05 | 2.0838e-05 | 2.0838e-05 | 2.0838e-05 | 2.0838e-05 | 2.0838e-05 | 2.0838e-05 | 2.0838e-05 | 2.0838e-05 | 2.0838e-05 | 2.0838e-05 | 2.0838e-05 | 2.0838e-05 | 2.0838e-05 | 2.0838e-05 | 2.0838e-05 | 2.0838e-05 | 2.0838e-05 | 2.0838e-05 | 2.0838e-05 | 2.0838e-05 | 1.7886e-05 | 1.7886e-05 | 9.7558e-05 | 9.7558e-05 | 1.6291e-05 | 2.0838e-05 | 2.0838e-05 | 2.0838e-05 | 2.0838e-05 | 2.0838e-05 | 2.0838e-05 | 2.0838e-05 | 2.0838e-05 | 0.00028378 | 0.00028378 | 0.00028378 | 0.00028378 | 0.00022427 | 0.00022427 | 0.00022427 | 0.0003075 | 0.0003075 | 0.00034375 | 0.0003635 | 0.00036865 | 0.00036865 | 0.00036865 | 0.00036865 | 0.00036865 | 0.00036865 | 5.725e-05 | 5.725e-05 | 0.000116 | 4.85e-05 | 0.00022953 | 0.00023285 | 0.00023285 | 0.00027784 | 0.00027168 | 0.00027784 | 0.00027784 | 0.00027784 | 0.00027784 | 0.00027168 | 0.00027784 | 0.00027168 | 0.00027168 | 0.00027168 | 0.00027168 | 5.2e-05 | 5.65e-05 | 3.3e-05 | 3.05e-05 | 0.0002695 | 0.0002695 | 0.0002695 | 0.00026965 | 0.0002682 | 0.012142
| Cobalt and Compounds | 7440-48-4 | Yes | Yes | 3.5558e-06 | 2.5281e-06 | 2.4336e-05 | 2.4336e-05 | 2.4336e-05 | 2.4336e-05 | 2.4336e-05 | 2.4336e-05 | 2.0319e-05 | 2.0319e-05 | 2.0319e-05 | 2.8352e-05 | 2.8352e-05 | 2.8352e-05 | 2.8352e-05 | 2.8352e-05 | 2.8352e-05 | 2.8352e-05 | 2.8352e-05 | 2.8352e-05 | 2.8352e-05 | 2.8352e-05 | 2.8352e-05 | 2.8352e-05 | 2.8352e-05 | 2.8352e-05 | 2.8352e-05 | 2.8352e-05 | 2.8352e-05 | 2.8352e-05 | 2.8352e-05 | 2.8352e-05 | 2.4336e-05 | 2.4336e-05 | 2.4336e-05 | 2.4336e-05 | 4.0638e-06 | 2.8352e-05 | 2.8352e-05 | 2.8352e-05 | 2.8352e-05 | 2.8352e-05 | 2.8352e-05 | 2.8352e-05 | 2.8352e-05 | 4.4698e-05 | 4.4698e-05 | 4.4698e-05 | 4.4698e-05 | 3.5326e-05 | 3.5326e-05 | 3.5326e-05 | 4.8435e-05 | 4.8435e-05 | 5.4145e-05 | 5.7255e-05 | 5.8067e-05 | 5.8067e-05 | 5.8067e-05 | 5.8067e-05 | 5.8067e-05 | 5.8067e-05 | 9.0175e-06 | 9.0175e-06 | 1.8271e-05 | 7.6393e-06 | 5.7255e-05 | 5.8082e-05 | 5.8082e-05 | 6.9305e-05 | 6.7769e-05 | 6.9305e-05 | 6.9305e-05 | 6.9305e-05 | 6.9305e-05 | 6.7769e-05 | 6.9305e-05 | 6.7769e-05 | 6.7769e-05 | 6.7769e-05 | 6.7769e-05 | 8.1906e-06 | 8.8994e-06 | 5.1979e-06 | 4.8041e-06 | 4.2449e-05 | 4.2449e-05 | 4.2449e-05 | 4.2473e-05 | 4.2245e-05 | 0.0032571
| Copper and Compounds | 7440-50-8 | Yes | Yes | 0.00016969 | 0.00012064 | 0.00014223 | 0.00014223 | 0.00014223 | 0.00014223 | 0.00014223 | 0.00014223 | 0.00011875 | 0.00011875 | 0.00011875 | 0.0001657 | 0.0001657 | 0.0001657 | 0.0001657 | 0.0001657 | 0.0001657 | 0.0001657 | 0.0001657 | 0.0001657 | 0.0001657 | 0.0001657 | 0.0001657 | 0.0001657 | 0.0001657 | 0.0001657 | 0.0001657 | 0.0001657 | 0.0001657 | 0.0001657 | 0.0001657 | 0.0001657 | 0.00014223 | 0.00014223 | 0.0007758 | 0.0007758 | 0.00012955 | 0.0001657 | 0.0001657 | 0.0001657 | 0.0001657 | 0.0001657 | 0.0001657 | 0.0001657 | 0.0001657 | 0.011635 | 0.011635 | 0.011635 | 0.011635 | 0.0091953 | 0.0091953 | 0.0091953 | 0.012608 | 0.012608 | 0.014094 | 0.014904 | 0.015115 | 0.015115 | 0.015115 | 0.015115 | 0.015115 | 0.015115 | 0.0023472 | 0.0023472 | 0.004756 | 0.0019885 | 0.0018253 | 0.0018516 | 0.0018516 | 0.0022094 | 0.0021604 | 0.0022094 | 0.0022094 | 0.0022094 | 0.0022094 | 0.0021604 | 0.0022094 | 0.0021604 | 0.0021604 | 0.0021604 | 0.0021604 | 0.002132 | 0.0023165 | 0.001353 | 0.0012505 | 0.01105 | 0.01105 | 0.01105 | 0.011056 | 0.010996 | 0.33273
| Lead and Compounds | 7439-92-1 | Yes | Yes | 0.0018737 | 0.0013322 | 0.00056187 | 0.00056187 | 0.00056187 | 0.00056187 | 0.00056187 | 0.00056187 | 0.00046914 | 0.00046914 | 0.00046914 | 0.00065461 | 0.00065461 | 0.00065461 | 0.00065461 | 0.00065461 | 0.00065461 | 0.00065461 | 0.00065461 | 0.00065461 | 0.00065461 | 0.00065461 | 0.00065461 | 0.00065461 | 0.00065461 | 0.00065461 | 0.00065461 | 0.00065461 | 0.00065461 | 0.00065461 | 0.00065461 | 0.00065461 | 0.00056187 | 0.00056187 | 0.00056187 | 0.00056187 | 9.3827e-05 | 0.00065461 | 0.00065461 | 0.00065461 | 0.00065461 | 0.00065461 | 0.00065461 | 0.00065461 | 0.00065461 | 0.023553 | 0.023553 | 0.023553 | 0.023553 | 0.018615 | 0.018615 | 0.018615 | 0.025522 | 0.025522 | 0.028531 | 0.03017 | 0.030598 | 0.030598 | 0.030598 | 0.030598 | 0.030598 | 0.030598 | 0.0047517 | 0.0047517 | 0.009628 | 0.0040255 | 0.0013219 | 0.001341 | 0.001341 | 0.0016002 | 0.0015647 | 0.0016002 | 0.0016002 | 0.0016002 | 0.0016002 | 0.0015647 | 0.0016002 | 0.0015647 | 0.0015647 | 0.0015647 | 0.0015647 | 0.004316 | 0.0046895 | 0.002739 | 0.0025315 | 0.022368 | 0.022368 | 0.022368 | 0.022381 | 0.022261 | 0.64487
| Manganese and Compounds | 7439-96-5 | Yes | Yes | 0.0001283 | 9.1218e-05 | 0.00011894 | 0.00011894 | 0.00011894 | 0.00011894 | 0.00011894 | 0.00011894 | 9.9309e-05 | 9.9309e-05 | 9.9309e-05 | 0.00013857 | 0.00013857 | 0.00013857 | 0.00013857 | 0.00013857 | 0.00013857 | 0.00013857 | 0.00013857 | 0.00013857 | 0.00013857 | 0.00013857 | 0.00013857 | 0.00013857 | 0.00013857 | 0.00013857 | 0.00013857 | 0.00013857 | 0.00013857 | 0.00013857 | 0.00013857 | 0.00013857 | 0.00011894 | 0.00011894 | 0.00064877 | 0.00064877 | 0.00010834 | 0.00013857 | 0.00013857 | 0.00013857 | 0.00013857 | 0.00013857 | 0.00013857 | 0.00013857 | 0.00013857 | 0.008797 | 0.008797 | 0.008797 | 0.008797 | 0.0069525 | 0.0069525 | 0.0069525 | 0.0095325 | 0.0095325 | 0.010656 | 0.011269 | 0.011428 | 0.011428 | 0.011428 | 0.011428 | 0.011428 | 0.011428 | 0.0017748 | 0.0017748 | 0.003596 | 0.0015035 | 0.0015264 | 0.0015484 | 0.0015484 | 0.0018476 | 0.0018067 | 0.0018476 | 0.0018476 | 0.0018476 | 0.0018476 | 0.0018067 | 0.0018476 | 0.0018067 | 0.0018067 | 0.0018067 | 0.0018067 | 0.001612 | 0.0017515 | 0.001023 | 0.0009455 | 0.0083545 | 0.0083545 | 0.0083545 | 0.0083591 | 0.0083142 | 0.25476
| Mercury and Compounds | 7439-97-6 | Yes | Yes | 0.000903 | 0.000642 | 4.6682e-05 | 4.6682e-05 | 4.6682e-05 | 4.6682e-05 | 4.6682e-05 | 4.6682e-05 | 3.8977e-05 | 3.8977e-05 | 3.8977e-05 | 5.4386e-05 | 5.4386e-05 | 5.4386e-05 | 5.4386e-05 | 5.4386e-05 | 5.4386e-05 | 5.4386e-05 | 5.4386e-05 | 5.4386e-05 | 5.4386e-05 | 5.4386e-05 | 5.4386e-05 | 5.4386e-05 | 5.4386e-05 | 5.4386e-05 | 5.4386e-05 | 5.4386e-05 | 5.4386e-05 | 5.4386e-05 | 5.4386e-05 | 5.4386e-05 | 4.6682e-05 | 4.6682e-05 | 2.3341e-05 | 2.3341e-05 | 3.8977e-06 | 5.4386e-05 | 5.4386e-05 | 5.4386e-05 | 5.4386e-05 | 5.4386e-05 | 5.4386e-05 | 5.4386e-05 | 5.4386e-05 | 0.0056755 | 0.0056755 | 0.0056755 | 0.0056755 | 0.0044855 | 0.0044855 | 0.0044855 | 0.00615 | 0.00615 | 0.006875 | 0.00727 | 0.007373 | 0.007373 | 0.007373 | 0.007373 | 0.007373 | 0.007373 | 0.001145 | 0.001145 | 0.00232 | 0.00097 | 5.4915e-05 | 5.5708e-05 | 5.5708e-05 | 6.6472e-05 | 6.4999e-05 | 6.6472e-05 | 6.6472e-05 | 6.6472e-05 | 6.6472e-05 | 6.4999e-05 | 6.6472e-05 | 6.4999e-05 | 6.4999e-05 | 6.4999e-05 | 6.4999e-05 | 0.00104 | 0.00113 | 0.00066 | 0.00061 | 0.00539 | 0.00539 | 0.00539 | 0.005393 | 0.005364 | 0.14741
| Nickel and Compounds | 7440-02-0 | Yes | Yes | 0.00016141 | 0.00011476 | 5.1616e-05 | 5.1616e-05 | 5.1616e-05 | 5.1616e-05 | 5.1616e-05 | 5.1616e-05 | 4.3097e-05 | 4.3097e-05 | 4.3097e-05 | 6.0136e-05 | 6.0136e-05 | 6.0136e-05 | 6.0136e-05 | 6.0136e-05 | 6.0136e-05 | 6.0136e-05 | 6.0136e-05 | 6.0136e-05 | 6.0136e-05 | 6.0136e-05 | 6.0136e-05 | 6.0136e-05 | 6.0136e-05 | 6.0136e-05 | 6.0136e-05 | 6.0136e-05 | 6.0136e-05 | 6.0136e-05 | 6.0136e-05 | 6.0136e-05 | 5.1616e-05 | 5.1616e-05 | 0.00028154 | 0.00028154 | 4.7015e-05 | 6.0136e-05 | 6.0136e-05 | 6.0136e-05 | 6.0136e-05 | 6.0136e-05 | 6.0136e-05 | 6.0136e-05 | 6.0136e-05 | 0.011067 | 0.011067 | 0.011067 | 0.011067 | 0.0087467 | 0.0087467 | 0.0087467 | 0.011992 | 0.011992 | 0.013406 | 0.014177 | 0.014377 | 0.014377 | 0.014377 | 0.014377 | 0.014377 | 0.014377 | 0.0022327 | 0.0022327 | 0.004524 | 0.0018915 | 0.0006624 | 0.00067197 | 0.00067197 | 0.00080181 | 0.00078404 | 0.00080181 | 0.00080181 | 0.00080181 | 0.00080181 | 0.00078404 | 0.00080181 | 0.00078404 | 0.00078404 | 0.00078404 | 0.00078404 | 0.002028 | 0.0022035 | 0.001287 | 0.0011895 | 0.01051 | 0.01051 | 0.01051 | 0.010516 | 0.01046 | 0.29313
| Phosphorus and compounds | 504 | Yes | -- | 0.0003162 | 0.00022481 | 0.002164 | 0.002164 | 0.002164 | 0.002164 | 0.002164 | 0.002164 | 0.0018069 | 0.0018069 | 0.0018069 | 0.0025212 | 0.0025212 | 0.0025212 | 0.0025212 | 0.0025212 | 0.0025212 | 0.0025212 | 0.0025212 | 0.0025212 | 0.0025212 | 0.0025212 | 0.0025212 | 0.0025212 | 0.0025212 | 0.0025212 | 0.0025212 | 0.0025212 | 0.0025212 | 0.0025212 | 0.0025212 | 0.0025212 | 0.002164 | 0.002164 | 0.012984 | 0.012984 | 0.0021682 | 0.0025212 | 0.0025212 | 0.0025212 | 0.0025212 | 0.0025212 | 0.0025212 | 0.0025212 | 0.0025212 | 0.023848 | 0.023848 | 0.023848 | 0.023848 | 0.018848 | 0.018848 | 0.018848 | 0.025842 | 0.025842 | 0.028889 | 0.030548 | 0.030981 | 0.030981 | 0.030981 | 0.030981 | 0.030981 | 0.030981 | 0.0048113 | 0.0048113 | 0.0097486 | 0.0040759 | 0.030548 | 0.03099 | 0.03099 | 0.036978 | 0.036158 | 0.036978 | 0.036978 | 0.036978 | 0.036978 | 0.036158 | 0.036978 | 0.036158 | 0.036158 | 0.036158 | 0.036158 | 0.0043701 | 0.0047483 | 0.0027733 | 0.0025632 | 0.022649 | 0.022649 | 0.022649 | 0.022661 | 0.022539 | 1.2559
| Selenium and Compounds | 7782-49-2 | Yes | Yes | 0.00049665 | 0.0003531 | 0.00058151 | 0.00058151 | 0.00058151 | 0.00058151 | 0.00058151 | 0.00058151 | 0.00048553 | 0.00048553 | 0.00048553 | 0.00067749 | 0.00067749 | 0.00067749 | 0.00067749 | 0.00067749 | 0.00067749 | 0.00067749 | 0.00067749 | 0.00067749 | 0.00067749 | 0.00067749 | 0.00067749 | 0.00067749 | 0.00067749 | 0.00067749 | 0.00067749 | 0.00067749 | 0.00067749 | 0.00067749 | 0.00067749 | 0.00067749 | 0.00058151 | 0.00058151 | 0.00058151 | 0.00058151 | 9.7107e-05 | 0.00067749 | 0.00067749 | 0.00067749 | 0.00067749 | 0.00067749 | 0.00067749 | 0.00067749 | 0.00067749 | 0.0062431 | 0.0062431 | 0.0062431 | 0.0062431 | 0.004934 | 0.004934 | 0.004934 | 0.006765 | 0.006765 | 0.0075625 | 0.007997 | 0.0081103 | 0.0081103 | 0.0081103 | 0.0081103 | 0.0081103 | 0.0081103 | 0.0012595 | 0.0012595 | 0.002552 | 0.001067 | 0.0013682 | 0.0013879 | 0.0013879 | 0.0016561 | 0.0016194 | 0.0016561 | 0.0016561 | 0.0016561 | 0.0016561 | 0.0016194 | 0.0016561 | 0.0016194 | 0.0016194 | 0.0016194 | 0.0016194 | 0.001144 | 0.001243 | 0.000726 | 0.000671 | 0.005929 | 0.005929 | 0.005929 | 0.0059323 | 0.0059004 | 0.20873
| Silver and compounds | 7440-22-4 | Yes | -- | 1.0839e-05 | 7.7061e-06 | 7.418e-05 | 7.418e-05 | 7.418e-05 | 7.418e-05 | 7.418e-05 | 7.418e-05 | 6.1937e-05 | 6.1937e-05 | 6.1937e-05 | 8.6423e-05 | 8.6423e-05 | 8.6423e-05 | 8.6423e-05 | 8.6423e-05 | 8.6423e-05 | 8.6423e-05 | 8.6423e-05 | 8.6423e-05 | 8.6423e-05 | 8.6423e-05 | 8.6423e-05 | 8.6423e-05 | 8.6423e-05 | 8.6423e-05 | 8.6423e-05 | 8.6423e-05 | 8.6423e-05 | 8.6423e-05 | 8.6423e-05 | 8.6423e-05 | 7.418e-05 | 7.418e-05 | 7.418e-05 | 7.418e-05 | 1.2387e-05 | 8.6423e-05 | 8.6423e-05 | 8.6423e-05 | 8.6423e-05 | 8.6423e-05 | 8.6423e-05 | 8.6423e-05 | 8.6423e-05 | 0.00013625 | 0.00013625 | 0.00013625 | 0.00013625 | 0.00010768 | 0.00010768 | 0.00010768 | 0.00014764 | 0.00014764 | 0.00016504 | 0.00017453 | 0.000177 | 0.000177 | 0.000177 | 0.000177 | 0.000177 | 0.000177 | 2.7487e-05 | 2.7487e-05 | 5.5695e-05 | 2.3286e-05 | 0.00017453 | 0.00017705 | 0.00017705 | 0.00021126 | 0.00020658 | 0.00021126 | 0.00021126 | 0.00021126 | 0.00021126 | 0.00020658 | 0.00021126 | 0.00020658 | 0.00020658 | 0.00020658 | 0.00020658 | 2.4967e-05 | 2.7127e-05 | 1.5844e-05 | 1.4644e-05 | 0.0001294 | 0.0001294 | 0.0001294 | 0.00012947 | 0.00012877 | 0.0099283
| Thallium and compounds | 7440-28-0 | Yes | -- | 5.4201e-05 | 3.8535e-05 | 0.00037094 | 0.00037094 | 0.00037094 | 0.00037094 | 0.00037094 | 0.00037094 | 0.00030972 | 0.00030972 | 0.00030972 | 0.00043217 | 0.00043217 | 0.00043217 | 0.00043217 | 0.00043217 | 0.00043217 | 0.00043217 | 0.00043217 | 0.00043217 | 0.00043217 | 0.00043217 | 0.00043217 | 0.00043217 | 0.00043217 | 0.00043217 | 0.00043217 | 0.00043217 | 0.00043217 | 0.00043217 | 0.00043217 | 0.00043217 | 0.00037094 | 0.00037094 | 0.00037094 | 0.00037094 | 6.1944e-05 | 0.00043217 | 0.00043217 | 0.00043217 | 0.00043217 | 0.00043217 | 0.00043217 | 0.00043217 | 0.00043217 | 0.00068133 | 0.00068133 | 0.00068133 | 0.00068133 | 0.00053847 | 0.00053847 | 0.00053847 | 0.00073829 | 0.00073829 | 0.00082532 | 0.00087274 | 0.00088511 | 0.00088511 | 0.00088511 | 0.00088511 | 0.00088511 | 0.00088511 | 0.00013745 | 0.00013745 | 0.00027851 | 0.00011645 | 0.00087274 | 0.00088535 | 0.00088535 | 0.0010564 | 0.001033 | 0.0010564 | 0.0010564 | 0.0010564 | 0.0010564 | 0.001033 | 0.0010564 | 0.001033 | 0.001033 | 0.001033 | 0.001033 | 0.00012485 | 0.00013565 | 7.9231e-05 | 7.3229e-05 | 0.00064705 | 0.00064705 | 0.00064705 | 0.00064741 | 0.00064393 | 0.049647
| Zinc and Compounds | 7440-66-6 | Yes | -- | 0.0011798 | 0.0008388 | 0.0080744 | 0.0080744 | 0.0080744 | 0.0080744 | 0.0080744 | 0.0080744 | 0.0067418 | 0.0067418 | 0.0067418 | 0.0094071 | 0.0094071 | 0.0094071 | 0.0094071 | 0.0094071 | 0.0094071 | 0.0094071 | 0.0094071 | 0.0094071 | 0.0094071 | 0.0094071 | 0.0094071 | 0.0094071 | 0.0094071 | 0.0094071 | 0.0094071 | 0.0094071 | 0.0094071 | 0.0094071 | 0.0094071 | 0.0094071 | 0.0080744 | 0.0080744 | 0.0080744 | 0.0080744 | 0.0013484 | 0.0094071 | 0.0094071 | 0.0094071 | 0.0094071 | 0.0094071 | 0.0094071 | 0.0094071 | 0.0094071 | 0.014831 | 0.014831 | 0.014831 | 0.014831 | 0.011721 | 0.011721 | 0.011721 | 0.01607 | 0.01607 | 0.017965 | 0.018997 | 0.019266 | 0.019266 | 0.019266 | 0.019266 | 0.019266 | 0.019266 | 0.002992 | 0.002992 | 0.0060624 | 0.0025347 | 0.018997 | 0.019272 | 0.019272 | 0.022995 | 0.022486 | 0.022995 | 0.022995 | 0.022995 | 0.022995 | 0.022486 | 0.022995 | 0.022486 | 0.022486 | 0.022486 | 0.022486 | 0.0027176 | 0.0029528 | 0.0017246 | 0.001594 | 0.014085 | 0.014085 | 0.014085 | 0.014092 | 0.014017 | 1.0807
ORGANIC COMPOUNDS
| 1,3-Butadiene | 106-99-0 | Yes | Yes | 0.050374 | 0.035814 | 0.34475 | 0.34475 | 0.34475 | 0.34475 | 0.34475 | 0.34475 | 0.28785 | 0.28785 | 0.28785 | 0.40165 | 0.40165 | 0.40165 | 0.40165 | 0.40165 | 0.40165 | 0.40165 | 0.40165 | 0.40165 | 0.40165 | 0.40165 | 0.40165 | 0.40165 | 0.40165 | 0.40165 | 0.40165 | 0.40165 | 0.40165 | 0.40165 | 0.40165 | 0.40165 | 0.34475 | 0.34475 | 0.36773 | 0.36773 | 0.061408 | 0.40165 | 0.40165 | 0.40165 | 0.40165 | 0.40165 | 0.40165 | 0.40165 | 0.40165 | 0.63321 | 0.63321 | 0.63321 | 0.63321 | 0.50045 | 0.50045 | 0.50045 | 0.68615 | 0.68615 | 0.76704 | 0.81111 | 0.8226 | 0.8226 | 0.8226 | 0.8226 | 0.8226 | 0.8226 | 0.12775 | 0.12775 | 0.25884 | 0.10822 | 0.81111 | 0.82283 | 0.82283 | 0.98181 | 0.96006 | 0.98181 | 0.98181 | 0.98181 | 0.98181 | 0.96006 | 0.98181 | 0.96006 | 0.96006 | 0.96006 | 0.96006 | 0.11951 | 0.12986 | 0.075846 | 0.0701 | 0.60136 | 0.60136 | 0.60136 | 0.6017 | 0.59846 | 46.2029
| 2-Methyl naphthalene | 91-57-6 | Yes | -- | -- | -- | 0.022752 | 0.022752 | 0.022752 | 0.022752 | 0.022752 | 0.022752 | 0.018997 | 0.018997 | 0.018997 | 0.026507 | 0.026507 | 0.026507 | 0.026507 | 0.026507 | 0.026507 | 0.026507 | 0.026507 | 0.026507 | 0.026507 | 0.026507 | 0.026507 | 0.026507 | 0.026507 | 0.026507 | 0.026507 | 0.026507 | 0.026507 | 0.026507 | 0.026507 | 0.026507 | 0.022752 | 0.022752 | 0.024052 | 0.024052 | 0.0040165 | 0.026507 | 0.026507 | 0.026507 | 0.026507 | 0.026507 | 0.026507 | 0.026507 | 0.026507 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.045883 | 0.046546 | 0.046546 | 0.055539 | 0.054309 | 0.055539 | 0.055539 | 0.055539 | 0.055539 | 0.054309 | 0.055539 | 0.054309 | 0.054309 | 0.054309 | 0.054309 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 1.8579
| Acenaphthene | 83-32-9 | Yes | -- | -- | -- | 0.0013203 | 0.0013203 | 0.0013203 | 0.0013203 | 0.0013203 | 0.0013203 | 0.0011024 | 0.0011024 | 0.0011024 | 0.0015382 | 0.0015382 | 0.0015382 | 0.0015382 | 0.0015382 | 0.0015382 | 0.0015382 | 0.0015382 | 0.0015382 | 0.0015382 | 0.0015382 | 0.0015382 | 0.0015382 | 0.0015382 | 0.0015382 | 0.0015382 | 0.0015382 | 0.0015382 | 0.0015382 | 0.0015382 | 0.0015382 | 0.0013203 | 0.0013203 | 0.0014368 | 0.0014368 | 0.00023993 | 0.0015382 | 0.0015382 | 0.0015382 | 0.0015382 | 0.0015382 | 0.0015382 | 0.0015382 | 0.0015382 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.0027408 | 0.0027804 | 0.0027804 | 0.0033176 | 0.0032441 | 0.0033176 | 0.0033176 | 0.0033176 | 0.0033176 | 0.0032441 | 0.0033176 | 0.0032441 | 0.0032441 | 0.0032441 | 0.0032441 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.10926
| Acenaphthylene | 208-96-8 | Yes | -- | -- | -- | 0.0015838 | 0.0015838 | 0.0015838 | 0.0015838 | 0.0015838 | 0.0015838 | 0.0013224 | 0.0013224 | 0.0013224 | 0.0018453 | 0.0018453 | 0.0018453 | 0.0018453 | 0.0018453 | 0.0018453 | 0.0018453 | 0.0018453 | 0.0018453 | 0.0018453 | 0.0018453 | 0.0018453 | 0.0018453 | 0.0018453 | 0.0018453 | 0.0018453 | 0.0018453 | 0.0018453 | 0.0018453 | 0.0018453 | 0.0018453 | 0.0015838 | 0.0015838 | 0.0015838 | 0.0015838 | 0.00026449 | 0.0018453 | 0.0018453 | 0.0018453 | 0.0018453 | 0.0018453 | 0.0018453 | 0.0018453 | 0.0018453 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.0030214 | 0.003065 | 0.003065 | 0.0036573 | 0.0035762 | 0.0036573 | 0.0036573 | 0.0036573 | 0.0036573 | 0.0035762 | 0.0036573 | 0.0035762 | 0.0035762 | 0.0035762 | 0.0035762 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.12613
| Acetaldehyde | 75-07-0 | Yes | Yes | 0.22385 | 0.15915 | 1.532 | 1.532 | 1.532 | 1.532 | 1.532 | 1.532 | 1.2791 | 1.2791 | 1.2791 | 1.7848 | 1.7848 | 1.7848 | 1.7848 | 1.7848 | 1.7848 | 1.7848 | 1.7848 | 1.7848 | 1.7848 | 1.7848 | 1.7848 | 1.7848 | 1.7848 | 1.7848 | 1.7848 | 1.7848 | 1.7848 | 1.7848 | 1.7848 | 1.7848 | 1.532 | 1.532 | 1.6976 | 1.6976 | 0.28348 | 1.7848 | 1.7848 | 1.7848 | 1.7848 | 1.7848 | 1.7848 | 1.7848 | 1.7848 | 2.2815 | 2.2815 | 2.2815 | 2.2815 | 1.8031 | 1.8031 | 1.8031 | 2.4722 | 2.4722 | 2.7637 | 2.9225 | 2.9639 | 2.9639 | 2.9639 | 2.9639 | 2.9639 | 2.9639 | 0.46028 | 0.46028 | 0.93262 | 0.38993 | 2.9225 | 2.9647 | 2.9647 | 3.5375 | 3.4591 | 3.5375 | 3.5375 | 3.5375 | 3.5375 | 3.4591 | 3.5375 | 3.4591 | 3.4591 | 3.4591 | 3.4591 | 0.43061 | 0.46788 | 0.27327 | 0.25257 | 2.1667 | 2.1667 | 2.1667 | 2.1679 | 2.1563 | 180.1877
| Acrolein | 107-02-8 | Yes | Yes | 0.007855 | 0.0055846 | 0.053758 | 0.053758 | 0.053758 | 0.053758 | 0.053758 | 0.053758 | 0.044885 | 0.044885 | 0.044885 | 0.062631 | 0.062631 | 0.062631 | 0.062631 | 0.062631 | 0.062631 | 0.062631 | 0.062631 | 0.062631 | 0.062631 | 0.062631 | 0.062631 | 0.062631 | 0.062631 | 0.062631 | 0.062631 | 0.062631 | 0.062631 | 0.062631 | 0.062631 | 0.062631 | 0.053758 | 0.053758 | 0.060926 | 0.060926 | 0.010174 | 0.062631 | 0.062631 | 0.062631 | 0.062631 | 0.062631 | 0.062631 | 0.062631 | 0.062631 | 0.098739 | 0.098739 | 0.098739 | 0.098739 | 0.078036 | 0.078036 | 0.078036 | 0.10699 | 0.10699 | 0.11961 | 0.12648 | 0.12827 | 0.12827 | 0.12827 | 0.12827 | 0.12827 | 0.12827 | 0.01992 | 0.01992 | 0.040362 | 0.016876 | 0.12648 | 0.12831 | 0.12831 | 0.1531 | 0.14971 | 0.1531 | 0.1531 | 0.1531 | 0.1531 | 0.14971 | 0.1531 | 0.14971 | 0.14971 | 0.14971 | 0.14971 | 0.018636 | 0.020249 | 0.011827 | 0.010931 | 0.093772 | 0.093772 | 0.093772 | 0.093825 | 0.09332 | 7.2124
| Anthracene | 120-12-7 | Yes | -- | -- | -- | 0.0010754 | 0.0010754 | 0.0010754 | 0.0010754 | 0.0010754 | 0.0010754 | 0.00089789 | 0.00089789 | 0.00089789 | 0.0012529 | 0.0012529 | 0.0012529 | 0.0012529 | 0.0012529 | 0.0012529 | 0.0012529 | 0.0012529 | 0.0012529 | 0.0012529 | 0.0012529 | 0.0012529 | 0.0012529 | 0.0012529 | 0.0012529 | 0.0012529 | 0.0012529 | 0.0012529 | 0.0012529 | 0.0012529 | 0.0012529 | 0.0010754 | 0.0010754 | 0.0008842 | 0.0008842 | 0.00014765 | 0.0012529 | 0.0012529 | 0.0012529 | 0.0012529 | 0.0012529 | 0.0012529 | 0.0012529 | 0.0012529 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.0016867 | 0.0017111 | 0.0017111 | 0.0020417 | 0.0019965 | 0.0020417 | 0.0020417 | 0.0020417 | 0.0020417 | 0.0019965 | 0.0020417 | 0.0019965 | 0.0019965 | 0.0019965 | 0.0019965 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.078884
| Benzene | 71-43-2 | Yes | Yes | 0.050362 | 0.035806 | 0.34467 | 0.34467 | 0.34467 | 0.34467 | 0.34467 | 0.34467 | 0.28778 | 0.28778 | 0.28778 | 0.40156 | 0.40156 | 0.40156 | 0.40156 | 0.40156 | 0.40156 | 0.40156 | 0.40156 | 0.40156 | 0.40156 | 0.40156 | 0.40156 | 0.40156 | 0.40156 | 0.40156 | 0.40156 | 0.40156 | 0.40156 | 0.40156 | 0.40156 | 0.40156 | 0.34467 | 0.34467 | 0.36437 | 0.36437 | 0.060846 | 0.40156 | 0.40156 | 0.40156 | 0.40156 | 0.40156 | 0.40156 | 0.40156 | 0.40156 | 0.54263 | 0.54263 | 0.54263 | 0.54263 | 0.42885 | 0.42885 | 0.42885 | 0.588 | 0.588 | 0.65731 | 0.69508 | 0.70493 | 0.70493 | 0.70493 | 0.70493 | 0.70493 | 0.70493 | 0.10947 | 0.10947 | 0.22181 | 0.092741 | 0.69508 | 0.70512 | 0.70512 | 0.84136 | 0.82272 | 0.84136 | 0.84136 | 0.84136 | 0.84136 | 0.82272 | 0.84136 | 0.82272 | 0.82272 | 0.82272 | 0.82272 | 0.10242 | 0.11128 | 0.064996 | 0.060072 | 0.51533 | 0.51533 | 0.51533 | 0.51562 | 0.51285 | 41.8932
| Chlorobenzene | 108-90-7 | Yes | Yes | 5.7155e-05 | 4.0635e-05 | 0.00039116 | 0.00039116 | 0.00039116 | 0.00039116 | 0.00039116 | 0.00039116 | 0.0003266 | 0.0003266 | 0.0003266 | 0.00045572 | 0.00045572 | 0.00045572 | 0.00045572 | 0.00045572 | 0.00045572 | 0.00045572 | 0.00045572 | 0.00045572 | 0.00045572 | 0.00045572 | 0.00045572 | 0.00045572 | 0.00045572 | 0.00045572 | 0.00045572 | 0.00045572 | 0.00045572 | 0.00045572 | 0.00045572 | 0.00045572 | 0.00039116 | 0.00039116 | 0.00039116 | 0.00039116 | 6.532e-05 | 0.00045572 | 0.00045572 | 0.00045572 | 0.00045572 | 0.00045572 | 0.00045572 | 0.00045572 | 0.00045572 | 0.00058253 | 0.00058253 | 0.00058253 | 0.00058253 | 0.00046039 | 0.00046039 | 0.00046039 | 0.00063124 | 0.00063124 | 0.00070565 | 0.00074619 | 0.00075676 | 0.00075676 | 0.00075676 | 0.00075676 | 0.00075676 | 0.00075676 | 0.00011752 | 0.00011752 | 0.00023812 | 9.9561e-05 | 0.00074619 | 0.00075697 | 0.00075697 | 0.00090323 | 0.00088322 | 0.00090323 | 0.00090323 | 0.00090323 | 0.00090323 | 0.00088322 | 0.00090323 | 0.00088322 | 0.00088322 | 0.00088322 | 0.00088322 | 0.00010995 | 0.00011946 | 6.9775e-05 | 6.4489e-05 | 0.00055323 | 0.00055323 | 0.00055323 | 0.00055354 | 0.00055056 | 0.045916
| Ethylbenzene | 100-41-4 | Yes | Yes | 0.0027782 | 0.0019752 | 0.019014 | 0.019014 | 0.019014 | 0.019014 | 0.019014 | 0.019014 | 0.015875 | 0.015875 | 0.015875 | 0.022152 | 0.022152 | 0.022152 | 0.022152 | 0.022152 | 0.022152 | 0.022152 | 0.022152 | 0.022152 | 0.022152 | 0.022152 | 0.022152 | 0.022152 | 0.022152 | 0.022152 | 0.022152 | 0.022152 | 0.022152 | 0.022152 | 0.022152 | 0.022152 | 0.019014 | 0.019014 | 0.021318 | 0.021318 | 0.0035599 | 0.022152 | 0.022152 | 0.022152 | 0.022152 | 0.022152 | 0.022152 | 0.022152 | 0.022152 | 0.031748 | 0.031748 | 0.031748 | 0.031748 | 0.025091 | 0.025091 | 0.025091 | 0.034402 | 0.034402 | 0.038458 | 0.040668 | 0.041244 | 0.041244 | 0.041244 | 0.041244 | 0.041244 | 0.041244 | 0.006405 | 0.006405 | 0.012978 | 0.0054261 | 0.040668 | 0.041255 | 0.041255 | 0.049226 | 0.048135 | 0.049226 | 0.049226 | 0.049226 | 0.049226 | 0.048135 | 0.049226 | 0.048135 | 0.048135 | 0.048135 | 0.048135 | 0.0059922 | 0.0065108 | 0.0038027 | 0.0035147 | 0.030151 | 0.030151 | 0.030151 | 0.030168 | 0.030006 | 2.3998
| Formaldehyde | 50-00-0 | Yes | Yes | 0.46843 | 0.33304 | 5.039 | 5.039 | 5.039 | 5.039 | 5.039 | 5.039 | 4.2073 | 4.2073 | 4.2073 | 5.8706 | 5.8706 | 5.8706 | 5.8706 | 5.8706 | 5.8706 | 5.8706 | 5.8706 | 5.8706 | 5.8706 | 5.8706 | 5.8706 | 5.8706 | 5.8706 | 5.8706 | 5.8706 | 5.8706 | 5.8706 | 5.8706 | 5.8706 | 5.8706 | 5.039 | 5.039 | 5.9028 | 5.9028 | 0.98571 | 5.8706 | 5.8706 | 5.8706 | 5.8706 | 5.8706 | 5.8706 | 5.8706 | 5.8706 | 5.0471 | 5.0471 | 5.0471 | 5.0471 | 3.9889 | 3.9889 | 3.9889 | 5.4691 | 5.4691 | 6.1138 | 6.4651 | 6.5567 | 6.5567 | 6.5567 | 6.5567 | 6.5567 | 6.5567 | 1.0182 | 1.0182 | 2.0631 | 0.86261 | 10.1618 | 10.3086 | 10.3086 | 12.3004 | 12.0278 | 12.3004 | 12.3004 | 12.3004 | 12.3004 | 12.0278 | 12.3004 | 12.0278 | 12.0278 | 12.0278 | 12.0278 | 0.95669 | 1.0395 | 0.60713 | 0.56114 | 4.7933 | 4.7933 | 4.7933 | 4.7959 | 4.7701 | 540.6079
| Hexane | 110-54-3 | Yes | Yes | 0.0083107 | 0.0059086 | 0.056877 | 0.056877 | 0.056877 | 0.056877 | 0.056877 | 0.056877 | 0.047489 | 0.047489 | 0.047489 | 0.066264 | 0.066264 | 0.066264 | 0.066264 | 0.066264 | 0.066264 | 0.066264 | 0.066264 | 0.066264 | 0.066264 | 0.066264 | 0.066264 | 0.066264 | 0.066264 | 0.066264 | 0.066264 | 0.066264 | 0.066264 | 0.066264 | 0.066264 | 0.066264 | 0.056877 | 0.056877 | 0.063987 | 0.063987 | 0.010685 | 0.066264 | 0.066264 | 0.066264 | 0.066264 | 0.066264 | 0.066264 | 0.066264 | 0.066264 | 0.078351 | 0.078351 | 0.078351 | 0.078351 | 0.061923 | 0.061923 | 0.061923 | 0.084901 | 0.084901 | 0.09491 | 0.10036 | 0.10178 | 0.10178 | 0.10178 | 0.10178 | 0.10178 | 0.10178 | 0.015807 | 0.015807 | 0.032028 | 0.013391 | 0.10036 | 0.10181 | 0.10181 | 0.12148 | 0.11879 | 0.12148 | 0.12148 | 0.12148 | 0.12148 | 0.11879 | 0.12148 | 0.11879 | 0.11879 | 0.11879 | 0.11879 | 0.014788 | 0.016068 | 0.0093848 | 0.0086738 | 0.074409 | 0.074409 | 0.074409 | 0.074451 | 0.07405 | 6.3903
| Propylene | 115-07-1 | Yes | Yes | 0.13431 | 0.095493 | 0.91923 | 0.91923 | 0.91923 | 0.91923 | 0.91923 | 0.91923 | 0.76751 | 0.76751 | 0.76751 | 1.0709 | 1.0709 | 1.0709 | 1.0709 | 1.0709 | 1.0709 | 1.0709 | 1.0709 | 1.0709 | 1.0709 | 1.0709 | 1.0709 | 1.0709 | 1.0709 | 1.0709 | 1.0709 | 1.0709 | 1.0709 | 1.0709 | 1.0709 | 1.0709 | 0.91923 | 0.91923 | 0.91923 | 0.91923 | 0.1535 | 1.0709 | 1.0709 | 1.0709 | 1.0709 | 1.0709 | 1.0709 | 1.0709 | 1.0709 | 1.369 | 1.369 | 1.369 | 1.369 | 1.0819 | 1.0819 | 1.0819 | 1.4834 | 1.4834 | 1.6583 | 1.7536 | 1.7784 | 1.7784 | 1.7784 | 1.7784 | 1.7784 | 1.7784 | 0.27618 | 0.27618 | 0.55959 | 0.23397 | 1.7536 | 1.7789 | 1.7789 | 2.1226 | 2.0756 | 2.1226 | 2.1226 | 2.1226 | 2.1226 | 2.0756 | 2.1226 | 2.0756 | 2.0756 | 2.0756 | 2.0756 | 0.25838 | 0.28074 | 0.16397 | 0.15155 | 1.3001 | 1.3001 | 1.3001 | 1.3008 | 1.2938 | 107.9019
| Toluene | 108-88-3 | Yes | Yes | 0.02198 | 0.015627 | 0.15043 | 0.15043 | 0.15043 | 0.15043 | 0.15043 | 0.15043 | 0.1256 | 0.1256 | 0.1256 | 0.17526 | 0.17526 | 0.17526 | 0.17526 | 0.17526 | 0.17526 | 0.17526 | 0.17526 | 0.17526 | 0.17526 | 0.17526 | 0.17526 | 0.17526 | 0.17526 | 0.17526 | 0.17526 | 0.17526 | 0.17526 | 0.17526 | 0.17526 | 0.17526 | 0.15043 | 0.15043 | 0.20614 | 0.20614 | 0.034424 | 0.17526 | 0.17526 | 0.17526 | 0.17526 | 0.17526 | 0.17526 | 0.17526 | 0.17526 | 0.307 | 0.307 | 0.307 | 0.307 | 0.24263 | 0.24263 | 0.24263 | 0.33266 | 0.33266 | 0.37188 | 0.39324 | 0.39882 | 0.39882 | 0.39882 | 0.39882 | 0.39882 | 0.39882 | 0.061935 | 0.061935 | 0.12549 | 0.052469 | 0.39324 | 0.39892 | 0.39892 | 0.476 | 0.46546 | 0.476 | 0.476 | 0.476 | 0.476 | 0.46546 | 0.476 | 0.46546 | 0.46546 | 0.46546 | 0.46546 | 0.057943 | 0.062957 | 0.036772 | 0.033986 | 0.29155 | 0.29155 | 0.29155 | 0.29171 | 0.29015 | 21.716
| Xylene (mixed isomers) | 1330-20-7 | Yes | Yes | 0.011134 | 0.0079162 | 0.076202 | 0.076202 | 0.076202 | 0.076202 | 0.076202 | 0.076202 | 0.063625 | 0.063625 | 0.063625 | 0.088779 | 0.088779 | 0.088779 | 0.088779 | 0.088779 | 0.088779 | 0.088779 | 0.088779 | 0.088779 | 0.088779 | 0.088779 | 0.088779 | 0.088779 | 0.088779 | 0.088779 | 0.088779 | 0.088779 | 0.088779 | 0.088779 | 0.088779 | 0.088779 | 0.076202 | 0.076202 | 0.082926 | 0.082926 | 0.013848 | 0.088779 | 0.088779 | 0.088779 | 0.088779 | 0.088779 | 0.088779 | 0.088779 | 0.088779 | 0.1235 | 0.1235 | 0.1235 | 0.1235 | 0.097603 | 0.097603 | 0.097603 | 0.13382 | 0.13382 | 0.1496 | 0.15819 | 0.16043 | 0.16043 | 0.16043 | 0.16043 | 0.16043 | 0.16043 | 0.024915 | 0.024915 | 0.050482 | 0.021107 | 0.15819 | 0.16048 | 0.16048 | 0.19149 | 0.18724 | 0.19149 | 0.19149 | 0.19149 | 0.19149 | 0.18724 | 0.19149 | 0.18724 | 0.18724 | 0.18724 | 0.18724 | 0.023309 | 0.025326 | 0.014792 | 0.013672 | 0.11728 | 0.11728 | 0.11728 | 0.11735 | 0.11672 | 9.4346
INORGANIC COMPOUNDS
| Ammonia | 7664-41-7 | Yes | Yes | 0.61789 | 0.4393 | 4.2288 | 4.2288 | 4.2288 | 4.2288 | 4.2288 | 4.2288 | 3.5308 | 3.5308 | 3.5308 | 4.9267 | 4.9267 | 4.9267 | 4.9267 | 4.9267 | 4.9267 | 4.9267 | 4.9267 | 4.9267 | 4.9267 | 4.9267 | 4.9267 | 4.9267 | 4.9267 | 4.9267 | 4.9267 | 4.9267 | 4.9267 | 4.9267 | 4.9267 | 4.9267 | 4.2288 | 4.2288 | 4.2288 | 4.2288 | 0.70616 | 4.9267 | 4.9267 | 4.9267 | 4.9267 | 4.9267 | 4.9267 | 4.9267 | 4.9267 | 2.3301 | 2.3301 | 2.3301 | 2.3301 | 1.8416 | 1.8416 | 1.8416 | 2.5249 | 2.5249 | 2.8226 | 2.9848 | 3.0271 | 3.0271 | 3.0271 | 3.0271 | 3.0271 | 3.0271 | 0.47009 | 0.47009 | 0.9525 | 0.39824 | 2.9848 | 3.0279 | 3.0279 | 3.6129 | 3.5329 | 3.6129 | 3.6129 | 3.6129 | 3.6129 | 3.5329 | 3.6129 | 3.5329 | 3.5329 | 3.5329 | 3.5329 | 0.4398 | 0.47785 | 0.2791 | 0.25796 | 2.2129 | 2.2129 | 2.2129 | 2.2142 | 2.2022 | 308.0993
| Hydrochloric Acid | 7647-01-0 | Yes | Yes | 0.14389 | 0.1023 | 0.98477 | 0.98477 | 0.98477 | 0.98477 | 0.98477 | 0.98477 | 0.82224 | 0.82224 | 0.82224 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 0.98477 | 0.98477 | 0.29543 | 0.29543 | 0.049334 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 1.1473 | 0.54263 | 0.54263 | 0.54263 | 0.54263 | 0.42885 | 0.42885 | 0.42885 | 0.588 | 0.588 | 0.65731 | 0.69508 | 0.70493 | 0.70493 | 0.70493 | 0.70493 | 0.70493 | 0.70493 | 0.10947 | 0.10947 | 0.22181 | 0.092741 | 0.69508 | 0.70512 | 0.70512 | 0.84136 | 0.82272 | 0.84136 | 0.84136 | 0.84136 | 0.84136 | 0.82272 | 0.84136 | 0.82272 | 0.82272 | 0.82272 | 0.82272 | 0.10242 | 0.11128 | 0.064996 | 0.060072 | 0.51533 | 0.51533 | 0.51533 | 0.51562 | 0.51285 | 70.2548
POLYCYCLIC AROMATIC HYDROCARBONS (PAH)
| Benz[a]anthracene | 56-55-3 | Yes | Yes | -- | -- | 9.4937e-05 | 9.4937e-05 | 9.4937e-05 | 9.4937e-05 | 9.4937e-05 | 9.4937e-05 | 7.9268e-05 | 7.9268e-05 | 7.9268e-05 | 0.00011061 | 0.00011061 | 0.00011061 | 0.00011061 | 0.00011061 | 0.00011061 | 0.00011061 | 0.00011061 | 0.00011061 | 0.00011061 | 0.00011061 | 0.00011061 | 0.00011061 | 0.00011061 | 0.00011061 | 0.00011061 | 0.00011061 | 0.00011061 | 0.00011061 | 0.00011061 | 0.00011061 | 9.4937e-05 | 9.4937e-05 | 9.4937e-05 | 9.4937e-05 | 1.5854e-05 | 0.00011061 | 0.00011061 | 0.00011061 | 0.00011061 | 0.00011061 | 0.00011061 | 0.00011061 | 0.00011061 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.00018111 | 0.00018372 | 0.00018372 | 0.00021922 | 0.00021436 | 0.00021922 | 0.00021922 | 0.00021922 | 0.00021922 | 0.00021436 | 0.00021922 | 0.00021436 | 0.00021436 | 0.00021436 | 0.00021436 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.0075607
| Benzo(a)pyrene | 50-32-8 | Yes | Yes | 9.5155e-06 | 6.7652e-06 | 2.6614e-05 | 2.6614e-05 | 2.6614e-05 | 2.6614e-05 | 2.6614e-05 | 2.6614e-05 | 2.2221e-05 | 2.2221e-05 | 2.2221e-05 | 3.1007e-05 | 3.1007e-05 | 3.1007e-05 | 3.1007e-05 | 3.1007e-05 | 3.1007e-05 | 3.1007e-05 | 3.1007e-05 | 3.1007e-05 | 3.1007e-05 | 3.1007e-05 | 3.1007e-05 | 3.1007e-05 | 3.1007e-05 | 3.1007e-05 | 3.1007e-05 | 3.1007e-05 | 3.1007e-05 | 3.1007e-05 | 3.1007e-05 | 3.1007e-05 | 2.6614e-05 | 2.6614e-05 | 2.8135e-05 | 2.8135e-05 | 4.6982e-06 | 3.1007e-05 | 3.1007e-05 | 3.1007e-05 | 3.1007e-05 | 3.1007e-05 | 3.1007e-05 | 3.1007e-05 | 3.1007e-05 | 0.00010253 | 0.00010253 | 0.00010253 | 0.00010253 | 8.1029e-05 | 8.1029e-05 | 8.1029e-05 | 0.0001111 | 0.0001111 | 0.00012419 | 0.00013133 | 0.00013319 | 0.00013319 | 0.00013319 | 0.00013319 | 0.00013319 | 0.00013319 | 2.0684e-05 | 2.0684e-05 | 4.191e-05 | 1.7523e-05 | 5.3671e-05 | 5.4446e-05 | 5.4446e-05 | 6.4966e-05 | 6.3526e-05 | 6.4966e-05 | 6.4966e-05 | 6.4966e-05 | 6.4966e-05 | 6.3526e-05 | 6.4966e-05 | 6.3526e-05 | 6.3526e-05 | 6.3526e-05 | 6.3526e-05 | 1.9351e-05 | 2.1026e-05 | 1.228e-05 | 1.135e-05 | 9.7368e-05 | 9.7368e-05 | 9.7368e-05 | 9.7423e-05 | 9.6899e-05 | 0.0047708
| Benzo[b]fluoranthene | 205-99-2 | Yes | Yes | -- | -- | 8.6747e-05 | 8.6747e-05 | 8.6747e-05 | 8.6747e-05 | 8.6747e-05 | 8.6747e-05 | 7.2429e-05 | 7.2429e-05 | 7.2429e-05 | 0.00010106 | 0.00010106 | 0.00010106 | 0.00010106 | 0.00010106 | 0.00010106 | 0.00010106 | 0.00010106 | 0.00010106 | 0.00010106 | 0.00010106 | 0.00010106 | 0.00010106 | 0.00010106 | 0.00010106 | 0.00010106 | 0.00010106 | 0.00010106 | 0.00010106 | 0.00010106 | 0.00010106 | 8.6747e-05 | 8.6747e-05 | 8.6747e-05 | 8.6747e-05 | 1.4486e-05 | 0.00010106 | 0.00010106 | 0.00010106 | 0.00010106 | 0.00010106 | 0.00010106 | 0.00010106 | 0.00010106 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.00016548 | 0.00016787 | 0.00016787 | 0.00020031 | 0.00019587 | 0.00020031 | 0.00020031 | 0.00020031 | 0.00020031 | 0.00019587 | 0.00020031 | 0.00019587 | 0.00019587 | 0.00019587 | 0.00019587 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.0069084
| Benzo[e]pyrene | 192-97-2 | Yes | -- | -- | -- | 6.0809e-05 | 6.0809e-05 | 6.0809e-05 | 6.0809e-05 | 6.0809e-05 | 6.0809e-05 | 5.0773e-05 | 5.0773e-05 | 5.0773e-05 | 7.0846e-05 | 7.0846e-05 | 7.0846e-05 | 7.0846e-05 | 7.0846e-05 | 7.0846e-05 | 7.0846e-05 | 7.0846e-05 | 7.0846e-05 | 7.0846e-05 | 7.0846e-05 | 7.0846e-05 | 7.0846e-05 | 7.0846e-05 | 7.0846e-05 | 7.0846e-05 | 7.0846e-05 | 7.0846e-05 | 7.0846e-05 | 7.0846e-05 | 7.0846e-05 | 6.0809e-05 | 6.0809e-05 | 6.4284e-05 | 6.4284e-05 | 1.0735e-05 | 7.0846e-05 | 7.0846e-05 | 7.0846e-05 | 7.0846e-05 | 7.0846e-05 | 7.0846e-05 | 7.0846e-05 | 7.0846e-05 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.00012263 | 0.0001244 | 0.0001244 | 0.00014844 | 0.00014515 | 0.00014844 | 0.00014844 | 0.00014844 | 0.00014844 | 0.00014515 | 0.00014844 | 0.00014515 | 0.00014515 | 0.00014515 | 0.00014515 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.0049656
| Benzo[g,h,i]perylene | 191-24-2 | Yes | Yes | -- | -- | 4.2782e-05 | 4.2782e-05 | 4.2782e-05 | 4.2782e-05 | 4.2782e-05 | 4.2782e-05 | 3.5721e-05 | 3.5721e-05 | 3.5721e-05 | 4.9843e-05 | 4.9843e-05 | 4.9843e-05 | 4.9843e-05 | 4.9843e-05 | 4.9843e-05 | 4.9843e-05 | 4.9843e-05 | 4.9843e-05 | 4.9843e-05 | 4.9843e-05 | 4.9843e-05 | 4.9843e-05 | 4.9843e-05 | 4.9843e-05 | 4.9843e-05 | 4.9843e-05 | 4.9843e-05 | 4.9843e-05 | 4.9843e-05 | 4.9843e-05 | 4.2782e-05 | 4.2782e-05 | 4.2782e-05 | 4.2782e-05 | 7.1442e-06 | 4.9843e-05 | 4.9843e-05 | 4.9843e-05 | 4.9843e-05 | 4.9843e-05 | 4.9843e-05 | 4.9843e-05 | 4.9843e-05 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 8.1612e-05 | 8.2791e-05 | 8.2791e-05 | 9.8788e-05 | 9.6599e-05 | 9.8788e-05 | 9.8788e-05 | 9.8788e-05 | 9.8788e-05 | 9.6599e-05 | 9.8788e-05 | 9.6599e-05 | 9.6599e-05 | 9.6599e-05 | 9.6599e-05 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.0034071
| Benzo[k]fluoranthene | 207-08-9 | Yes | Yes | -- | -- | 2.5532e-05 | 2.5532e-05 | 2.5532e-05 | 2.5532e-05 | 2.5532e-05 | 2.5532e-05 | 2.1318e-05 | 2.1318e-05 | 2.1318e-05 | 2.9746e-05 | 2.9746e-05 | 2.9746e-05 | 2.9746e-05 | 2.9746e-05 | 2.9746e-05 | 2.9746e-05 | 2.9746e-05 | 2.9746e-05 | 2.9746e-05 | 2.9746e-05 | 2.9746e-05 | 2.9746e-05 | 2.9746e-05 | 2.9746e-05 | 2.9746e-05 | 2.9746e-05 | 2.9746e-05 | 2.9746e-05 | 2.9746e-05 | 2.9746e-05 | 2.5532e-05 | 2.5532e-05 | 2.5532e-05 | 2.5532e-05 | 4.2636e-06 | 2.9746e-05 | 2.9746e-05 | 2.9746e-05 | 2.9746e-05 | 2.9746e-05 | 2.9746e-05 | 2.9746e-05 | 2.9746e-05 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 4.8705e-05 | 4.9409e-05 | 4.9409e-05 | 5.8956e-05 | 5.7649e-05 | 5.8956e-05 | 5.8956e-05 | 5.8956e-05 | 5.8956e-05 | 5.7649e-05 | 5.8956e-05 | 5.7649e-05 | 5.7649e-05 | 5.7649e-05 | 5.7649e-05 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.0020333
| Chrysene | 218-01-9 | Yes | Yes | -- | -- | 0.00012396 | 0.00012396 | 0.00012396 | 0.00012396 | 0.00012396 | 0.00012396 | 0.0001035 | 0.0001035 | 0.0001035 | 0.00014441 | 0.00014441 | 0.00014441 | 0.00014441 | 0.00014441 | 0.00014441 | 0.00014441 | 0.00014441 | 0.00014441 | 0.00014441 | 0.00014441 | 0.00014441 | 0.00014441 | 0.00014441 | 0.00014441 | 0.00014441 | 0.00014441 | 0.00014441 | 0.00014441 | 0.00014441 | 0.00014441 | 0.00012396 | 0.00012396 | 0.00013104 | 0.00013104 | 2.1882e-05 | 0.00014441 | 0.00014441 | 0.00014441 | 0.00014441 | 0.00014441 | 0.00014441 | 0.00014441 | 0.00014441 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.00024997 | 0.00025358 | 0.00025358 | 0.00030258 | 0.00029588 | 0.00030258 | 0.00030258 | 0.00030258 | 0.00030258 | 0.00029588 | 0.00030258 | 0.00029588 | 0.00029588 | 0.00029588 | 0.00029588 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.010122
| Dibenz[a,h]anthracene | 53-70-3 | Yes | Yes | -- | -- | 1.9185e-06 | 1.9185e-06 | 1.9185e-06 | 1.9185e-06 | 1.9185e-06 | 1.9185e-06 | 1.6019e-06 | 1.6019e-06 | 1.6019e-06 | 2.2352e-06 | 2.2352e-06 | 2.2352e-06 | 2.2352e-06 | 2.2352e-06 | 2.2352e-06 | 2.2352e-06 | 2.2352e-06 | 2.2352e-06 | 2.2352e-06 | 2.2352e-06 | 2.2352e-06 | 2.2352e-06 | 2.2352e-06 | 2.2352e-06 | 2.2352e-06 | 2.2352e-06 | 2.2352e-06 | 2.2352e-06 | 2.2352e-06 | 2.2352e-06 | 1.9185e-06 | 1.9185e-06 | 2.0281e-06 | 2.0281e-06 | 3.3868e-07 | 2.2352e-06 | 2.2352e-06 | 2.2352e-06 | 2.2352e-06 | 2.2352e-06 | 2.2352e-06 | 2.2352e-06 | 2.2352e-06 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 3.869e-06 | 3.9248e-06 | 3.9248e-06 | 4.6832e-06 | 4.5794e-06 | 4.6832e-06 | 4.6832e-06 | 4.6832e-06 | 4.6832e-06 | 4.5794e-06 | 4.6832e-06 | 4.5794e-06 | 4.5794e-06 | 4.5794e-06 | 4.5794e-06 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.00015666
| Fluoranthene | 206-44-0 | Yes | Yes | -- | -- | 0.00062578 | 0.00062578 | 0.00062578 | 0.00062578 | 0.00062578 | 0.00062578 | 0.00052249 | 0.00052249 | 0.00052249 | 0.00072906 | 0.00072906 | 0.00072906 | 0.00072906 | 0.00072906 | 0.00072906 | 0.00072906 | 0.00072906 | 0.00072906 | 0.00072906 | 0.00072906 | 0.00072906 | 0.00072906 | 0.00072906 | 0.00072906 | 0.00072906 | 0.00072906 | 0.00072906 | 0.00072906 | 0.00072906 | 0.00072906 | 0.00062578 | 0.00062578 | 0.00072356 | 0.00072356 | 0.00012083 | 0.00072906 | 0.00072906 | 0.00072906 | 0.00072906 | 0.00072906 | 0.00072906 | 0.00072906 | 0.00072906 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.0013803 | 0.0014002 | 0.0014002 | 0.0016708 | 0.0016337 | 0.0016708 | 0.0016708 | 0.0016708 | 0.0016708 | 0.0016337 | 0.0016708 | 0.0016337 | 0.0016337 | 0.0016337 | 0.0016337 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.053292
| Fluorene | 86-73-7 | Yes | -- | -- | -- | 0.0036949 | 0.0036949 | 0.0036949 | 0.0036949 | 0.0036949 | 0.0036949 | 0.0030851 | 0.0030851 | 0.0030851 | 0.0043048 | 0.0043048 | 0.0043048 | 0.0043048 | 0.0043048 | 0.0043048 | 0.0043048 | 0.0043048 | 0.0043048 | 0.0043048 | 0.0043048 | 0.0043048 | 0.0043048 | 0.0043048 | 0.0043048 | 0.0043048 | 0.0043048 | 0.0043048 | 0.0043048 | 0.0043048 | 0.0043048 | 0.0036949 | 0.0036949 | 0.0042723 | 0.0042723 | 0.00071343 | 0.0043048 | 0.0043048 | 0.0043048 | 0.0043048 | 0.0043048 | 0.0043048 | 0.0043048 | 0.0043048 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.0081499 | 0.0082676 | 0.0082676 | 0.0098651 | 0.0096465 | 0.0098651 | 0.0098651 | 0.0098651 | 0.0098651 | 0.0096465 | 0.0098651 | 0.0096465 | 0.0096465 | 0.0096465 | 0.0096465 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.31467
| Indeno[1,2,3-cd]pyrene | 193-39-5 | Yes | Yes | -- | -- | 1.6985e-05 | 1.6985e-05 | 1.6985e-05 | 1.6985e-05 | 1.6985e-05 | 1.6985e-05 | 1.4182e-05 | 1.4182e-05 | 1.4182e-05 | 1.9789e-05 | 1.9789e-05 | 1.9789e-05 | 1.9789e-05 | 1.9789e-05 | 1.9789e-05 | 1.9789e-05 | 1.9789e-05 | 1.9789e-05 | 1.9789e-05 | 1.9789e-05 | 1.9789e-05 | 1.9789e-05 | 1.9789e-05 | 1.9789e-05 | 1.9789e-05 | 1.9789e-05 | 1.9789e-05 | 1.9789e-05 | 1.9789e-05 | 1.9789e-05 | 1.6985e-05 | 1.6985e-05 | 2.0949e-05 | 2.0949e-05 | 3.4982e-06 | 1.9789e-05 | 1.9789e-05 | 1.9789e-05 | 1.9789e-05 | 1.9789e-05 | 1.9789e-05 | 1.9789e-05 | 1.9789e-05 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 3.9962e-05 | 4.0539e-05 | 4.0539e-05 | 4.8372e-05 | 4.7301e-05 | 4.8372e-05 | 4.8372e-05 | 4.8372e-05 | 4.8372e-05 | 4.7301e-05 | 4.8372e-05 | 4.7301e-05 | 4.7301e-05 | 4.7301e-05 | 4.7301e-05 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.0014928
| Naphthalene | 91-20-3 | Yes | Yes | 0.0053255 | 0.0037862 | 0.048754 | 0.048754 | 0.048754 | 0.048754 | 0.048754 | 0.048754 | 0.040707 | 0.040707 | 0.040707 | 0.056801 | 0.056801 | 0.056801 | 0.056801 | 0.056801 | 0.056801 | 0.056801 | 0.056801 | 0.056801 | 0.056801 | 0.056801 | 0.056801 | 0.056801 | 0.056801 | 0.056801 | 0.056801 | 0.056801 | 0.056801 | 0.056801 | 0.056801 | 0.056801 | 0.048754 | 0.048754 | 0.05154 | 0.05154 | 0.0086067 | 0.056801 | 0.056801 | 0.056801 | 0.056801 | 0.056801 | 0.056801 | 0.056801 | 0.056801 | 0.05738 | 0.05738 | 0.05738 | 0.05738 | 0.045349 | 0.045349 | 0.045349 | 0.062177 | 0.062177 | 0.069507 | 0.0735 | 0.074541 | 0.074541 | 0.074541 | 0.074541 | 0.074541 | 0.074541 | 0.011576 | 0.011576 | 0.023455 | 0.0098067 | 0.09832 | 0.09974 | 0.09974 | 0.11901 | 0.11637 | 0.11901 | 0.11901 | 0.11901 | 0.11901 | 0.11637 | 0.11901 | 0.11637 | 0.11637 | 0.11637 | 0.11637 | 0.01083 | 0.011767 | 0.0068729 | 0.0063522 | 0.054493 | 0.054493 | 0.054493 | 0.054523 | 0.05423 | 5.4349
| Perylene | 198-55-0 | Yes | -- | -- | -- | 2.3044e-06 | 2.3044e-06 | 2.3044e-06 | 2.3044e-06 | 2.3044e-06 | 2.3044e-06 | 1.9241e-06 | 1.9241e-06 | 1.9241e-06 | 2.6848e-06 | 2.6848e-06 | 2.6848e-06 | 2.6848e-06 | 2.6848e-06 | 2.6848e-06 | 2.6848e-06 | 2.6848e-06 | 2.6848e-06 | 2.6848e-06 | 2.6848e-06 | 2.6848e-06 | 2.6848e-06 | 2.6848e-06 | 2.6848e-06 | 2.6848e-06 | 2.6848e-06 | 2.6848e-06 | 2.6848e-06 | 2.6848e-06 | 2.6848e-06 | 2.3044e-06 | 2.3044e-06 | 2.3044e-06 | 2.3044e-06 | 3.8482e-07 | 2.6848e-06 | 2.6848e-06 | 2.6848e-06 | 2.6848e-06 | 2.6848e-06 | 2.6848e-06 | 2.6848e-06 | 2.6848e-06 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 4.396e-06 | 4.4595e-06 | 4.4595e-06 | 5.3211e-06 | 5.2032e-06 | 5.3211e-06 | 5.3211e-06 | 5.3211e-06 | 5.3211e-06 | 5.2032e-06 | 5.3211e-06 | 5.2032e-06 | 5.2032e-06 | 5.2032e-06 | 5.2032e-06 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.00018352
| Phenanthrene | 85-01-8 | Yes | -- | -- | -- | 0.0088832 | 0.0088832 | 0.0088832 | 0.0088832 | 0.0088832 | 0.0088832 | 0.007417 | 0.007417 | 0.007417 | 0.010349 | 0.010349 | 0.010349 | 0.010349 | 0.010349 | 0.010349 | 0.010349 | 0.010349 | 0.010349 | 0.010349 | 0.010349 | 0.010349 | 0.010349 | 0.010349 | 0.010349 | 0.010349 | 0.010349 | 0.010349 | 0.010349 | 0.010349 | 0.010349 | 0.0088832 | 0.0088832 | 0.0088832 | 0.0088832 | 0.0014834 | 0.010349 | 0.010349 | 0.010349 | 0.010349 | 0.010349 | 0.010349 | 0.010349 | 0.010349 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.016946 | 0.017191 | 0.017191 | 0.020512 | 0.020058 | 0.020512 | 0.020512 | 0.020512 | 0.020512 | 0.020058 | 0.020512 | 0.020058 | 0.020058 | 0.020058 | 0.020058 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.70744
| Pyrene | 129-00-0 | Yes | -- | -- | -- | 0.0024448 | 0.0024448 | 0.0024448 | 0.0024448 | 0.0024448 | 0.0024448 | 0.0020413 | 0.0020413 | 0.0020413 | 0.0028483 | 0.0028483 | 0.0028483 | 0.0028483 | 0.0028483 | 0.0028483 | 0.0028483 | 0.0028483 | 0.0028483 | 0.0028483 | 0.0028483 | 0.0028483 | 0.0028483 | 0.0028483 | 0.0028483 | 0.0028483 | 0.0028483 | 0.0028483 | 0.0028483 | 0.0028483 | 0.0028483 | 0.0024448 | 0.0024448 | 0.0024448 | 0.0024448 | 0.00040825 | 0.0028483 | 0.0028483 | 0.0028483 | 0.0028483 | 0.0028483 | 0.0028483 | 0.0028483 | 0.0028483 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.0046637 | 0.0047311 | 0.0047311 | 0.0056452 | 0.0055201 | 0.0056452 | 0.0056452 | 0.0056452 | 0.0056452 | 0.0055201 | 0.0056452 | 0.0055201 | 0.0055201 | 0.0055201 | 0.0055201 | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.1947
| PAH | 401 | Yes | Yes | 0.010345 | 0.007355 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.10544 | 0.10544 | 0.10544 | 0.10544 | 0.083331 | 0.083331 | 0.083331 | 0.11425 | 0.11425 | 0.12772 | 0.13506 | 0.13697 | 0.13697 | 0.13697 | 0.13697 | 0.13697 | 0.13697 | 0.021272 | 0.021272 | 0.043101 | 0.018021 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0.019901 | 0.021623 | 0.012629 | 0.011673 | 0.10013 | 0.10013 | 0.10013 | 0.10019 | 0.099652 | 2.6723
DIESEL PARTICULATE MATTER (DPM)
| DPM | 200 | Yes | Yes | 1.8112 | 1.2877 | 6.2811 | 6.2811 | 6.2811 | 6.2811 | 6.2811 | 6.2811 | 5.2444 | 5.2444 | 5.2444 | 7.3178 | 7.3178 | 7.3178 | 7.3178 | 7.3178 | 7.3178 | 7.3178 | 7.3178 | 7.3178 | 7.3178 | 7.3178 | 7.3178 | 7.3178 | 7.3178 | 7.3178 | 7.3178 | 7.3178 | 7.3178 | 7.3178 | 7.3178 | 7.3178 | 6.2811 | 6.2811 | 8.973 | 8.973 | 1.4984 | 7.3178 | 7.3178 | 7.3178 | 7.3178 | 7.3178 | 7.3178 | 7.3178 | 7.3178 | 97.5743 | 97.5743 | 97.5743 | 97.5743 | 77.1156 | 77.1156 | 77.1156 | 105.732 | 105.732 | 118.1964 | 124.9873 | 126.7581 | 126.7581 | 126.7581 | 126.7581 | 126.7581 | 126.7581 | 19.6851 | 19.6851 | 39.8859 | 16.6764 | 63.334 | 64.2488 | 64.2488 | 76.6629 | 74.9641 | 76.6629 | 76.6629 | 76.6629 | 76.6629 | 74.9641 | 76.6629 | 74.9641 | 74.9641 | 74.9641 | 74.9641 | 18.4164 | 20.0102 | 11.6873 | 10.8019 | 92.666 | 92.666 | 92.666 | 92.7175 | 92.219 | 3858.9598
Total TAC Emissions Estimate | [94 empty] | 5217.5846