## Input_Cooling Towers
Table 1
Input Cooling Tower Rates and Parameters
Intel Corporation
Toxics Emissions Sub-Unit (TESU) ID (1) |  |  | Site | Building | Maximum Recirculation Rate (2) (GPM) | Average Recirculation Rate (2) (GPM) | Drift Loss of Circulating Water (2) (%) | Stack ID
RAC4-CT114-1 |  |  | Ronler Acres | CUB4 | 10722 | 5361 | 0.0005 | CTC4_01
RAC4-CT114-2 |  |  | Ronler Acres | CUB4 | 10722 | 5361 | 0.0005 | CTC4_02
RAC4-CT114-3 |  |  | Ronler Acres | CUB4 | 10722 | 5361 | 0.0005 | CTC4_03
RAC4-CT114-4 |  |  | Ronler Acres | CUB4 | 10722 | 5361 | 0.0005 | CTC4_04
RAC4-CT114-5 |  |  | Ronler Acres | CUB4 | 10722 | 5361 | 0.0005 | CTC4_05
RAC4-CT114-6 |  |  | Ronler Acres | CUB4 | 10722 | 5361 | 0.0005 | CTC4_06
RAC4-CT114-7 |  |  | Ronler Acres | CUB4 | 10722 | 5361 | 0.0005 | CTC4_07
RAC4-CT114-8 |  |  | Ronler Acres | CUB4 | 10722 | 5361 | 0.0005 | CTC4_08
RAC4-CT114-9 |  |  | Ronler Acres | CUB4 | 10722 | 5361 | 0.0005 | CTC4_09
RAC4-CT114-10 |  |  | Ronler Acres | CUB4 | 10722 | 5361 | 0.0005 | CTC4_10
RAC4-CT114-11 |  |  | Ronler Acres | CUB4 | 10722 | 5361 | 0.0005 | CTC4_11
RAC4-CT114-12 |  |  | Ronler Acres | CUB4 | 10722 | 5361 | 0.0005 | CTC4_12
RAC4-CT114-13 |  |  | Ronler Acres | CUB4 | 10722 | 5361 | 0.0005 | CTC4_13
RAC4-CT114-14 |  |  | Ronler Acres | CUB4 | 10722 | 5361 | 0.0005 | CTC4_14
RAC4-CT114-15 |  |  | Ronler Acres | CUB4 | 10722 | 5361 | 0.0005 | CTC4_15
RAC4-CT114-16 |  |  | Ronler Acres | CUB4 | 10722 | 5361 | 0.0005 | CTC4_16
RAC4-CT114-17 |  |  | Ronler Acres | CUB4X | 10722 | 5361 | 0.0005 | CTC4_17
RAC4-CT114-18 |  |  | Ronler Acres | CUB4X | 10722 | 5361 | 0.0005 | CTC4_18
RAC4-CT114-19 |  |  | Ronler Acres | CUB4X | 10722 | 5361 | 0.0005 | CTC4_19
RAC4-CT114-20 |  |  | Ronler Acres | CUB4X | 10722 | 5361 | 0.0005 | CTC4_20
RAC5-CT115-1 |  |  | Ronler Acres | CUB5 | 10722 | 5361 | 0.0005 | CTC5_01
RAC5-CT115-2 |  |  | Ronler Acres | CUB5 | 10722 | 5361 | 0.0005 | CTC5_02
RAC5-CT115-3 |  |  | Ronler Acres | CUB5 | 10722 | 5361 | 0.0005 | CTC5_03
RAC5-CT115-4 |  |  | Ronler Acres | CUB5 | 10722 | 5361 | 0.0005 | CTC5_04
RAC5-CT115-5 |  |  | Ronler Acres | CUB5 | 10722 | 5361 | 0.0005 | CTC5_05
RAC5-CT115-6 |  |  | Ronler Acres | CUB5 | 10722 | 5361 | 0.0005 | CTC5_06
RAC5-CT115-7 |  |  | Ronler Acres | CUB5 | 10722 | 5361 | 0.0005 | CTC5_07
RAC5-CT115-8 |  |  | Ronler Acres | CUB5 | 10722 | 5361 | 0.0005 | CTC5_08
RA5-CT114-1 |  |  | Ronler Acres | RA5 | 10722 | 5361 | 0.0005 | CTR5_01
RA6-CT114-1 |  |  | Ronler Acres | RA6 | 10722 | 5361 | 0.0005 | CTR6_01
RAC5-CT115-9 |  | (3) | Ronler Acres | CUB5 | 10722 | 5361 | 0.0005 | CTC5_09
RAC5-CT115-10 |  | (3) | Ronler Acres | CUB5 | 10722 | 5361 | 0.0005 | CTC5_10
RAC5-CT115-11 |  | (3) | Ronler Acres | CUB5 | 10722 | 5361 | 0.0005 | CTC5_11
RAC5-CT115-12 |  | (3) | Ronler Acres | CUB5 | 10722 | 5361 | 0.0005 | CTC5_12
RAC5-CT115-13 |  | (3) | Ronler Acres | CUB5 | 10722 | 5361 | 0.0005 | CTC5_13
RAC5-CT115-14 |  | (3) | Ronler Acres | CUB5 | 10722 | 5361 | 0.0005 | CTC5_14
RAC5-CT115-15 |  | (3) | Ronler Acres | CUB5 | 10722 | 5361 | 0.0005 | CTC5_15
RAC5-CT115-16 |  | (3) | Ronler Acres | CUB5 | 10722 | 5361 | 0.0005 | CTC5_16
RAC5-CT115-17 |  |  | Ronler Acres | CUB5 | 10722 | 5361 | 0.0005 | CTC5_17
CT-114-1-210 |  |  | Ronler Acres | CUB3 | 7700 | 3850 | 0.001 | CTC3_01
CT-114-2-210 |  |  | Ronler Acres | CUB3 | 7700 | 3850 | 0.001 | CTC3_02
CT-114-3-210 |  |  | Ronler Acres | CUB3 | 7700 | 3850 | 0.001 | CTC3_03
CT-114-4-210 |  |  | Ronler Acres | CUB3 | 7700 | 3850 | 0.001 | CTC3_04
CT-114-5-210 |  |  | Ronler Acres | CUB3 | 7700 | 3850 | 0.001 | CTC3_05
CUB3-CT114-21-10 |  |  | Ronler Acres | CUB3X | 7700 | 3850 | 0.001 | CTC3_06
CUB3-CT114-22-10 |  |  | Ronler Acres | CUB3X | 7700 | 3850 | 0.001 | CTC3_07
CUB3-CT114-23-10 |  |  | Ronler Acres | CUB3X | 7700 | 3850 | 0.001 | CTC3_08
CUB3-CT114-24-10 |  |  | Ronler Acres | CUB3X | 7700 | 3850 | 0.001 | CTC3_09
CUB3-CT114-25-10 |  |  | Ronler Acres | CUB3X | 7700 | 3850 | 0.001 | CTC3_10
CUB3-CT114-26-10 |  |  | Ronler Acres | CUB3X | 7700 | 3850 | 0.001 | CTC3_11
RP1-CT114-1-200 |  |  | Ronler Acres | RP1 | 3844 | 1922 | 0.001 | CTRP1_01
RP1-CT114-2-200 |  |  | Ronler Acres | RP1 | 3844 | 1922 | 0.001 | CTRP1_02
RP1-CT114-3-00 |  | (3) | Ronler Acres | RP1 | 3844 | 1922 | 0.001 | CTRP1_03
CUB2-CT114-1-210 |  |  | Ronler Acres | CUB2 | 8000 | 4000 | 0.001 | CTC2_01
CUB2-CT114-2-210 |  |  | Ronler Acres | CUB2 | 8000 | 4000 | 0.001 | CTC2_02
CUB2-CT114-3-210 |  |  | Ronler Acres | CUB2 | 8000 | 4000 | 0.001 | CTC2_03
CUB2-CT114-4-210 |  |  | Ronler Acres | CUB2 | 8000 | 4000 | 0.001 | CTC2_04
CUB2-CT114-5-210 |  |  | Ronler Acres | CUB2 | 8000 | 4000 | 0.001 | CTC2_05
CUB2-CT114-6-210 |  |  | Ronler Acres | CUB2 | 8000 | 4000 | 0.001 | CTC2_06
CUB2-CT114-7-210 |  |  | Ronler Acres | CUB2 | 8000 | 4000 | 0.001 | CTC2_07
CUB2-CT114-8-210 |  |  | Ronler Acres | CUB2 | 8000 | 4000 | 0.001 | CTC2_08
CUB2-CT114-9-210 |  |  | Ronler Acres | CUB2 | 8000 | 4000 | 0.001 | CTC2_09
CUB2-CT114-10-210 |  | (3) | Ronler Acres | CUB2 | 8000 | 4000 | 0.001 | CTC2_10
CUB2-CT114-11-10 |  |  | Ronler Acres | CUB2X | 8000 | 4000 | 0.001 | CTC2_11
CUB2-CT114-12-10 |  |  | Ronler Acres | CUB2X | 8000 | 4000 | 0.001 | CTC2_12
CUB2-CT114-13-10 |  |  | Ronler Acres | CUB2X | 8000 | 4000 | 0.001 | CTC2_13
CUB2-CT114-14-10 |  | (3) | Ronler Acres | CUB2X | 8000 | 4000 | 0.001 | CTC2_14
F20-CT114-1-210 |  |  | Ronler Acres | CUB1 | 8000 | 4000 | 0.001 | CTC1_01
F20-CT114-2-210 |  |  | Ronler Acres | CUB1 | 8000 | 4000 | 0.001 | CTC1_02
F20-CT114-3-210 |  |  | Ronler Acres | CUB1 | 8000 | 4000 | 0.001 | CTC1_03
F20-CT114-4-210 |  |  | Ronler Acres | CUB1 | 8000 | 4000 | 0.001 | CTC1_04
F20-CT114-5-210 |  |  | Ronler Acres | CUB1 | 8000 | 4000 | 0.001 | CTC1_05
F20-CT114-6-210 |  |  | Ronler Acres | CUB1 | 8000 | 4000 | 0.001 | CTC1_06
F20-CT114-7-210 |  |  | Ronler Acres | CUB1 | 8000 | 4000 | 0.001 | CTC1_07
F20-CT114-8-210 |  |  | Ronler Acres | CUB1 | 8000 | 4000 | 0.001 | CTC1_08
F20-CT114-9-210 |  |  | Ronler Acres | CUB1 | 8000 | 4000 | 0.001 | CTC1_09
F20-CT114-10-210 |  | (3) | Ronler Acres | CUB1 | 8000 | 4000 | 0.001 | CTC1_10
F20-CT114-11-210 |  | (3) | Ronler Acres | CUB1 | 8000 | 4000 | 0.001 | CTC1_11
N2-CT114-1 |  |  | Ronler Acres | N2 Plant | 10722 | 5361 | 0.001 | CTN2_01
N2-CT114-2 |  |  | Ronler Acres | N2 Plant | 10724 | 5361 | 0.001 | CTN2_02
N2-CT114-3 |  |  | Ronler Acres | N2 Plant | 10724 | 5361 | 0.001 | CTN2_03
RACB3-CT-114-1-35 |  |  | Ronler Acres | PCB-1 | 7700 | 3850 | 0.001 | CTCB_01
RACB3-CT-114-2-35 |  |  | Ronler Acres | PCB-1 | 7700 | 3850 | 0.001 | CTCB_02
RACB3-CT-114-3-35 |  |  | Ronler Acres | PCB-1 | 7700 | 3850 | 0.001 | CTCB_03
AL4-CHW-CT2 |  |  | Aloha | AL4 | 1500 | 750 | 0.001 | CTA4_01
AL4-CHW-CT3 |  |  | Aloha | AL4 | 1500 | 750 | 0.001 | CTA4_02
F15-CT29-1-1 |  |  | Aloha | F15 | 4680 | 2340 | 0.001 | CTF15_01
F15-CT29-1-2 |  |  | Aloha | F15 | 4680 | 2340 | 0.001 | CTF15_02
F15-CT29-1-3 |  |  | Aloha | F15 | 4680 | 2340 | 0.001 | CTF15_03
F15-CT29-1-4 |  |  | Aloha | F15 | 4680 | 2340 | 0.001 | CTF15_04
F15-CT29-1-5 |  |  | Aloha | F15 | 4680 | 2340 | 0.001 | CTF15_05
F15-CT29-1-6-1 |  |  | Aloha | F15 | 1956 | 978 | 0.001 | CTF15_06
References
(1) | Only those cooling towers dosed with chemicals listed in OAR 340-245-8040 were included.
(2) | Information provided by Intel Corporation based on vendor specifications.
(3) | Equipment is planned for future use.

## COOL_Ronler
Table 2
Cooling Towers TAC Emission Estimates—Ronler Campus
Intel Corporation
Source |  | Drift Loss of Circulating Water (1) (%) | Recirculation Flow Rate (1) (GPM) |  | Drift Loss |  | TAC Concentration (ppm) | [5 empty] | Emissions Estimate
[13 empty] | Glutaraldehyde |  | Methanol |  | Aluminum |  | Copper |  | Phosphoric Acid |  | Sulfuric Acid
[13 empty] | 111-30-8 |  | 67-56-1 |  | 7429-90-5 |  | 7440-50-8 |  | 7664-38-2 |  | 7664-93-9
|  |  | Maximum Daily | Average Annual | Daily (a) (lb/day) | Annual (b) (lb/yr) | Glutaraldehyde (4) | Methanol (4) | Aluminum (c) | Copper (4) | Phosphoric Acid (4) | Sulfuric Acid (4) | Daily (d) (lb/day) | Annual (e) (lb/yr) | Daily (d) (lb/day) | Annual (e) (lb/yr) | Daily (d) (lb/day) | Annual (e) (lb/yr) | Daily (d) (lb/day) | Annual (e) (lb/yr) | Daily (d) (lb/day) | Annual (e) (lb/yr) | Daily (d) (lb/day) | Annual (e) (lb/yr)
RAC4-CT114-1 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | -- | 0.3 | 0.3 | -- | -- | -- | -- | 1.0662e-06 | 0.00019459 | -- | -- | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-2 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | -- | 0.3 | 0.3 | -- | -- | -- | -- | 1.0662e-06 | 0.00019459 | -- | -- | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-3 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | -- | 0.3 | 0.3 | -- | -- | -- | -- | 1.0662e-06 | 0.00019459 | -- | -- | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-4 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | -- | 0.3 | 0.3 | -- | -- | -- | -- | 1.0662e-06 | 0.00019459 | -- | -- | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-5 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | -- | 0.3 | 0.3 | -- | -- | -- | -- | 1.0662e-06 | 0.00019459 | -- | -- | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-6 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | -- | 0.3 | 0.3 | -- | -- | -- | -- | 1.0662e-06 | 0.00019459 | -- | -- | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-7 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | -- | 0.3 | 0.3 | -- | -- | -- | -- | 1.0662e-06 | 0.00019459 | -- | -- | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-8 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | -- | 0.3 | 0.3 | -- | -- | -- | -- | 1.0662e-06 | 0.00019459 | -- | -- | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-9 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | -- | 0.3 | 0.3 | -- | -- | -- | -- | 1.0662e-06 | 0.00019459 | -- | -- | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-10 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | -- | 0.3 | 0.3 | -- | -- | -- | -- | 1.0662e-06 | 0.00019459 | -- | -- | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-11 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | -- | 0.3 | 0.3 | -- | -- | -- | -- | 1.0662e-06 | 0.00019459 | -- | -- | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-12 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | -- | 0.3 | 0.3 | -- | -- | -- | -- | 1.0662e-06 | 0.00019459 | -- | -- | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-13 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | -- | 0.3 | 0.3 | -- | -- | -- | -- | 1.0662e-06 | 0.00019459 | -- | -- | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-14 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | -- | 0.3 | 0.3 | -- | -- | -- | -- | 1.0662e-06 | 0.00019459 | -- | -- | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-15 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | -- | 0.3 | 0.3 | -- | -- | -- | -- | 1.0662e-06 | 0.00019459 | -- | -- | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-16 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | -- | 0.3 | 0.3 | -- | -- | -- | -- | 1.0662e-06 | 0.00019459 | -- | -- | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-17 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | -- | 0.3 | 0.3 | -- | -- | -- | -- | 1.0662e-06 | 0.00019459 | -- | -- | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-18 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | -- | 0.3 | 0.3 | -- | -- | -- | -- | 1.0662e-06 | 0.00019459 | -- | -- | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-19 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | -- | 0.3 | 0.3 | -- | -- | -- | -- | 1.0662e-06 | 0.00019459 | -- | -- | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC4-CT114-20 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0016561 | -- | 0.3 | 0.3 | -- | -- | -- | -- | 1.0662e-06 | 0.00019459 | -- | -- | 0.00019315 | 0.03525 | 0.00019315 | 0.03525
RAC5-CT115-1 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019483 | -- | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022893 | -- | -- | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-2 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019483 | -- | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022893 | -- | -- | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-3 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019483 | -- | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022893 | -- | -- | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-4 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019483 | -- | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022893 | -- | -- | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-5 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019483 | -- | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022893 | -- | -- | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-6 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019483 | -- | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022893 | -- | -- | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-7 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019483 | -- | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022893 | -- | -- | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-8 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019483 | -- | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022893 | -- | -- | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-9 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019483 | -- | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022893 | -- | -- | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-10 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019483 | -- | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022893 | -- | -- | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-11 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019483 | -- | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022893 | -- | -- | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-12 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019483 | -- | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022893 | -- | -- | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-13 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019483 | -- | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022893 | -- | -- | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-14 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019483 | -- | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022893 | -- | -- | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-15 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019483 | -- | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022893 | -- | -- | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-16 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019483 | -- | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022893 | -- | -- | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RAC5-CT115-17 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.0019483 | -- | 0.26471 | 0.26471 | -- | -- | -- | -- | 1.2544e-06 | 0.00022893 | -- | -- | 0.00017043 | 0.031103 | 0.00017043 | 0.031103
RA5-CT114-1 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.033122 | -- | 4.5 | 4.5 | -- | -- | -- | -- | 2.1325e-05 | 0.0038918 | -- | -- | 0.0028973 | 0.52875 | 0.0028973 | 0.52875
RA6-CT114-1 |  | 0.0005 | 10722 | 5361 | 643.8347 | 117499.8247 | -- | -- | 0.033122 | -- | 4.5 | 4.5 | -- | -- | -- | -- | 2.1325e-05 | 0.0038918 | -- | -- | 0.0028973 | 0.52875 | 0.0028973 | 0.52875
CT-114-1-210 |  | 0.001 | 7700 | 3850 | 924.7392 | 168764.904 | -- | -- | 0.0030111 | -- | 0.46023 | 0.21455 | -- | -- | -- | -- | 2.7844e-06 | 0.00050816 | -- | -- | 0.00042559 | 0.07767 | 0.0001984 | 0.036208
CT-114-2-210 |  | 0.001 | 7700 | 3850 | 924.7392 | 168764.904 | -- | -- | 0.0030111 | -- | 0.46023 | 0.21455 | -- | -- | -- | -- | 2.7844e-06 | 0.00050816 | -- | -- | 0.00042559 | 0.07767 | 0.0001984 | 0.036208
CT-114-3-210 |  | 0.001 | 7700 | 3850 | 924.7392 | 168764.904 | -- | -- | 0.0030111 | -- | 0.46023 | 0.21455 | -- | -- | -- | -- | 2.7844e-06 | 0.00050816 | -- | -- | 0.00042559 | 0.07767 | 0.0001984 | 0.036208
CT-114-4-210 |  | 0.001 | 7700 | 3850 | 924.7392 | 168764.904 | -- | -- | 0.0030111 | -- | 0.46023 | 0.21455 | -- | -- | -- | -- | 2.7844e-06 | 0.00050816 | -- | -- | 0.00042559 | 0.07767 | 0.0001984 | 0.036208
CT-114-5-210 |  | 0.001 | 7700 | 3850 | 924.7392 | 168764.904 | -- | -- | 0.0030111 | -- | 0.46023 | 0.21455 | -- | -- | -- | -- | 2.7844e-06 | 0.00050816 | -- | -- | 0.00042559 | 0.07767 | 0.0001984 | 0.036208
CUB3-CT114-21-10 |  | 0.001 | 7700 | 3850 | 924.7392 | 168764.904 | -- | -- | 0.0030111 | -- | 0.46023 | 0.21455 | -- | -- | -- | -- | 2.7844e-06 | 0.00050816 | -- | -- | 0.00042559 | 0.07767 | 0.0001984 | 0.036208
CUB3-CT114-22-10 |  | 0.001 | 7700 | 3850 | 924.7392 | 168764.904 | -- | -- | 0.0030111 | -- | 0.46023 | 0.21455 | -- | -- | -- | -- | 2.7844e-06 | 0.00050816 | -- | -- | 0.00042559 | 0.07767 | 0.0001984 | 0.036208
CUB3-CT114-23-10 |  | 0.001 | 7700 | 3850 | 924.7392 | 168764.904 | -- | -- | 0.0030111 | -- | 0.46023 | 0.21455 | -- | -- | -- | -- | 2.7844e-06 | 0.00050816 | -- | -- | 0.00042559 | 0.07767 | 0.0001984 | 0.036208
CUB3-CT114-24-10 |  | 0.001 | 7700 | 3850 | 924.7392 | 168764.904 | -- | -- | 0.0030111 | -- | 0.46023 | 0.21455 | -- | -- | -- | -- | 2.7844e-06 | 0.00050816 | -- | -- | 0.00042559 | 0.07767 | 0.0001984 | 0.036208
CUB3-CT114-25-10 |  | 0.001 | 7700 | 3850 | 924.7392 | 168764.904 | -- | -- | 0.0030111 | -- | 0.46023 | 0.21455 | -- | -- | -- | -- | 2.7844e-06 | 0.00050816 | -- | -- | 0.00042559 | 0.07767 | 0.0001984 | 0.036208
CUB3-CT114-26-10 |  | 0.001 | 7700 | 3850 | 924.7392 | 168764.904 | -- | -- | 0.0030111 | -- | 0.46023 | 0.21455 | -- | -- | -- | -- | 2.7844e-06 | 0.00050816 | -- | -- | 0.00042559 | 0.07767 | 0.0001984 | 0.036208
RP1-CT114-1-200 |  | 0.001 | 3844 | 1922 | 461.649 | 84250.9469 | 25 | 0.275 | 0.011041 | -- | 1.6875 | 0.7875 | 0.011541 | 2.1063 | 0.00012695 | 0.023169 | 5.0969e-06 | 0.00093018 | -- | -- | 0.00077903 | 0.14217 | 0.00036355 | 0.066348
RP1-CT114-2-200 |  | 0.001 | 3844 | 1922 | 461.649 | 84250.9469 | 25 | 0.275 | 0.011041 | -- | 1.6875 | 0.7875 | 0.011541 | 2.1063 | 0.00012695 | 0.023169 | 5.0969e-06 | 0.00093018 | -- | -- | 0.00077903 | 0.14217 | 0.00036355 | 0.066348
RP1-CT114-3-00 |  | 0.001 | 3844 | 1922 | 461.649 | 84250.9469 | 25 | 0.275 | 0.011041 | -- | 1.6875 | 0.7875 | 0.011541 | 2.1063 | 0.00012695 | 0.023169 | 5.0969e-06 | 0.00093018 | -- | -- | 0.00077903 | 0.14217 | 0.00036355 | 0.066348
CUB2-CT114-1-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | 7.5 | 0.0825 | 0.0033122 | -- | 0.50625 | 0.23625 | 0.0072058 | 1.3151 | 7.9263e-05 | 0.014466 | 3.1822e-06 | 0.00058076 | -- | -- | 0.00048639 | 0.088766 | 0.00022698 | 0.041424
CUB2-CT114-2-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | 7.5 | 0.0825 | 0.0033122 | -- | 0.50625 | 0.23625 | 0.0072058 | 1.3151 | 7.9263e-05 | 0.014466 | 3.1822e-06 | 0.00058076 | -- | -- | 0.00048639 | 0.088766 | 0.00022698 | 0.041424
CUB2-CT114-3-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | 7.5 | 0.0825 | 0.0033122 | -- | 0.50625 | 0.23625 | 0.0072058 | 1.3151 | 7.9263e-05 | 0.014466 | 3.1822e-06 | 0.00058076 | -- | -- | 0.00048639 | 0.088766 | 0.00022698 | 0.041424
CUB2-CT114-4-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | 7.5 | 0.0825 | 0.0033122 | -- | 0.50625 | 0.23625 | 0.0072058 | 1.3151 | 7.9263e-05 | 0.014466 | 3.1822e-06 | 0.00058076 | -- | -- | 0.00048639 | 0.088766 | 0.00022698 | 0.041424
CUB2-CT114-5-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | 7.5 | 0.0825 | 0.0033122 | -- | 0.50625 | 0.23625 | 0.0072058 | 1.3151 | 7.9263e-05 | 0.014466 | 3.1822e-06 | 0.00058076 | -- | -- | 0.00048639 | 0.088766 | 0.00022698 | 0.041424
CUB2-CT114-6-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | 7.5 | 0.0825 | 0.0033122 | -- | 0.50625 | 0.23625 | 0.0072058 | 1.3151 | 7.9263e-05 | 0.014466 | 3.1822e-06 | 0.00058076 | -- | -- | 0.00048639 | 0.088766 | 0.00022698 | 0.041424
CUB2-CT114-7-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | 7.5 | 0.0825 | 0.0033122 | -- | 0.50625 | 0.23625 | 0.0072058 | 1.3151 | 7.9263e-05 | 0.014466 | 3.1822e-06 | 0.00058076 | -- | -- | 0.00048639 | 0.088766 | 0.00022698 | 0.041424
CUB2-CT114-8-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | 7.5 | 0.0825 | 0.0033122 | -- | 0.50625 | 0.23625 | 0.0072058 | 1.3151 | 7.9263e-05 | 0.014466 | 3.1822e-06 | 0.00058076 | -- | -- | 0.00048639 | 0.088766 | 0.00022698 | 0.041424
CUB2-CT114-9-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | 7.5 | 0.0825 | 0.0033122 | -- | 0.50625 | 0.23625 | 0.0072058 | 1.3151 | 7.9263e-05 | 0.014466 | 3.1822e-06 | 0.00058076 | -- | -- | 0.00048639 | 0.088766 | 0.00022698 | 0.041424
CUB2-CT114-10-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | 7.5 | 0.0825 | 0.0033122 | -- | 0.50625 | 0.23625 | 0.0072058 | 1.3151 | 7.9263e-05 | 0.014466 | 3.1822e-06 | 0.00058076 | -- | -- | 0.00048639 | 0.088766 | 0.00022698 | 0.041424
CUB2-CT114-11-10 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | 18.75 | 0.20625 | 0.0082804 | -- | 1.2656 | 0.59062 | 0.018014 | 3.2876 | 0.00019816 | 0.036164 | 7.9556e-06 | 0.0014519 | -- | -- | 0.001216 | 0.22191 | 0.00056745 | 0.10356
CUB2-CT114-12-10 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | 18.75 | 0.20625 | 0.0082804 | -- | 1.2656 | 0.59062 | 0.018014 | 3.2876 | 0.00019816 | 0.036164 | 7.9556e-06 | 0.0014519 | -- | -- | 0.001216 | 0.22191 | 0.00056745 | 0.10356
CUB2-CT114-13-10 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | 18.75 | 0.20625 | 0.0082804 | -- | 1.2656 | 0.59062 | 0.018014 | 3.2876 | 0.00019816 | 0.036164 | 7.9556e-06 | 0.0014519 | -- | -- | 0.001216 | 0.22191 | 0.00056745 | 0.10356
CUB2-CT114-14-10 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | 18.75 | 0.20625 | 0.0082804 | -- | 1.2656 | 0.59062 | 0.018014 | 3.2876 | 0.00019816 | 0.036164 | 7.9556e-06 | 0.0014519 | -- | -- | 0.001216 | 0.22191 | 0.00056745 | 0.10356
F20-CT114-1-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | -- | -- | 0.0030111 | -- | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.8929e-06 | 0.00052796 | -- | -- | 0.00044217 | 0.080696 | 0.00020635 | 0.037658
F20-CT114-2-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | -- | -- | 0.0030111 | -- | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.8929e-06 | 0.00052796 | -- | -- | 0.00044217 | 0.080696 | 0.00020635 | 0.037658
F20-CT114-3-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | -- | -- | 0.0030111 | -- | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.8929e-06 | 0.00052796 | -- | -- | 0.00044217 | 0.080696 | 0.00020635 | 0.037658
F20-CT114-4-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | -- | -- | 0.0030111 | -- | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.8929e-06 | 0.00052796 | -- | -- | 0.00044217 | 0.080696 | 0.00020635 | 0.037658
F20-CT114-5-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | -- | -- | 0.0030111 | -- | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.8929e-06 | 0.00052796 | -- | -- | 0.00044217 | 0.080696 | 0.00020635 | 0.037658
F20-CT114-6-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | -- | -- | 0.0030111 | -- | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.8929e-06 | 0.00052796 | -- | -- | 0.00044217 | 0.080696 | 0.00020635 | 0.037658
F20-CT114-7-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | -- | -- | 0.0030111 | -- | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.8929e-06 | 0.00052796 | -- | -- | 0.00044217 | 0.080696 | 0.00020635 | 0.037658
F20-CT114-8-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | -- | -- | 0.0030111 | -- | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.8929e-06 | 0.00052796 | -- | -- | 0.00044217 | 0.080696 | 0.00020635 | 0.037658
F20-CT114-9-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | -- | -- | 0.0030111 | -- | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.8929e-06 | 0.00052796 | -- | -- | 0.00044217 | 0.080696 | 0.00020635 | 0.037658
F20-CT114-10-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | -- | -- | 0.0030111 | -- | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.8929e-06 | 0.00052796 | -- | -- | 0.00044217 | 0.080696 | 0.00020635 | 0.037658
F20-CT114-11-210 |  | 0.001 | 8000 | 4000 | 960.768 | 175340.16 | -- | -- | 0.0030111 | -- | 0.46023 | 0.21477 | -- | -- | -- | -- | 2.8929e-06 | 0.00052796 | -- | -- | 0.00044217 | 0.080696 | 0.00020635 | 0.037658
N2-CT114-1 |  | 0.001 | 10722 | 5361 | 1287.6693 | 234999.6494 | -- | -- | -- | -- | 4.05 | 4.05 | -- | -- | -- | -- | -- | -- | -- | -- | 0.0052151 | 0.95175 | 0.0052151 | 0.95175
N2-CT114-2 |  | 0.001 | 10724 | 5361 | 1287.9095 | 234999.6494 | -- | -- | -- | 0.06 | 4.05 | 4.05 | -- | -- | -- | -- | -- | -- | 7.7275e-05 | 0.0141 | 0.005216 | 0.95175 | 0.005216 | 0.95175
N2-CT114-3 |  | 0.001 | 10724 | 5361 | 1287.9095 | 234999.6494 | -- | -- | -- | 0.06 | 4.05 | 4.05 | -- | -- | -- | -- | -- | -- | 7.7275e-05 | 0.0141 | 0.005216 | 0.95175 | 0.005216 | 0.95175
RACB3-CT-114-1-35 |  | 0.001 | 7700 | 3850 | 924.7392 | 168764.904 | 25 | 0.275 | 0.011041 | -- | 1.6875 | 0.7875 | 0.023118 | 4.2191 | 0.0002543 | 0.04641 | 1.021e-05 | 0.0018633 | -- | -- | 0.0015605 | 0.28479 | 0.00072823 | 0.1329
RACB3-CT-114-2-35 |  | 0.001 | 7700 | 3850 | 924.7392 | 168764.904 | 25 | 0.275 | 0.011041 | -- | 1.6875 | 0.7875 | 0.023118 | 4.2191 | 0.0002543 | 0.04641 | 1.021e-05 | 0.0018633 | -- | -- | 0.0015605 | 0.28479 | 0.00072823 | 0.1329
RACB3-CT-114-3-35 |  | 0.001 | 7700 | 3850 | 924.7392 | 168764.904 | 25 | 0.275 | 0.011041 | -- | 1.6875 | 0.7875 | 0.023118 | 4.2191 | 0.0002543 | 0.04641 | 1.021e-05 | 0.0018633 | -- | -- | 0.0015605 | 0.28479 | 0.00072823 | 0.1329
Total | [12 empty] | 0.24809 | 45.2772 | 0.002729 | 0.49805 | 0.00025731 | 0.04696 | 0.00015455 | 0.0282 | 0.054494 | 9.9447 | 0.040469 | 7.3853
Notes
TAC = Toxic Air Contaminant
(a) | Daily drift loss (lb/day) = (maximum daily recirculation flow rate [gpm]) x (density of water [lb/gal]) x (drift loss percent of circulating water [%] / 100) x (60 min/hr) x (daily hours of operation [hrs/day])
[6 empty] | Density of water (lb/gal) = | 8.34
[6 empty] | Daily hours of operation (hrs/day) = | 24 | (2)
(b) | Annual drift loss (lb/yr) = (average annual recirculation flow rate [gpm]) x (density of water [lb/gal]) x (drift loss percent of circulating water [%] / 100) x (60 min/hr) x (daily hours of operation [hrs/day]) x (annual days of operation [days/yr])
[6 empty] | Annual days of operation (days/yr) = | 365 | (2)
(c) | Aluminum concentration (ppm) = (aluminum distearate concentration [ppm]) x (molecular weight of aluminum [g/mol]) / (molecular weight of aluminum distearate [g/mol])
[6 empty] | Molecular weight of aluminum (g/mol) = | 26.98
[6 empty] | Molecular weight of aluminum distearate (g/mol) = | 610.93
[6 empty] | Concentration of aluminum distearate - RAC4 (ppm) = | 0.0375 | (4)
[6 empty] | Concentration of aluminum distearate - RAC5 (ppm = | 0.044118 | (4)
[6 empty] | Concentration of aluminum distearate - CUB3, F20 (ppm) = | 0.068182 | (4)
[6 empty] | Concentration of aluminum distearate - RP1, PAWN (ppm) = | 0.25 | (4)
[6 empty] | Concentration of aluminum distearate - CUB2 (ppm) = | 0.075 | (4)
[6 empty] | Concentration of aluminum distearate - CUB2_EXP (ppm) = | 0.1875 | (4)
(d) | Daily emissions estimate (lb/day) = (daily drift loss [lb/day]) x (concentration [ppm] / 1,000,000) | [6 empty] | (3)
(e) | Annual emissions estimate (lb/yr) = (annual drift loss [lb/yr]) x (concentration [ppm] / 1,000,000) | [6 empty] | (3)
References
(1) | See Table 1, Input Cooling Tower Rates and Parameters.
(2) | Based on continuous operation.
(3) | Assumes the composition of the drift loss is same as the cooling tower makeup water.
(4) | Information provided by Intel Corporation. TAC concentration Is based on dosage rates and TAC percentage in SDS.

## COOL_Aloha
Table 3
Cooling Towers TAC Emission Estimates—Aloha Campus
Intel Corporation
Source |  | Drift Loss of Circulating Water (1) (%) | Recirculation Flow Rate (1) (GPM) |  | Drift Loss |  | TAC Concentration (ppm) |  |  | Emissions Estimate
[10 empty] | Phosphoric Acid |  | Aluminum |  | Sulfuric Acid
[10 empty] | 7664-38-2 |  | 7429-90-5 |  | 7664-93-9
|  |  | Maximum Daily | Average Annual | Daily (a) (lb/day) | Annual (b) (lb/yr) | Phosphoric Acid (4) | Aluminum (c) | Sulfuric Acid (4) | Daily (d) (lb/day) | Annual (e) (lb/yr) | Daily (d) (lb/day) | Annual (e) (lb/yr) | Daily (d) (lb/day) | Annual (e) (lb/yr)
AL4-CHW-CT2 |  | 0.001 | 1500 | 750 | 180.144 | 32876.28 | 2.5312 | 0.016561 | 1.1812 | 0.00045599 | 0.083218 | 2.9833e-06 | 0.00054446 | 0.0002128 | 0.038835
AL4-CHW-CT3 |  | 0.001 | 1500 | 750 | 180.144 | 32876.28 | 2.5312 | 0.016561 | 1.1812 | 0.00045599 | 0.083218 | 2.9833e-06 | 0.00054446 | 0.0002128 | 0.038835
F15-CT29-1-1 |  | 0.001 | 4680 | 2340 | 562.0493 | 102573.9936 | 1.0125 | 0.0066243 | 0.4725 | 0.00056907 | 0.10386 | 3.7232e-06 | 0.00067948 | 0.00026557 | 0.048466
F15-CT29-1-2 |  | 0.001 | 4680 | 2340 | 562.0493 | 102573.9936 | 1.0125 | 0.0066243 | 0.4725 | 0.00056907 | 0.10386 | 3.7232e-06 | 0.00067948 | 0.00026557 | 0.048466
F15-CT29-1-3 |  | 0.001 | 4680 | 2340 | 562.0493 | 102573.9936 | 1.0125 | 0.0066243 | 0.4725 | 0.00056907 | 0.10386 | 3.7232e-06 | 0.00067948 | 0.00026557 | 0.048466
F15-CT29-1-4 |  | 0.001 | 4680 | 2340 | 562.0493 | 102573.9936 | 1.0125 | 0.0066243 | 0.4725 | 0.00056907 | 0.10386 | 3.7232e-06 | 0.00067948 | 0.00026557 | 0.048466
F15-CT29-1-5 |  | 0.001 | 4680 | 2340 | 562.0493 | 102573.9936 | 1.0125 | 0.0066243 | 0.4725 | 0.00056907 | 0.10386 | 3.7232e-06 | 0.00067948 | 0.00026557 | 0.048466
F15-CT29-1-6-1 |  | 0.001 | 1956 | 978 | 234.9078 | 42870.6691 | 5.0625 | 0.033122 | 2.3625 | 0.0011892 | 0.21703 | 7.7805e-06 | 0.0014199 | 0.00055497 | 0.10128
Total | [9 empty] | 0.0049466 | 0.90275 | 3.2363e-05 | 0.0059063 | 0.0023084 | 0.42128
Notes
TAC = Toxic Air Contaminant
(a) | Daily drift loss (lb/day) = (maximum daily recirculation flow rate [gpm]) x (density of water [lb/gal]) x (drift loss percent of circulating water [%] / 100) x (60 min/hr) x (daily hours of operation [hrs/day])
[5 empty] | Density of water (lb/gal) = | 8.34
[5 empty] | Daily hours of operation (hrs/day) = | 24 | (2)
(b) | Annual drift loss (lb/yr) = (average annual recirculation flow rate [gpm]) x (density of water [lb/gal]) x (drift loss percent of circulating water [%] / 100) x (60 min/hr) x (daily hours of operation [hrs/day]) x (annual days of operation [days/yr])
[5 empty] | Annual days of operation (days/yr) = | 365 | (2)
(c) | Daily emissions estimate (lb/day) = (daily drift loss [lb/day]) x (concentration [ppm] / 1,000,000) | [5 empty] | (3)
(d) | Aluminum concentration (ppm) = (aluminum distearate concentration [ppm]) x (molecular weight of aluminum [g/mol]) / (molecular weight of aluminum distearate [g/mol])
[5 empty] | Molecular weight of aluminum (g/mol) = | 26.98
[5 empty] | Molecular weight of aluminum distearate (g/mol) = | 610.93
[5 empty] | Concentration of aluminum distearate - AL4 (ppm) = | 0.375 | (4)
[5 empty] | Concentration of aluminum distearate - F15 (ppm) = | 0.15 | (4)
(e) | Annual emissions estimate (lb/yr) = (annual drift loss [lb/yr]) x (concentration [ppm] / 1,000,000) | [5 empty] | (3)
References
(1) | See Table 1, Input Cooling Tower Rates and Parameters.
(2) | Based on continuous operation.
(3) | Assumes the composition of the drift loss is same as the cooling tower makeup water.
(4) | Information provided by Intel Corporation. TAC concentration Is based on dosage rates and TAC percentage in SDS.